## Sheet1
N Test Enac | Code CA Manufacturer Plant | Production order (PO) | Drum | Cable | Diameter | Number of cables | Laboratory | Compound | Open or Closed Doors Humidity content | Humidity | Temperature | Safety Margin | Test date | Euroclasse | FS | THR1200s | HRRmax | Time | FIGRA | Euroclass | TSP1200s | Peak SPR | Smoke | Flaming inf 10s | Flaming sup 10s | Droplets
|  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.25 | 14 | Paron | SXLPE+0400FEIT+1602SEES | -- | 51.4 | 24 | No | 2015-07-27 | D_s2_d2 | 2.8 | 45.5 | 61.2 | 1236 | 104.6 | D | 56.6 | 0.09 | s2 | y | y | d2
|  |  |  | DRAKA VODAFONE 2015/06 96 FO G657 A2 | 9.4 | 17 | Paron | LSOH | -- | 43.8 | 24.4 | No | 2015-07-28 | D_s2_d2 | 3.3 | 51.5 | 268.1 | 681 | 708.6 | D | 256.5 | 0.71 | s2 | y | y | d2
TN_2015_98 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.85 | 180 | Vilanova | 1300IEES | -- | 73 | 25 | No | 2015-07-30 | C_s2_d0 | 1.7 | 13.1 | 34.8 | 705 | 99.6 | C | 149.1 | 0.4 | s2 | n | n | d0
TN_2015_99 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.85 | 180 | Vilanova | 1300IEES | -- | 74 | 27 | No | 2015-07-30 | B2_s2_d0 | 1.1 | 9.8 | 24.6 | 624 | 104.6 | B2 | 88.7 | 0.26 | s2 | n | n | d0
TN_2015_0100 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.25 | 14 | Vilanova | SXLPE+0400FEIT+1602SEES | -- | 90 | 24 | No | 2015-08-26 | B2_s1_d0 | 0.67 | 4.8 | 13.4 | 822 | 25.7 | B2 | 30.5 | 0.08 | s1 | n | n | d0
TN_2015_0101 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.25 | 14 | Vilanova | SXLPE+0400FEIT+1602SEES | -- | 81 | 27 | No | 2015-08-26 | C_s1_d1 | 1.3 | 19.1 | 26.4 | 1158 | 51.2 | C | 46.4 | 0.1 | s1 | y | n | d1
TN_2015_0102 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 4X4 | 12.5 | 12 | Vilanova | SXLPE+0400FEIT+1602SEES | -- | 92 | 24 | No | 2015-09-03 | B2_s1_d2 | 0.35 | 6.1 | 9.1 | 789 | 32 | B2 | 4.4 | 0.01 | s1 | n | y | d2
TN_2015_0103 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.85 | 180 | Vilanova | 1602SEES | -- | 90 | 23 | No | 2015-09-03 | B2_s1_d0 | 0.45 | 4.6 | 12.2 | 636 | 44.9 | B2 | 5.6 | 0.02 | s1 | n | n | d0
TN_2015_0104 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.81 | 180 | Vilanova | 5300SEIT | -- | 90 | 23 | No | 2015-09-03 | B2_s1_d0 | 0.55 | 7.7 | 15.1 | 591 | 75.9 | B2 | 9.8 | 0.02 | s1 | n | n | d0
TN_2015_0105 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.81 | 180 | Vilanova | 1420FEES | -- | 85 | 23 | No | 2015-09-04 | B2_s1_d0 | 0.25 | 3.2 | 7.7 | 603 | 33.1 | B2 | 3 | 0.01 | s1 | n | n | d0
TN_2015_0106 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.85 | 180 | Vilanova | 1602SEES | -- | 72 | 22 | No | 2015-09-09 | B2_s1_d0 | 0.45 | 4.5 | 10.7 | 618 | 43.9 | B2 | 7.9 | 0.02 | s1 | n | n | d0
TN_2015_0107 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.85 | 180 | Vilanova | 1602SEES | -- | 67 | 23 | No | 2015-09-09 | B2_s1_d0 | 0.75 | 4.6 | 13.3 | 663 | 47.3 | B2 | 28.2 | 0.05 | s1 | n | n | d0
TN_2015_0108 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.81 | 180 | Vilanova | 5300SEIT | -- | 64 | 24 | No | 2015-09-09 | B2_s1_d0 | 1 | 8.8 | 22.3 | 713 | 64.7 | B2 | 18.3 | 0.04 | s1 | n | n | d0
|  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.81 | 180 | Paron | 5300SEIT | -- | 65.7 | 23.9 | No | 2015-09-16 | B2_s1_d0 | 0.9 | 9.9 | 21 | 792 | 66 | B2 | 24 | 0.01 | s1 | n | n | d0
|  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.85 | 180 | Paron | 1602SEES | -- | 68 | 23.6 | No | 2015-09-16 | C_s1_d0 | 1.45 | 15.4 | 35 | 816 | 76.2 | C | 44.4 | 0.13 | s1 | n | n | d0
TN_2015_0109 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.81 | 180 | Vilanova | 5300SEIT | -- | 60 | 24 | No | 2015-09-17 | B2_s1_d0 | 0.95 | 7.7 | 19.2 | 672 | 60.1 | B2 | 19.4 | 0.03 | s1 | n | n | d0
|  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.25 | 14 | Paron | SXLPE+0400FEIT+1602SEES | -- | 58.2 | 22 | No | 2015-09-18 | E ou F_s2_d2 | 3.3 | 76.8 | 188.3 | 1443 | 165 | E ou F | 84.8 | 0.49 | s2 | y | y | d2
TN_2015_0110 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 4X4 | 12.5 | 12 | Vilanova | SXLPE+0400FEIT+1602SEES | -- | 46 | 22.7 | No | 2015-09-23 | B2_s1_d0 | 0.45 | 8.7 | 14.3 | 852 | 45.6 | B2 | 13.4 | 0.02 | s1 | n | n | d0
TN_2015_0111 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3X150+1X70 0.6/1KV | 47.5 | 4 | Vilanova | SXLPE+0400FEIT+1602SEES | -- | 40.8 | 24.7 | No | 2015-09-23 | B2_s1_d0 | 0.42 | 4.5 | 6.1 | 990 | 18.8 | B2 | 1.9 | 0.01 | s1 | n | n | d0
TN_2015_0112 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3X150+1X70 0.6/1KV | 47.5 | 4 | Vilanova | SXLPE+0400FEIT+1602SEES | -- | 39.7 | 25.2 | No | 2015-09-23 | B2_s1_d0 | 0.55 | 5.5 | 7.2 | 1080 | 18.5 | B2 | 3 | 0.01 | s1 | n | n | d0
|  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X70 | 13.65 | 11 | CEIS | 1300IEES | -- | 36 | 24.3 | No | 2015-09-25 | B2_s1_d0 | 0.4 | 3.52 | 7.4 | 705 | 19.2 | B2 | 0.9 | 0.01 | s1 | n | n | d0
TN_2015_0113 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.46 | 15 | Vilanova | SXLPE+0400FEIT+1602SEES | 2720 | 58 | 21.2 | No | 2015-09-28 | C_s1_d0 | 1.3 | 15.6 | 27.9 | 882 | 55.4 | C | 43.8 | 0.013 | s1 | n | n | d0
TN_2015_0114 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.73 | 14 | Vilanova | XLPE+TP0851+1602SEES | 2200 | 51.1 | 24 | No | 2015-09-28 | C_s1_d1 | 1.55 | 20.3 | 37.4 | 900 | 69 | C | 49.5 | 0.11 | s1 | y | n | d1
TN_2015_0115 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.01 | 15 | Vilanova | SXLPE+0400FEIT+1602SEES | 1895 | 42 | 25.8 | No | 2015-09-28 | D_s2_d1 | 2.15 | 29.1 | 38.8 | 849 | 85.5 | D | 108.1 | 0.17 | s2 | y | n | d1
|  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 10.2 | 15 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 41.9 | 20.3 | No | 2015-09-29 | B2_s1_d0 | 0.7 | 5.9 | 12.8 | 816 | 38.4 | B2 | 16.1 | 0.03 | s1 | n | n | d0
|  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 10 | 15 | Paron | SXLPE+0400FEIT+1602SEES | 2335-2357-2349 | 37.1 | 21.8 | No | 2015-09-29 | B2_s1_d1 | 0.78 | 11 | 24.7 | 876 | 48.5 | B2 | 41.1 | 0.09 | s1 | y | n | d1
|  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 10 | 15 | Paron | SXLPE+TP0851+1602SEES | -- | 39.4 | 20.2 | No | 2015-10-02 | B2_s1_d0 | 0.68 | 10.9 | 21 | 738 | 48.3 | B2 | 20.3 | 0.04 | s1 | n | n | d0
TN_2015_0116 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.07 | 15 | Vilanova | XLPE+400FEIT+ECCOH5549 | 1605 | 58.7 | 23 | No | 2015-10-02 | B2_s1_d0 | 1.17 | 14 | 28.2 | 825 | 56 | B2 | 16.3 | 0.04 | s1 | n | n | d0
TN_2015_0117 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.91 | 15 | Vilanova | XLPE+400FEIT+5300SEIT | 2517 | 54.4 | 24.4 | No | 2015-10-02 | C_s1_d2 | 1.45 | 22.4 | 43.2 | 921 | 72.1 | C | 20.4 | 0.06 | s1 | y | y | d2
TN_2015_0121 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.25 | 14 | Vilanova | SXLPE+0400FEIT+1602SEES | 2852 | 52 | 21 | No | 2015-10-07 | D_s1_d2 | 3.3 | 49.1 | 73.6 | 1500 | 106.2 | D | 20.8 | 0.05 | s1 | y | y | d2
TN_2015_0122 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.25 | 14 | Vilanova | SXLPE+0400FEIT+1602SEES | 2715 | 44.4 | 24 | No | 2015-10-07 | D_s1_d2 | 3.3 | 60 | 120.9 | 1440 | 109.5 | D | 46.3 | 0.1 | s1 | y | y | d2
|  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.4 | 15 | CEIS | SXLPE+1420FEES+1602SEES | -- | 59 | 18.17 | No | 2015-10-07 | B2_s1_d2 | 0.8 | 14.1 | 26.2 | 771 | 62.1 | B2 | 15.7 | 0.05 | s1 | n | y | d2
TN_2015_0118 |  |  |  | RED ELEC RHZ1-RA-2OL(AS) 1X1200MM2 36/66KV | 86.8 | 2 | Vilanova | 6000SEES+SKINDYM7100.15MM | -- | 49.3 | 23.8 | No | 2015-10-09 | C_s1_d2 | 1.11 | 16 | 37 | 1494 | 31 | C | 3.6 | 0.01 | s1 | n | y | d2
TN_2015_0119 |  |  |  | RED ELEC RHZ1-RA-2OL(AS) 1X630MM2 127/220KV | 101 | 2 | Vilanova | 6000SEES+SKINDYM7100.15MM | -- | 48.3 | 21.9 | No | 2015-10-09 | B2_s1_d2 | 0.96 | 11.5 | 19.5 | 1497 | 21.6 | B2 | 33 | 0.04 | s1 | n | y | d2
TN_2015_0120 |  |  |  | RED ELEC RHZ1-RA-2OL(AS) 1X630MM2 127/220KV | 101 | 2 | Vilanova | 6000SEES+SKINDYM7100.15MM | -- | 51.7 | 20.7 | No | 2015-10-09 | B2_s1_d2 | 0.94 | 7.5 | 10 | 771 | 21.2 | B2 | 7.2 | 0.02 | s1 | n | y | d2
|  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 10 | 15 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 46.5 | 22.6 | No | 2015-10-09 | B2_s1_d0 | 0.7 | 8.5 | 14 | 867 | 43.3 | B2 | 10.9 | 0.02 | s1 | n | n | d0
TN_2015_0123 |  |  |  | RED ELEC RHZ1-RA-2OL(AS) 1X630MM2 127/220KV | 101 | 2 | Vilanova | 6000SEES+SKINDYM7100.15MM | -- | 57.7 | 17.1 | No | 2015-10-16 | B2_s1_d2 | 0.9 | 14.3 | 18.6 | 1437 | 36.7 | B2 | 7.9 | 0.02 | s1 | n | y | d2
TN_2015_0124 |  |  |  | RED ELEC RHZ1-RA-2OL(AS) 1X1200MM2 36/66KV | 86.8 | 2 | Vilanova | 6000SEES+SKINDYM7100.15MM | -- | 55.1 | 15.6 | No | 2015-10-16 | B2_s1_d2 | 0.92 | 12.3 | 23 | 1497 | 24.2 | B2 | 15.6 | 0.04 | s1 | n | y | d2
TN_2015_0125 |  |  |  | RED ELEC RHZ1-RA-2OL(AS) 1X1600MM2 76/132KV | 109.6 | 2 | Vilanova | 6000SEES+SKINDYM7100.15MM | -- | 53 | 19.6 | No | 2015-10-16 | B2_s1_d1 | 1.3 | 10.3 | 15.7 | 879 | 30.9 | B2 | 19.2 | 0.04 | s1 | y | n | d1
TN_2015_0126 |  |  |  | RED ELEC RHZ1-RA-2OL(AS) 1X1600MM2 76/132KV | 109.6 | 2 | Vilanova | 6000SEES+SKINDYM7100.15MM | -- | 51.1 | 18.5 | No | 2015-10-21 | B2_s1_d2 | 0.8 | 8.7 | 11 | 882 | 22.4 | B2 | 9.5 | 0.02 | s1 | n | y | d2
TN_2015_0127 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.35 | 15 | Vilanova | SXLPE-FR+5300SEIT | 1756 | 52.1 | 17 | No | 2015-10-21 | D_s1_d2 | 1.4 | 20.6 | 60.1 | 708 | 147.9 | D | 35.2 | 0.05 | s1 | n | y | d2
TN_2015_0128 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.75 | 15 | Vilanova | SXLPE-FR+1602SEES | 2151 | 57.7 | 15.5 | No | 2015-10-21 | D_s1_d2 | 3.3 | 58.3 | 78.6 | 915 | 135.6 | D | 48 | 0.17 | s1 | n | y | d2
TN_2015_0129 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.07 | 15 | Vilanova | XLPE+400FEIT+5300SEIT | 2514 | 51.7 | 19.2 | No | 2015-10-29 | B2_s1_d1 | 0.96 | 15 | 27.6 | 843 | 52.4 | B2 | 11.8 | 0.03 | s1 | y | n | d1
TN_2015_0130 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.09 | 15 | Vilanova | XLPE+400FEIT+MEGOLONS-540 | 2591 | 48.3 | 21.4 | No | 2015-11-29 | C_s1_d0 | 1.46 | 17.4 | 29.7 | 708 | 76.6 | C | 44.9 | 0.08 | s1 | n | n | d0
TN_2015_0131 |  |  |  | MK-HF06 KEVI 1X6 | 4.65 | 60 | Vilanova | LSOH | 1662 | 44.3 | 23.2 | No | 2015-11-29 | C_s1_d1 | 1.5 | 10.4 | 34.9 | 636 | 108.8 | C | 33.4 | 0.16 | s1 | y | n | d1
TN_2015_0132 |  |  |  | AL-HEPRZ1(S) 1X240MM2 12/20KV | 38.5 | 5 | Vilanova | HEPR+6000SEES | 1154 | 42.5 | 24.2 | No | 2015-11-29 | D_s1_d2 | 2.1 | 34 | 94.5 | 1500 | 78.7 | D | 5.9 | 0.05 | s1 | n | y | d2
|  |  |  | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.82 | 180 | Paron | PE0.10-0.15+53AESEIT | 1231 1216 1455 | 40 | 24.3 | No | 2015-11-02 | C_s1_d2 | 1.65 | 21.5 | 48.5 | 738 | 137.6 | C | 45.9 | 0.15 | s1 | y | y | d2
TN_2015_0133 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.25 | 14 | Vilanova | SXLPE+0400FEIT+1602SEES | 2811 | 63.9 | 22.8 | No | 2015-11-03 | D_s1_d2 | 2.2 | 30.2 | 40.1 | 945 | 63.4 | D | 35.6 | 0.08 | s1 | n | y | d2
TN_2015_0134 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.25 | 14 | Vilanova | SXLPE+0400FEIT+1602SEES | 3017 | 69.3 | 21.3 | No | 2015-11-03 | D_s1_d1 | 2.25 | 35.7 | 47.2 | 1071 | 81.7 | D | 12.7 | 0.04 | s1 | y | n | d1
TN_2015_0135 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.46 | 15 | Vilanova | SXLPE+0400FEIT+1602SEES | 3278 | 75.6 | 18.8 | No | 2015-11-03 | C_s1_d2 | 1.22 | 17.4 | 35 | 876 | 63.4 | C | 31.5 | 0.1 | s1 | n | y | d2
|  |  |  | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.83 | 180 | Paron | 1602SEES | 1974 1249 1210 | 55.8 | 23.4 | No | 2015-11-04 | B2_s1_d0 | 0.7 | 9.4 | 19.6 | 807 | 52 | B2 | 22.1 | 0.04 | s1 | n | n | d0
|  |  |  | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.82 | 180 | Paron | 5300SEIT | 2097 1953 1858 | 52.4 | 24.3 | No | 2015-11-04 | B2_s1_d0 | 0.7 | 8.7 | 17.3 | 807 | 66.3 | B2 | 12.7 | 0.02 | s1 | n | n | d0
TN_2015_0136 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.46 | 15 | Vilanova | SXLPE+0400FEIT+1602SEES | 1974 | 78.9 | 18.1 | No | 2015-11-08 | B2_s1_d1 | 0.83 | 13.1 | 26.3 | 774 | 56 | B2 | 43.4 | 0.07 | s1 | y | n | d1
TN_2015_0137 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.73 | 14 | Vilanova | XLPE+TP0851+1602SEES | 1986 | 73 | 19.7 | No | 2015-11-08 | C_s1_d1 | 1.4 | 19.8 | 29.2 | 819 | 56.7 | C | 35.2 | 0.09 | s1 | y | n | d1
TN_2015_0138 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.73 | 14 | Vilanova | XLPE+TP0851+1602SEES | 2047 | 68.5 | 20.8 | No | 2015-11-08 | C_s1_d1 | 1.12 | 15.6 | 25.4 | 750 | 56.7 | C | 17 | 0.03 | s1 | y | n | d1
TN_2015_0139 |  |  |  | DRAKA 2015 16 FO 10D TKT MOVISTAR | 13.4 | 12 | Vilanova | JELLYINTUBES1600SEES+1600SEES | 2114 | 68.7 | 18.8 | No | 2015-11-10 | E ou F_s2_d2 | 3.3 | 123.3 | 219.5 | 1218 | 270 | E ou F | 75.4 | 0.29 | s2 | y | y | d2
TN_2015_0140 |  |  |  | DRAKA 2015 16 FO 10D TKT MOVISTAR | 12.6 | 12 | Vilanova | DRYTUBES1600SEES+1600SEES | 2210 | 53.5 | 22.6 | No | 2015-11-10 | E ou F_s1_d2 | 3.3 | 99 | 167.1 | 1161 | 208.9 | E ou F | 46.7 | 0.11 | s1 | y | y | d2
|  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.85 | 180 | Paron | 1602SEES | 2640 | 43 | 23.4 | No | 2015-11-12 | B2_s1_d0 | 0.75 | 7.7 | 17.1 | 687 | 54.2 | B2 | 19.4 | 0.05 | s1 | n | n | d0
|  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.85 | 180 | Paron | 1602SEES | -- | 46 | 23 | No | 2015-11-12 | B2_s1_d0 | 0.75 | 7.9 | 19.4 | 678 | 56.5 | B2 | 19.4 | 0.04 | s1 | n | n | d0
|  |  |  | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.82 | 180 | Paron | SW3800FR | -- | 51.3 | 26.8 | No | 2015-11-17 | B2_s2_d0 | 1.1 | 11.8 | 29.4 | 765 | 70.9 | B2 | 71.5 | 0.16 | s2 | n | n | d0
|  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 9.7 | 15 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 41.6 | 20.4 | No | 2015-12-02 | B2_s1_d0 | 0.75 | 8.6 | 19.6 | 777 | 49.1 | B2 | 24.5 | 0.04 | s1 | n | n | d0
|  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 10.2 | 15 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 43.4 | 21.1 | No | 2015-12-02 | B2_s1_d0 | 0.7 | 8.8 | 15.2 | 921 | 40.8 | B2 | 15.2 | 0.02 | s1 | n | n | d0
|  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.82 | 180 | Paron | SW3800FR | -- | 38 | 19 | No | 2015-12-03 | D_s2_d0 | 2.4 | 24.1 | 40.8 | 807 | 89.7 | D | 114.7 | 0.17 | s2 | n | n | d0
|  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.3 | 15 | Paron | XLPE+400FEIT+5300SEIT | -- | 41.3 | 21 | No | 2015-12-09 | B2_s1_d1 | 0.85 | 13 | 23 | 909 | 39.6 | B2 | 42.2 | 0.1 | s1 | y | n | d1
|  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.1 | 15 | Paron | XLPE+400FEIT+5300SEIT | -- | 42.8 | 21.2 | No | 2015-12-09 | C_s2_d2 | 1.3 | 18.5 | 33.9 | 903 | 59.3 | C | 55.5 | 0.12 | s2 | y | y | d2
TN_2015_0141 |  |  |  | DRAKA 2015 16 FO 10D TKT MOVISTAR | 12.7 | 12 | Vilanova | DRYTUBES1600SEES+1700SEES | 1847 | 61.8 | 16.9 | No | 2015-12-10 | D_s1_d1 | 2.75 | 47 | 61.4 | 1062 | 106.9 | D | 35.7 | 0.05 | s1 | y | n | d1
TN_2015_0142 |  |  |  | DRAKA 2015 16 FO 10D TKT MOVISTAR | 12.45 | 13 | Vilanova | DRYTUBES1600SEES+5300SEIT | 1966 | 58.3 | 19.3 | No | 2015-12-10 | E ou F_s2_d2 | 3.3 | 83.4 | 146.3 | 1230 | 157.8 | E ou F | 60 | 0.14 | s2 | n | y | d2
TN_2015_0143 |  |  |  | MK-HF06 KEVI 1X6 | 5.01 | 30 | Vilanova | LSOH | 1879 | 64.5 | 15 | No | 2015-12-10 | B2_s1_d0 | 0.75 | 2.9 | 12.8 | 519 | 78.5 | B2 | 4.1 | 0.02 | s1 | n | n | d0
DE16066 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.1 | 15 | Paron | SXLPE+0400FEIT+1602SEES | -- | 42.8 | 21.2 | No | 2015-12-14 | C_s2_d2 | 1.58 | 23 | 34.9 | 1020 | 55.4 | C | 53.6 | 0.12 | s2 | y | y | d2
DE16066 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.1 | 15 | Paron | SXLPE+0400FEIT+1602SEES | -- | 40.2 | 21 | No | 2015-12-14 | C_s2_d2 | 1.75 | 27.9 | 40.7 | 933 | 68.7 | C | 77.4 | 0.25 | s2 | y | y | d2
TN_2015_0144 |  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 10.26 | 15 | Vilanova | SXLPE+0400FEIT+1602SEES | 1958 | 69 | 12.4 | No | 2015-12-14 | B2_s1_d1 | 0.66 | 10.2 | 19.8 | 861 | 55.1 | B2 | 1.5 | 0.01 | s1 | y | n | d1
TN_2015_0145 |  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 9.6 | 15 | Vilanova | SXLPE+400FEIT+SW3800FR | 2231 | 59.7 | 13.3 | No | 2015-12-14 | B2_s1_d1 | 0.49 | 6.1 | 11.4 | 654 | 38.2 | B2 | 0 | 0 | s1 | y | n | d1
TN_2015_0146 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.4 | 15 | Vilanova | XLPE+400FEIT+SW3800FR | 2145 | 56.9 | 15 | No | 2015-12-14 | B2_s1_d0 | 0.5 | 9.8 | 22.3 | 801 | 52.9 | B2 | 31.4 | 0.08 | s1 | n | n | d0
TN_2015_0147 |  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 9.8 | 15 | Vilanova | SXLPE+0400FEIT+1602SEES | 2045 | 57 | 17.3 | No | 2015-12-16 | B2_s1_d0 | 0.97 | 12.4 | 26.8 | 837 | 54.9 | B2 | 24 | 0.05 | s1 | n | n | d0
|  | TN_2020_1984 |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.7 | 14 | Paron | LSOH | -- | 47.5 | 24 | No | 2015-12-16 | B2_s1_d1 | 0.8 | 13.7 | 23.1 | 795 | 51.1 | B2 | 40.7 | 0.11 | s1 | y | n | d1
|  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.2 | 15 | Paron | XLPE+TP0851+1602SEES | -- | 49 | 23.4 | No | 2015-12-16 | C_s2_d1 | 1.56 | 24.7 | 38.4 | 984 | 61.2 | C | 69.2 | 0.17 | s2 | y | n | d1
TN_2015_0148 |  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 9.54 | 15 | Vilanova | SXLPE+400FEIT+ECCOH5549 | 1971 | 66 | 16.7 | No | 2015-12-21 | B2_s1_d0 | 0.72 | 7.4 | 18 | 771 | 38.7 | B2 | 5.4 | 0.02 | s1 | n | n | d0
TN_2015_0149 |  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 9.65 | 15 | Vilanova | SXLPE+0400FEIT+5300SEIT | 2018 | 69.2 | 15.3 | No | 2015-12-21 | B2_s1_d0 | 0.62 | 6.4 | 10.6 | 807 | 35.8 | B2 | 0 | 0 | s1 | n | n | d0
16010002 |  |  |  | HO7ZZ-F- 3G1.5 | 9.88 | 15 | Paron | SV3600FR | -- | 38.9 | 16 | No | 2016-01-12 | D_s2_d2 | 2.14 | 22 | 35.9 | 858 | 66 | D | 81.5 | 0.14 | s2 | y | y | d2
TN_2016_0150 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.7 | 15 | Vilanova | 1602SEES+5300SEIT | 1744 | 45.7 | 12 | No | 2016-01-18 | B2_s1_d0 | 0.78 | 6.9 | 14.9 | 798 | 41 | B2 | 18.7 | 0.04 | s1 | n | n | d0
TN_2016_0151 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.6 | 15 | Vilanova | 1602SEES+16AASEES | 1689 | 42.1 | 14.1 | No | 2016-01-18 | B2_s1_d0 | 0.77 | 8.9 | 19.7 | 792 | 55.7 | B2 | 24.7 | 0.08 | s1 | n | n | d0
TN_2016_0152 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.5 | 15 | Vilanova | 1602SEES+16ABSEES | 1742 | 39.8 | 16 | No | 2016-01-18 | B2_s1_d0 | 0.76 | 9 | 18.4 | 774 | 51.4 | B2 | 20.6 | 0.05 | s1 | n | n | d0
16010004 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.8 | 14 | Paron | XLPE+400FEIT+41ALSEIT | -- | 24.3 | 19.7 | No | 2016-01-21 | C_s2_d2 | 1.1 | 19.6 | 35.4 | 1014 | 51.7 | C | 59.3 | 0.15 | s2 | y | y | d2
16010004 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.6 | 14 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 21.7 | 20.3 | No | 2016-01-21 | C_s1_d0 | 1.2 | 21.4 | 40 | 999 | 59.5 | C | 43.4 | 0.12 | s1 | n | n | d0
16010006 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.25 | 14 | Paron | SXLPE+0400FEIT+1602SEES | -- | 36.9 | 22 | No | 2016-01-25 | D_s1_d2 | 2.75 | 40.1 | 62.7 | 1494 | 77.6 | D | 46.6 | 0.09 | s1 | y | y | d2
TN_2016_0153 |  |  |  | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.79 | 180 | Vilanova | 5300SEIT | 1478 | 73.3 | 12.8 | No | 2016-01-27 | B2_s1_d0 | 0.75 | 5.9 | 12.5 | 741 | 45.1 | B2 | 3.6 | 0.02 | s1 | n | n | d0
TN_2016_0154 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.68 | 195 | Vilanova | SW3800FR | 1567 | 15.3 | 18 | No | 2016-01-27 | B2_s2_d0 | 1.1 | 7.7 | 23.2 | 645 | 68.6 | B2 | 95.4 | 0.17 | s2 | n | n | d0
TN_2016_0155 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.76 | 195 | Vilanova | PESKIN*0.1-0.15MM+53AESEIT | 1788 | 18.2 | 18.9 | No | 2016-01-27 | C_s2_d2 | 1.62 | 17.3 | 41.4 | 717 | 103.7 | C | 65.2 | 0.13 | s2 | n | y | d2
16010007 |  |  |  | DRAKA 2015 16 FO 10D TKT MOVISTAR | 12.7 | 12 | Paron | DRYTUBES1600SEES+1700SEES | 1805 | 40 | 22.8 | No | 2016-01-27 | D_s2_d2 | 3.3 | 69.5 | 116.5 | 1398 | 116.5 | D | 70 | 0.22 | s2 | y | y | d2
16010008 |  |  |  | DRAKA 2015 16 FO 10D TKT MOVISTAR | 12.7 | 12 | Paron | DRYTUBES1600SEES+1600SEES | 1607 | 40 | 22.5 | No | 2016-01-27 | E ou F_s2_d2 | 3.3 | 70.8 | 129.1 | 1134 | 173 | E ou F | 102 | 0.25 | s2 | y | y | d2
TN_2016_0156 |  |  |  | DRAKA 2015 16 FO 10D TKT MOVISTAR | 12.5 | 12 | Vilanova | DRYTUBES1600SEES+5300SEIT | 1942 | 59.3 | 11.6 | No | 2016-01-31 | D_s1_d1 | 3.3 | 61.2 | 89.7 | 1422 | 110.5 | D | 35.4 | 0.07 | s1 | y | n | d1
TN_2016_0157 |  |  |  | DRAKA 2015 16 FO 10D TKT MOVISTAR | 12.7 | 12 | Vilanova | DRYTUBES1600SEES+1700SEES | 1847 | 53.7 | 14.9 | No | 2016-01-31 | D_s1_d2 | 1.9 | 30.9 | 44.5 | 951 | 87 | D | 23.5 | 0.05 | s1 | n | y | d2
TN_2015_0158 |  |  |  | DRAKA 2015 16 FO 10D TKT MOVISTAR | 12.6 | 12 | Vilanova | DRYTUBES1600SEES+1600SEES | 1802 | 49.1 | 17.2 | No | 2016-01-31 | E ou F_s1_d2 | 3.3 | 98 | 175.9 | 1149 | 226.9 | E ou F | 40.1 | 0.11 | s1 | n | y | d2
TN_2016_0159 |  |  |  | TKT 128F TELEFONICA DRY TUBES | 17.95 | 8 | Vilanova | DRYTUBES1700SEES+1700SEES | 1633 | 44.3 | 18.2 | No | 2016-02-10 | D_s1_d2 | 1.85 | 39 | 54.4 | 1500 | 75.8 | D | 36.3 | 0.12 | s1 | n | y | d2
TN_2016_0160 |  |  |  | TKT 128F TELEFONICA DRY TUBES | 17.7 | 8 | Vilanova | DRYTUBES1600SEES+1600SEES | 1689 | 38.6 | 20.3 | No | 2016-02-10 | D_s2_d2 | 1.95 | 44.7 | 69.4 | 1482 | 84.1 | D | 51.7 | 0.09 | s2 | n | y | d2
16020002 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 3.31 | 135 | Paron | 54AASEIT | -- | 37.7 | 21.7 | No | 2016-02-10 | B2_s1_d0 | 0.7 | 9.2 | 17.9 | 780 | 90.6 | B2 | 14 | 0.04 | s1 | n | n | d0
16020003 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X10 | 6.6 | 21 | Paron | 54AASEIT | -- | 43.7 | 19.8 | No | 2016-02-10 | B2_s1_d0 | 1.12 | 8.5 | 24.5 | 657 | 79.7 | B2 | 29.7 | 0.14 | s1 | n | n | d0
TN_2016_0161 |  |  |  | FR-N1 X1G1-U- 3G1.5 MM² | 10.15 | 15 | Vilanova | SXLPE+0400FEIT+5300SEIT | 1841 | 46.7 | 17 | No | 2016-02-10 | B2_s1_d0 | 0.49 | 5.4 | 10.8 | 939 | 29 | B2 | 7.7 | 0.04 | s1 | n | n | d0
16020005 |  |  |  | TKT 128F TELEFONICA DRY TUBES | 18 | 8 | Paron | DRYTUBES1700SEES+1700SEES | -- | 34.1 | 22 | No | 2016-02-12 | D_s2_d0 | 1.9 | 30.7 | 38.8 | 1149 | 64.7 | D | 59.3 | 0.1 | s2 | n | n | d0
16020006 |  |  |  | TKT 128F TELEFONICA DRY TUBES | 17.8 | 8 | Paron | DRYTUBES1600SEES+1600SEES | -- | 38.2 | 21 | No | 2016-02-12 | D_s2_d0 | 2.2 | 33.2 | 42.3 | 1185 | 67.2 | D | 70.2 | 0.12 | s2 | n | n | d0
TN_2016_0162 |  |  |  | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.75 | 195 | Vilanova | 1602SEES | 1786 | 57.6 | 15.1 | No | 2016-02-14 | B2_s1_d0 | 0.69 | 6.2 | 10.5 | 798 | 42.5 | B2 | 5.5 | 0.03 | s1 | n | n | d0
TN_2016_0163 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.1 | 15 | Vilanova | SXLPE+0400FEIT+1602SEES | 2142 | 41.6 | 17.3 | No | 2016-02-14 | C_s1_d1 | 1.67 | 21.6 | 36.2 | 849 | 67.5 | C | 37.7 | 0.09 | s1 | y | n | d1
TN_2016_0164 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.1 | 15 | Vilanova | SXLPE+0400FEIT+1602SEES | 2180 | 36.4 | 19.2 | No | 2016-02-14 | C_s1_d2 | 1.83 | 27.4 | 45.7 | 897 | 81.7 | C | 43.8 | 0.1 | s1 | n | y | d2
TN_2016_0165 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.07 | 15 | Vilanova | SXLPE+0400FEIT+ECCOH5549 | 2241 | 35.7 | 11.5 | No | 2016-02-18 | B2_s1_d1 | 0.47 | 7 | 17.1 | 747 | 46 | B2 | 10.8 | 0.03 | s1 | y | n | d1
TN_2016_0166 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.07 | 15 | Vilanova | SXLPE+0400FEIT+ECCOH5549 | 2149 | 33.1 | 13.1 | No | 2016-02-18 | B2_s1_d0 | 0.72 | 8.9 | 22.2 | 702 | 55.3 | B2 | 10.5 | 0.03 | s1 | n | n | d0
TN_2016_0167 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.91 | 14 | Vilanova | SXLPE+0400FEIT+5300SEIT | 2082 | 30.9 | 14.1 | No | 2016-02-18 | C_s1_d1 | 0.96 | 16.2 | 32.6 | 912 | 55.6 | C | 29.6 | 0.07 | s1 | y | n | d1
TN_2016_0172 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10 | 15 | Vilanova | SXLPE+1420FEES+16AASEES | 1667 | 50.2 | 16.2 | No | 2016-02-23 | B2_s1_d1 | 0.47 | 9.9 | 27.6 | 696 | 69.9 | B2 | 13.3 | 0.04 | s1 | y | n | d1
TN_2016_0173 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.5 | 15 | Vilanova | SXLPE+1420FEES+16ABSEES | 1702 | 42.2 | 18.4 | No | 2016-02-23 | B2_s1_d1 | 0.92 | 11.5 | 25.2 | 693 | 64.7 | B2 | 33.1 | 0.05 | s1 | y | n | d1
TN_2016_0174 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.1 | 17 | Vilanova | SXLPE-FR+16ABSEES | 1598 | 31.8 | 20.4 | No | 2016-02-23 | D_s2_d2 | 3.3 | 38.8 | 75.3 | 759 | 164.9 | D | 86.7 | 0.19 | s2 | n | y | d2
TN_2016_0175 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.1 | 17 | Vilanova | SXLPE-FR+16ABSEES | 1659 | 51.7 | 15.5 | No | 2016-02-28 | D_s2_d2 | 3.3 | 59.1 | 116.8 | 1254 | 129.4 | D | 69.8 | 0.28 | s2 | n | y | d2
TN_2016_0176 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 1X120 | 18.85 | 8 | Vilanova | SXLPE_EXPANSO+1643SEES+5%LLDPE | 1749 | 61.7 | 13.2 | No | 2016-02-28 | E ou F_s2_d2 | 3.3 | 76.5 | 153.8 | 1080 | 258.8 | E ou F | 67.5 | 0.19 | s2 | n | y | d2
16030001 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.68 | 15 | Paron | ID3600+5300SEIT | -- | 28.8 | 20.5 | No | 2016-03-01 | C_s1_d2 | 1.38 | 19.7 | 44.5 | 822 | 112.9 | C | 35.5 | 0.07 | s1 | y | y | d2
TN_2016_0178 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10 | 15 | Vilanova | SXLPE+1420FEES+16AASEES | -- | 42.8 | 13.7 | No | 2016-03-07 | B2_s1_d0 | 0.72 | 8.8 | 22.8 | 717 | 62 | B2 | 27.6 | 0.05 | s1 | n | n | d0
TN_2016_0181 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10 | 15 | Vilanova | SXLPE+1420FEES+16AASEES | 2105 | 39.1 | 15.6 | No | 2016-03-07 | B2_s1_d0 | 0.53 | 9.1 | 20.7 | 828 | 50.9 | B2 | 16.7 | 0.04 | s1 | n | n | d0
TN_2016_0182 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.5 | 15 | Vilanova | SXLPE+1420FEES+16ABSEES | 2116 | 36.7 | 17.6 | No | 2016-03-07 | B2_s1_d2 | 0.8 | 9.6 | 20.8 | 687 | 57.8 | B2 | 14.8 | 0.04 | s1 | n | y | d2
TN_2016_0185 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.5 | 15 | Vilanova | SXLPE+1420FEES+16ABSEES | 2185 | 65.6 | 13.6 | No | 2016-03-18 | B2_s1_d2 | 1.12 | 11.9 | 27.1 | 816 | 56.6 | B2 | 25 | 0.05 | s1 | n | y | d2
TN_2016_0186 |  |  |  | AFUMEX EASY RZ 0.6/1.0KV 3G1.5 | 7.6 | 19 | Vilanova | SXLPE+6000SEES | 1987 | 59.1 | 16.1 | No | 2016-03-18 | D_s2_d2 | 3.3 | 69.8 | 320.2 | 726 | 753.2 | D | 59.7 | 0.34 | s2 | n | y | d2
16030013 |  |  |  | FR-N1X1G1 1*16 MM² | 10.6 | 14 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 41.7 | 18.7 | No | 2016-03-21 | B2_s1_d2 | 0.4 | 3.8 | 6.8 | 558 | 27.2 | B2 | 4.5 | 0.01 | s1 | y | y | d2
16030014 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.3 | 15 | Paron | SXLPE+1420FEES+16ABSEES | 1252 | 35.5 | 22.3 | No | 2016-02-23 | B2_s1_d2 | 0.7 | 9.8 | 22.3 | 705 | 58.9 | B2 | 13.1 | 0.04 | s1 | y | y | d2
TN_2016_0187 |  |  |  | AL-HEPRZ1(S) 1X240MM2 12/20KV | 38.3 | 5 | Vilanova | HEPR+6000SEES | -- | 75.1 | 12.4 | No | 2016-04-01 | D_s1_d2 | 2.1 | 40.7 | 92.2 | 1500 | 76.8 | D | 12.7 | 0.05 | s1 | n | y | d2
TN_2016_0188 |  |  |  | AL-HEPRZ1(S) 1X240MM2 12/20KV | 38.3 | 5 | Vilanova | HEPR+6000SEES | -- | 70.4 | 13.8 | No | 2016-04-01 | D_s1_d2 | 1.75 | 33.5 | 78.3 | 1497 | 65.4 | D | 12.1 | 0.04 | s1 | n | y | d2
16030015 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.5 | 15 | Paron | SXLPE+1420FEES+16AASEES | 1283 | 32.9 | 23 | No | 2016-03-23 | B2_s1_d2 | 0.7 | 9.2 | 22.3 | 726 | 53.7 | B2 | 13.4 | 0.03 | s1 | y | y | d2
TN_2016_0189 |  |  |  | AFUMEX HT EN 50382-2 150C 3.6_6.0KV 1X185 | 24.1 | 7 | Vilanova | SILICONAWACKER420_70 | -- | 68.7 | 15.9 | No | 2016-04-06 | B2_s1_d0 | 0.34 | 1.2 | 3 | 600 | 0 | B2 | 2.3 | 0.01 | s1 | n | n | d0
TN_2016_0190 |  |  |  | AFUMEX HT EN 50382 150C 1.8/3KV 1X120MM | 20.7 | 7 | Vilanova | SILICONAWACKER420_70 | -- | 64.8 | 17.5 | No | 2016-04-06 | B2_s1_d0 | 0.25 | 4.1 | 5 | 1050 | 0 | B2 | 8.14 | 0.01 | s1 | n | n | d0
TN_2016_0191 |  |  |  | AFUMEX DA 1X70MM | 18.4 | 8 | Vilanova | SXLPE+1643SEES | -- | 60.6 | 18.5 | No | 2016-04-06 | D_s1_d2 | 2.5 | 33.6 | 83.6 | 1500 | 69.7 | D | 21.8 | 0.06 | s1 | y | y | d2
TN_2016_0192 |  |  | 131030Z | RHZ1-OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44.25 | 5 | Vilanova | XLPE+1420FEES+6000SEES | -- | 72.6 | 16.9 | No | 2016-04-11 | B2_s1_d2 | 0.83 | 6.6 | 8.7 | 999 | 24.4 | B2 | 11.3 | 0.04 | s1 | y | y | d2
TN_2016_0193 |  |  | 131030Z | RHZ1-OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44.25 | 5 | Vilanova | XLPE+1420FEES+6000SEES | -- | 67.3 | 17.8 | No | 2016-04-12 | B2_s1_d2 | 0.9 | 10.3 | 12 | 1116 | 31.7 | B2 | 0.3 | 0.005 | s1 | y | y | d2
TN_2016_0194 |  |  | 131030Z | RHZ1-OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44.25 | 5 | Vilanova | XLPE+1420FEES+6000SEES | -- | 64.7 | 19.1 | No | 2016-04-12 | B2_s1_d2 | 0.96 | 12.2 | 14.9 | 1068 | 38.4 | B2 | 15.9 | 0.04 | s1 | y | y | d2
TN_2016_0193 |  |  | 131030Z | RHZ1-OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44.45 | 5 | CEIS | XLPE+1420FEES+6000SEES | -- | 50 | 14.66 | No | 2017-02-23 | C_s1_d2 | 1.05 | 17.9 | 24.9 | 1500 | 44.2 | C | 3.2 | 0.01 | s1 | y | y | d2
TN_2016_0194 |  |  | 131030Z | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44.45 | 5 | CEIS | XLPE+1420FEES+6000SEES | -- | 55 | 12.92 | No | 2017-02-27 | B2_s1_d2 | 0.95 | 7.7 | 10.2 | 804 | 22.3 | B2 | 8 | 0.02 | s1 | y | y | d2
TN_2016_0195 |  |  |  | HN07 V-K RETOX 1X240 PRYSMIAN (G) IEMMEQU ECOLOGY LINE PH FREE | 24.8 | 7 | Vilanova | PVC2600IPIT+SKIN2200GPIT | -- | 56.1 | 19.1 | No | 2016-04-19 | B2_s2_d0 | 0.87 | 7.1 | 20.6 | 648 | 86.9 | B2 | 227.6 | 0.49 | s2 | n | n | d0
TN_2016_0196 |  |  |  | HN07 V-K RETOX 1X240 PRYSMIAN (G) IEMMEQU ECOLOGY LINE PH FREE | 24.8 | 7 | Vilanova | PVC2600IPIT+SKIN2200GPIT | -- | 48.4 | 19.2 | No | 2016-04-19 | B2_s2_d0 | 0.8 | 7.5 | 20.8 | 636 | 101.5 | B2 | 233.7 | 0.5 | s2 | n | n | d0
TN_2016_0197 |  |  |  | DRAKA 2015 8FO 10D KT MOVISTAR (SECO) | 6.7 | 21 | Vilanova | DRYTUBES1500SEES | -- | 39.7 | 21.6 | No | 2016-04-19 | D_s2_d2 | 3.3 | 55.6 | 242 | 642 | 738.4 | D | 58.8 | 0.21 | s2 | y | y | d2
TN_2016_0198 |  |  |  | HN07 V-K RETOX 1X240 PRYSMIAN (G) IEMMEQU ECOLOGY LINE PH FREE | 24.8 | 7 | Vilanova | PVC2600IPIT+SKIN2200GPIT | -- | 68.1 | 14.3 | No | 2016-04-24 | B2_s2_d0 | 0.77 | 8.2 | 20.1 | 594 | 89.1 | B2 | 202.5 | 0.52 | s2 | n | n | d0
TN_2016_0199 |  |  |  | HN07V-K RETOX 1X10 PRYSMIAN (S) IEMMEQU ECOLOGY LINE PH FREE | 6.2 | 25 | Vilanova | PVC2600IPIT+SKIN2200GPIT | -- | 61.1 | 16.5 | No | 2016-04-24 | C_s2_d0 | 1.12 | 4.8 | 25.8 | 408 | 270.4 | C | 110.4 | 0.84 | s2 | n | n | d0
TN_2016_0200 |  |  |  | HN07V-K RETOX 1X10 PRYSMIAN (S) IEMMEQU ECOLOGY LINE PH FREE | 6.2 | 25 | Vilanova | PVC2600IPIT+SKIN2200GPIT | -- | 55.4 | 18.1 | No | 2016-04-24 | C_s2_d0 | 1.12 | 4.1 | 28.6 | 399 | 296.2 | C | 107.2 | 0.79 | s2 | n | n | d0
TN_2016_0201 |  |  |  | AL-VOLTALENE XZ1(S)1X240K 0.6/1.0KV | 24.15 | 7 | Vilanova | SXLPE+6000SEES | -- | 74.2 | 15.6 | No | 2016-04-28 | D_s1_d2 | 1.8 | 38.5 | 97.2 | 1500 | 89.1 | D | 20.7 | 0.11 | s1 | y | y | d2
TN_2016_0202 |  |  |  | DRAKA 2016 16 FO 10D 7A2 INT-V MOVISTAR 139911 | 7.5 | 19 | Vilanova | LSOH | -- | 71.2 | 16.4 | No | 2016-04-28 | D_s2_d2 | 3.3 | 43.3 | 124.8 | 870 | 219.2 | D | 104.6 | 0.25 | s2 | y | y | d2
TN_2016_0203 |  |  |  | DRAKA 2015 8FO 10D KT MOVISTAR (CON GRASA | 6.9 | 21 | Vilanova | JELLYINTUBES1500SEES | -- | 70.6 | 16.7 | No | 2016-04-28 | E ou F_s2_d2 | 3.3 | 70.4 | 322.7 | 627 | 987 | E ou F | 70.4 | 0.19 | s2 | y | y | d2
TN_2016_0204 |  |  |  | HN07V-K RETOX 1X10 PRYSMIAN (S) IEMMEQU ECOLOGY LINE PH FREE | 6.2 | 25 | Vilanova | PVC2600IPIT+SKIN2200GPIT | -- | 75 | 17.8 | No | 2016-05-10 | C_s2_d0 | 1 | 3.5 | 22.1 | 426 | 184 | C | 79 | 0.59 | s2 | n | n | d0
TN_2016_0205 |  |  |  | FG7R 0.6/1KV G-SETTE PIU 1X240 PRYSMIAN (G) 2015 ECOLOGY LINE | 27.6 | 6 | Vilanova | SXLPE+2700SPIT | -- | 67.7 | 19.9 | No | 2016-05-10 | D_s3_d2 | 3 | 43.8 | 130.9 | 1500 | 109.1 | D | 930.2 | 3.27 | s3 | y | y | d2
TN_2016_0206 |  |  |  | FG7R 0.6/1KV G-SETTE PIU 1X240 PRYSMIAN (G) 2015 ECOLOGY LINE | 27.6 | 6 | Vilanova | SXLPE+2700SPIT | -- | 57.4 | 23.7 | No | 2016-05-18 | D_s3_d2 | 3 | 54.3 | 137.1 | 1500 | 114.2 | D | 1122.7 | 2.48 | s3 | y | y | d2
TN_2016_0207 |  |  |  | AL-VOLTALENE XZ1(S)1X25K 0.6/1.0KV | 10.23 | 15 | Vilanova | SXLPE+6000SEES | -- | 68.1 | 19.5 | No | 2016-05-18 | E ou F_s2_d2 | 3.3 | 97.4 | 467.5 | 930 | 742.1 | E ou F | 96.5 | 0.37 | s2 | y | y | d2
TN_2016_0208 |  |  |  | AL-VOLTALENE XZ1(S)1X25K 0.6/1.0KV | 10.23 | 15 | Vilanova | SXLPE+6000SEES | -- | 59.9 | 22.5 | No | 2016-05-18 | E ou F_s2_d2 | 3.3 | 96.6 | 480.4 | 897 | 807.8 | E ou F | 102.9 | 0.4 | s2 | y | y | d2
TN_2016_0209 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.15 | 15 | Vilanova | SXLPE+1420FEES+4110SEES | -- | 62.7 | 21.3 | No | 2016-05-20 | D_s2_d2 | 1.72 | 30.2 | 54.1 | 984 | 81.7 | D | 77.6 | 0.15 | s2 | y | y | d2
TN_2016_0210 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.3 | 17 | Vilanova | SXLPE+4110SEES | -- | 55.7 | 23.7 | No | 2016-05-20 | D_s1_d2 | 2.2 | 36.7 | 60.2 | 798 | 141.4 | D | 49.7 | 0.09 | s1 | y | y | d2
TN_2016_0214 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.1 | 15 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 60.4 | 23.4 | No | 2016-05-25 | B2_s1_d1 | 0.8 | 10.3 | 19.2 | 816 | 43.8 | B2 | 32.1 | 0.06 | s1 | y | n | d1
TN_2016_0215 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.3 | 15 | Vilanova | SXLPE+0400FEIT+4110SEES | -- | 66.2 | 21.4 | No | 2016-05-25 | D_s2_d2 | 1.34 | 30.4 | 48.1 | 1071 | 90.1 | D | 80.8 | 0.21 | s2 | n | y | d2
TN_2016_0216 |  |  |  | FG7R 0.6/1KV G-SETTE PIU 1X240 PRYSMIAN (G) 2015 ECOLOGY LINE | 27.6 | 6 | Vilanova | SXLPE+2700SPIT | -- | 55.6 | 24.3 | No | 2016-05-25 | D_s3_d2 | 3.3 | 59.7 | 159.9 | 1497 | 133.6 | D | 1169.6 | 2.85 | s3 | y | y | d2
TN_2016_0217 |  |  |  | FG7OR 0.6/1KV G-SETTE PIU 2X35 PRYSMIAN (G) 2014 ECOLOGY LINE | 23.3 | 7 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 55.9 | 19.3 | No | 2016-05-29 | C_s3_d2 | 0.86 | 16.7 | 26.8 | 1374 | 50.1 | C | 409.4 | 0.56 | s3 | y | y | d2
TN_2016_0218 |  |  |  | FG7OR 0.6/1KV G-SETTE PIU 2X35 PRYSMIAN (G) 2014 ECOLOGY LINE | 23.3 | 7 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 46.1 | 22.1 | No | 2016-05-29 | C_s2_d2 | 0.79 | 20.3 | 38 | 1374 | 60.5 | C | 366.2 | 0.55 | s2 | y | y | d2
TN_2016_0219 |  |  |  | FG7OR 0.6/1KV G-SETTE PIU 2X35 PRYSMIAN (G) 2014 ECOLOGY LINE | 23.3 | 7 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 40.5 | 24.2 | No | 2016-05-29 | B2_s2_d2 | 0.75 | 7.4 | 19.6 | 1389 | 18.1 | B2 | 363.2 | 0.54 | s2 | y | y | d2
16060002 |  |  |  | FR-N1X1G1 1*16 MM² | 10.4 | 15 | Paron | SXLPE+0400FEIT+16ABSEES | -- | 58.8 | 22.9 | No | 2016-06-01 | B2_s1_d0 | 0.6 | 6.9 | 13 | 906 | 27.8 | B2 | 11.8 | 0.02 | s1 | n | n | d0
16060001 |  |  |  | FR-N1X1G1 1*16 MM² | 10 | 15 | Paron | SXLPE+0400FEIT+16AASEES | -- | 62.2 | 22.3 | No | 2016-06-01 | B2_s1_d2 | 0.7 | 6.4 | 14 | 870 | 27.6 | B2 | 11.4 | 0.02 | s1 | y | y | d2
TN_2016_0220 |  |  |  | FG7OR 0.6/1KV G-SETTE PIU 5G1.5 PRYSMIAN (G) 2015 ECOLOGY LINE | 12.96 | 12 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 42.9 | 21.5 | No | 2016-06-01 | D_s3_d1 | 3.3 | 40.8 | 58.1 | 1026 | 103.6 | D | 1051.4 | 1.46 | s3 | y | n | d1
TN_2016_0221 |  |  |  | FG7OR 0.6/1KV G-SETTE PIU 5G1.5 PRYSMIAN (G) 2015 ECOLOGY LINE | 12.96 | 12 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 38.8 | 25.1 | No | 2016-06-01 | D_s3_d1 | 3.3 | 53.5 | 130.9 | 1491 | 110.9 | D | 1473.3 | 2.59 | s3 | y | n | d1
TN_2016_0223 |  |  |  | FG7OR 0.6/1KV G-SETTE PIU 3X1.5 PRYSMIAN (G) 2015 ECOLOGY LINE | 11.1 | 14 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 55.5 | 23.7 | No | 2016-06-07 | C_s2_d0 | 1.22 | 13.4 | 32.3 | 780 | 87.6 | C | 399.4 | 1.1 | s2 | n | n | d0
TN_2016_0224 |  |  |  | FG7OR 0.6/1KV G-SETTE PIU 3X1.5 PRYSMIAN (G) 2015 ECOLOGY LINE | 11.1 | 14 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 51.5 | 25.9 | No | 2016-06-07 | C_s3_d0 | 1.19 | 15.7 | 34.5 | 618 | 109.5 | C | 440.6 | 1.1 | s3 | n | n | d0
TN_2016_0225 |  |  |  | FG7OR 0.6/1KV G-SETTE PIU 3X1.5 PRYSMIAN (G) 2015 ECOLOGY LINE | 11.1 | 14 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 47.1 | 27.1 | No | 2016-06-07 | C_s3_d0 | 1.4 | 18.2 | 33.7 | 633 | 101.1 | C | 496.7 | 1.12 | s3 | n | n | d0
16060005 |  |  |  | FR-N1X1G1 1*16 MM² | 10 | 15 | Paron | SXLPE+0400FEIT+16AASEES | -- | 61.8 | 23.9 | No | 2016-06-08 | B2_s1_d2 | 0.65 | 7 | 13.6 | 825 | 32.8 | B2 | 13.4 | 0.02 | s1 | y | y | d2
TN_2016_0226 |  |  |  | FG7OR 0.6/1KV G-SETTE PIU 7X1.5 PRYSMIAN (G) 2015 ECOLOGY LINE | 14.7 | 10 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 52.6 | 24.6 | No | 2016-06-09 | D_s3_d0 | 2.05 | 29.2 | 41.5 | 978 | 78.1 | D | 605 | 0.82 | s3 | n | n | d0
TN_2016_0227 |  |  |  | FG7OR 0.6/1KV G-SETTE PIU 7X1.5 PRYSMIAN (G) 2015 ECOLOGY LINE | 14.7 | 10 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 47.3 | 26.6 | No | 2016-06-09 | D_s3_d0 | 1.95 | 31.8 | 42.4 | 1239 | 78 | D | 573.2 | 0.78 | s3 | n | n | d0
TN_2016_0228 |  |  |  | FG7OR 0.6/1KV G-SETTE PIU 7X1.5 PRYSMIAN (G) 2015 ECOLOGY LINE | 14.7 | 10 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 43.4 | 27.8 | No | 2016-06-09 | C_s3_d0 | 1.75 | 26.2 | 45.6 | 858 | 81.9 | C | 532.9 | 0.84 | s3 | n | n | d0
TN_2016_0229 |  |  |  | AL-AFUMEX RRFWZ1-AS 2X35 | 35 | 5 | Vilanova | SXLPE+BEDDINGSXLPE+STEELTAPECORRUGATED+6000SEES | -- | 62.2 | 24.3 | No | 2016-06-15 | E ou F_s2_d2 | 3.3 | 77.6 | 314 | 1500 | 261.6 | E ou F | 75 | 0.3 | s2 | y | y | d2
16060007 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.3 | 15 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 56.7 | 22.7 | No | 2016-06-16 | B2_s1_d1 | 0.7 | 8.4 | 14.8 | 852 | 31.5 | B2 | 17.8 | 0.03 | s1 | y | n | d1
16060008 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.3 | 15 | Paron | SXLPE+1420FEES+4110SEES | -- | 54.7 | 23 | No | 2016-06-16 | C_s2_d2 | 1.56 | 24.7 | 45.1 | 1050 | 61.2 | C | 124.3 | 0.27 | s2 | y | y | d2
16060009 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.3 | 17 | Paron | SXLPE+4110SEES | -- | 60.1 | 22.2 | No | 2016-06-17 | E ou F_s2_d2 | 3.3 | 76.1 | 129.3 | 1374 | 214.7 | E ou F | 161.3 | 0.37 | s2 | y | y | d2
16060012 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.7 | 15 | Paron | GFR325+5300SEIT | -- | 59 | 28 | No | 2016-06-24 | B2_s1_d2 | 0.85 | 11.4 | 17.5 | 999 | 63 | B2 | 37.5 | 0.07 | s1 | y | y | d2
16060013 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.5 | 15 | Paron | GFR325+5300SEIT | -- | 63.6 | 26 | No | 2016-06-24 | B2_s2_d2 | 0.9 | 12.3 | 20.5 | 975 | 48.6 | B2 | 57.3 | 0.14 | s2 | y | y | d2
TN_2016_0230 |  |  |  | HO7V-K SPEEDY FLAM EASY LINE 1X2.5MM | 3.4 | 120 | Vilanova | PVC2600IPIT+SKIN2200GPIT | -- | 61.3 | 25 | No | 2016-06-27 | D_s2_d0 | 1.3 | 10.4 | 46.2 | 438 | 353.8 | D | 267.8 | 1.37 | s2 | n | n | d0
TN_2016_0231 |  |  |  | HO7V-K SPEEDY FLAM EASY LINE 1X2.5MM | 3.4 | 120 | Vilanova | PVC2600IPIT+SKIN2200GPIT | -- | 56.4 | 26.2 | No | 2016-06-27 | C_s2_d0 | 1.29 | 10.7 | 31.9 | 441 | 244.1 | C | 219.4 | 1.01 | s2 | n | n | d0
TN_2016_0232 |  |  |  | HO7V-K SPEEDY FLAM EASY LINE 1X2.5MM | 3.4 | 120 | Vilanova | PVC2600IPIT+SKIN2200GPIT | -- | 51.9 | 27.2 | No | 2016-06-27 | C_s2_d0 | 1.17 | 6.4 | 29.4 | 453 | 230 | C | 198 | 0.92 | s2 | n | n | d0
TN_2016_0233 |  |  |  | FROR 450/750 FLEXI PIU 3G2.5 PRYSMIAN (G) 2016 ECOLOGY LINE | 10.1 | 15 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 59.9 | 26.6 | No | 2016-07-04 | B2_s2_d0 | 1.18 | 11.6 | 29 | 519 | 137.2 | B2 | 337.5 | 1.29 | s2 | n | n | d0
TN_2016_0234 |  |  |  | FROR 450/750 FLEXI PIU 3G2.5 PRYSMIAN (G) 2016 ECOLOGY LINE | 10.1 | 15 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 52.9 | 27.6 | No | 2016-07-04 | B2_s2_d0 | 0.86 | 6 | 22.8 | 474 | 133.9 | B2 | 249 | 1.03 | s2 | n | n | d0
TN_2016_0235 |  |  |  | FROR 450/750 FLEXI PIU 2X6 PRYSMIAN (G) 2016 ECOLOGY LINE | 11.85 | 13 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 56.3 | 28.5 | No | 2016-07-04 | C_s3_d0 | 1.25 | 11.3 | 33.8 | 561 | 140.2 | C | 488.9 | 1.49 | s3 | n | n | d0
TN_2016_0236 |  |  |  | DRAKA 2016 6FO G652D - 42SCRAP CPR TEST VERSION 1 | 15.2 | 10 | Vilanova | DRYPBTTUBESANDAFIRSTJACKETWITHBEDDINGCOMPOUND0400FEIT;SECONDJACKET1602N | -- | 68.4 | 27.5 | No | 2016-07-07 | B2_s1_d0 | 0.6 | 9.9 | 15 | 810 | 39.5 | B2 | 26.5 | 0.04 | s1 | n | n | d0
TN_2016_0237 |  |  |  | DRAKA 2016 6FO G652D - 42SCRAP CPR TEST VERSION 2 | 16 | 9 | Vilanova | DRYPBTTUBESANDAFIRSTJACKETWITHCERAMIFIABLECOMPOUND57AAFEIT;SECONDJACKET1602N | -- | 65.5 | 29 | No | 2016-07-07 | D_s2_d1 | 2.12 | 38.2 | 52.4 | 945 | 101.1 | D | 67.9 | 0.09 | s2 | y | n | d1
TN_2016_0238 |  |  |  | DRAKA 2016 6FO G652D - 42SCRAP CPR TEST VERSION 3 | 15.5 | 9 | Vilanova | DRYHFFR-LSTUBESANDAFIRSTJACKETWITHCERAMIFIABLECOMPOUND57AAFEIT;SECONDJACKET1602N | -- | 60.2 | 29.8 | No | 2016-07-07 | B2_s1_d0 | 0.86 | 13 | 22.8 | 885 | 39.8 | B2 | 21.2 | 0.03 | s1 | n | n | d0
TN_2016_0239 |  |  |  | DRAKA 2016 6FO G652D - 42SCRAP CPR TEST VERSION 1 | 15.2 | 10 | Vilanova | DRYPBTTUBESANDAFIRSTJACKETWITHBEDDINGCOMPOUND0400FEIT;SECONDJACKET1602N | -- | 64.5 | 26.9 | No | 2016-07-12 | B2_s2_d0 | 0.56 | 9 | 13.8 | 729 | 37.9 | B2 | 84.5 | 0.1 | s2 | n | n | d0
TN_2016_0240 |  |  |  | DRAKA 2016 6FO G652D - 42SCRAP CPR TEST VERSION 2 | 16 | 9 | Vilanova | DRYPBTTUBESANDAFIRSTJACKETWITHCERAMIFIABLECOMPOUND57AAFEIT;SECONDJACKET1602N | -- | 57.3 | 28 | No | 2016-07-12 | C_s2_d0 | 1.55 | 22.1 | 34.8 | 864 | 76.6 | C | 50.3 | 0.09 | s2 | n | n | d0
TN_2016_0241 |  |  |  | DRAKA 2016 6FO G652D - 42SCRAP CPR TEST VERSION 3 | 15.5 | 9 | Vilanova | DRYHFFR-LSTUBESANDAFIRSTJACKETWITHCERAMIFIABLECOMPOUND57AAFEIT;SECONDJACKET1602N | -- | 54 | 29.2 | No | 2016-07-12 | B2_s1_d0 | 0.74 | 14.6 | 23.7 | 825 | 53.1 | B2 | 12.8 | 0.04 | s1 | n | n | d0
TN_2016_0242 |  |  |  | FROR 450/750 FLEXI PIU 2X6 PRYSMIAN (G) 2016 ECOLOGY LINE | 11.86 | 13 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 59.8 | 26.1 | No | 2016-07-19 | C_s3_d0 | 1.27 | 12.9 | 37.1 | 570 | 142.3 | C | 471.1 | 1.57 | s3 | n | n | d0
TN_2016_0243 |  |  |  | FROR 450/750 FLEXI PIU 2X6 PRYSMIAN (G) 2016 ECOLOGY LINE | 11.86 | 13 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 48.3 | 28.2 | No | 2016-07-19 | C_s3_d0 | 1.6 | 20.1 | 49.1 | 621 | 163.7 | C | 517.8 | 1.59 | s3 | n | n | d0
TN_2016_0244 |  |  |  | FROR 450/750 FLEXI PIU 5G1.5 PRYSMIAN (G) 2016 ECOLOGY LINE | 10 | 15 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 44.3 | 29.6 | No | 2016-07-19 | C_s3_d0 | 1.32 | 10.3 | 31.1 | 555 | 151.3 | C | 410 | 1.43 | s3 | n | n | d0
16070009 |  |  |  | HO7Z1-K TYPE 2 1X240 MM² PRYSMIAN<G> 2016 FM9 450/750V AFUMEX 750 | 25.7 | 6 | Paron | 1602SEES | -- | 47.1 | 29.3 | No | 2016-07-20 | B2_s1_d0 | 0.42 | 2.8 | 3.5 | 663 | 9.7 | B2 | 11.8 | 0.02 | s1 | n | n | d0
16070008 |  |  |  | CEI 20-22 III IEMMEQUF FG7(0) M1 AFUMEX 1000 1X240MM2 PRYSMIAN<G> 2016 SAFETY LINE PATENTED | 29.6 | 6 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 51.9 | 28.25 | No | 2016-07-20 | B2_s1_d0 | 0.42 | 2.9 | 4.4 | 693 | 11.2 | B2 | 14.4 | 0.02 | s1 | n | n | d0
16070010 |  | 16360 | drum | FR-N1X1G1 12X1.5 MM² | 16.7 | 9 | Paron | SXLPE+400FEIT+16AASEES | -- | 53.9 | 24.5 | No | 2016-07-22 | B2_s1_d2 | 0.6 | 7.4 | 15.9 | 1455 | 15.4 | B2 | 12.5 | 0.02 | s1 | y | y | d2
16070011 |  | 16360 | drum | FR-N1X1G1 12X1.5 MM² | 16.7 | 9 | Paron | SXLPE+400FEIT+16ABSEES | -- | 55.3 | 24.8 | No | 2016-07-22 | B2_s1_d2 | 0.7 | 8.1 | 18.5 | 1419 | 17 | B2 | 21 | 0.03 | s1 | y | y | d2
TN_2016_0245 |  |  |  | ASCABLE-RECAEL RZ1-K (AS) 1KV 3G2.5 | 10.05 | 15 | Vilanova | SXLPE+LSOH | -- | 61.3 | 28.2 | No | 2016-07-25 | E ou F_s2_d2 | 3.3 | 95.1 | 260.9 | 1182 | 297.4 | E ou F | 190.6 | 0.59 | s2 | y | y | d2
TN_2016_0246 |  |  |  | ASCABLE-RECAEL HO7Z1-K (AS) TYPE2 AENOR (HAR) 1X10MM2 | 6.05 | 25 | Vilanova | LSOH | -- | 51.1 | 31.1 | No | 2016-07-25 | B2_s1_d0 | 0.6 | 2.3 | 10.2 | 525 | 49.1 | B2 | 2.2 | 0.01 | s1 | n | n | d0
16070012 |  |  |  | FR-N1X1G1 1*16 MM² | 10.4 | 15 | Paron | SXLPE+0400FEIT+16ABSEES | -- | 46.3 | 24.3 | No | 2016-07-26 | B2_s1_d2 | 0.5 | 6.7 | 13.6 | 795 | 33.7 | B2 | 13 | 0.02 | s1 | y | y | d2
TN_2016_0247 |  |  |  | FROR 450/750 FLEXI PIU 5G1.5 PRYSMIAN (G) 2016 ECOLOGY LINE | 10 | 15 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 69.6 | 27.7 | No | 2016-07-27 | C_s3_d0 | 1.3 | 10.8 | 31.5 | 549 | 131 | C | 404.3 | 1.45 | s3 | n | n | d0
TN_2016_0248 |  |  |  | FROR 450/750 FLEXI PIU 5G1.5 PRYSMIAN (G) 2016 ECOLOGY LINE | 10 | 15 | Vilanova | IZ1000IT+0900FPIT+2700SPIT | -- | 65.5 | 28.9 | No | 2016-07-27 | C_s3_d0 | 1.48 | 11.9 | 32.3 | 552 | 136.3 | C | 422.8 | 1.39 | s3 | n | n | d0
TN_2016_0249 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.78 | 15 | Vilanova | GFR325+5300SEIT | -- | 62.9 | 29.7 | No | 2016-07-27 | C_s1_d2 | 0.94 | 21 | 32.3 | 873 | 57.5 | C | 36 | 0.08 | s1 | y | y | d2
TN_2016_0250 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.03 | 15 | Vilanova | GFR325+5300SEIT+20%-1420FEES | -- | 69.1 | 26.7 | No | 2016-07-28 | B2_s1_d2 | 1.15 | 14.5 | 27.6 | 861 | 56.3 | B2 | 20.2 | 0.07 | s1 | y | y | d2
TN_2016_0251 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.75 | 15 | Vilanova | GFR325+5300SEIT+20%-1420FEES | -- | 64.8 | 28.2 | No | 2016-07-28 | B2_s1_d2 | 0.96 | 11.7 | 22 | 885 | 55.8 | B2 | 31.3 | 0.04 | s1 | y | y | d2
TN_2016_0252 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.94 | 15 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 72.5 | 26.8 | No | 2016-07-29 | C_s1_d2 | 1.02 | 14.7 | 46.9 | 660 | 132 | C | 20.7 | 0.04 | s1 | y | y | d2
TN_2016_0256 |  |  |  | DRAKA 2016 RAISER 16FO 10D-7A2 INT-V MOVISTAR 146371 | 7 | 21 | Vilanova | LSOH | -- | 74.9 | 26.1 | No | 2016-08-03 | D_s1_d2 | 3.3 | 37.8 | 123.8 | 705 | 320.1 | D | 48.6 | 0.15 | s1 | y | y | d2
TN_2016_0257 |  |  |  | ACOMETIDA_620D 16K_0141 | 3.02 | 150 | Vilanova | LSOH | -- | 62.5 | 28.2 | No | 2016-08-03 | B2_s1_d1 | 1.19 | 15 | 28.3 | 660 | 116.3 | B2 | 25.1 | 0.06 | s1 | y | n | d1
TN_2016_0258 |  | 81090739/10 | -- | AFUMEX FIRS SZ1-K 0.6_1KV PH90 (AS+) 3G1.5MM | 9.8 | 15 | Vilanova | SILASTIC+SKINDEEPRID2400+1643SEES | -- | 63.3 | 29.9 | No | 2016-08-03 | D_s2_d2 | 3.3 | 58.4 | 121 | 1041 | 261.9 | D | 104 | 0.36 | s2 | y | y | d2
TN_2016_0261 |  | 81090739/10 | -- | AFUMEX FIRS SZ1-K 0.6_1KV PH90 (AS+) 3G1.5MM | 9.8 | 15 | Vilanova | SILASTIC+SKINDEEPRID2400+1643SEES | -- | 54.9 | 19.8 | No | 2016-09-19 | D_s3_d2 | 2.7 | 38.2 | 86.7 | 690 | 257.2 | D | -- | - | s3 | y | y | d2
TN_2016_0262 |  | 81090739/10 | -- | AFUMEX FIRS SZ1-K 0.6_1KV PH90 (AS+) 3G1.5MM | 9.8 | 15 | Vilanova | SILASTIC+SKINDEEPRID2400+1643SEES | -- | 47 | 23.4 | No | 2016-09-19 | D_s3_d2 | 3.3 | 40.9 | 85.4 | 672 | 257.8 | D | -- | -- | s3 | y | y | d2
TN_2016_0263 |  | 60512/10 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.88 | 180 | Vilanova | 1602SEES | -- | 65.2 | 24 | No | 2016-10-07 | C_s1_d0 | 1.4 | 14.2 | 36.5 | 591 | 138.9 | C | 45.9 | 0.16 | s1 | n | n | d0
TN_2016_0264 |  | 60514/10 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X2.5 | 3.55 | 105 | Vilanova | 1602SEES | -- | 67.9 | 21.9 | No | 2016-10-07 | B2_s1_d0 | 0.87 | 8.2 | 24.5 | 600 | 99.5 | B2 | 36.9 | 0.08 | s1 | n | n | d0
TN_2016_0265 |  | 60513/10 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X4 | 4.08 | 90 | Vilanova | 1602SEES | -- | 47 | 25.6 | No | 2016-10-05 | B2_s1_d0 | 0.98 | 9 | 23.4 | 663 | 64.8 | B2 | 0 | 0 | s1 | n | n | d0
TN_2016_0266 |  | 60515/10 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X6 | 4.6 | 60 | Vilanova | 1602SEES | -- | 55 | 24.3 | No | 2016-10-05 | B2_s1_d0 | 0.75 | 7.5 | 19.1 | 615 | 65.6 | B2 | 0 | 0 | s1 | n | n | d0
TN_2016_0267 |  | 60516/10 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X10 | 5.98 | 25 | Vilanova | 1602SEES | -- | 64.7 | 295.65 | No | 2016-10-05 | B2_s1_d0 | 0.39 | 3.6 | 12.4 | 462 | 77.5 | B2 | 0 | 0 | s1 | n | n | d0
TN_2016_0268 |  | 60541/10 | 317338H | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X240 | 24.5 | 7 | Vilanova | 1602SEES | -- | 69.5 | 19.6 | No | 2016-10-07 | B2_s1_d0 | 0.22 | 1.9 | 3.7 | 693 | 9.4 | B2 | 22.9 | 0.04 | s1 | n | n | d0
TN_2016_0269 |  | 60568/10 | 308557N | AFUMEX EASY RZ1-K 0.6/1.0KV 3X150+1X70 0.6/1KV | 50.7 | 4 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 51.7 | 17.4 | No | 2016-10-12 | B2_s1_d0 | 0.25 | 4.1 | 5.7 | 708 | 14.1 | B2 | 0.6 | 0 | s1 | n | n | d0
TN_2016_0270 |  | 60542/10 | 314353N | AFUMEX EASY RZ1-K 0.6/1.0KV 1X240 | 30.5 | 6 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 50.2 | 18.4 | No | 2016-10-12 | B2_s1_d0 | 0.45 | 3.5 | 5.4 | 606 | 17.6 | B2 | 5.3 | 0.01 | s1 | n | n | d0
TN_2016_0271 |  | 60516/10 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X10 | 5.98 | 25 | Vilanova | 1602SEES | -- | 49.8 | 20.4 | No | 2016-10-12 | B2_s1_d1 | 0.6 | 3.9 | 13.5 | 522 | 62.3 | B2 | 2.7 | 0.01 | s1 | y | n | d1
16100001 |  | 16490 | drum | FR-N1X1G1 12X1.5 MM² | 16.9 | 9 | Paron | GFR325+400FEIT+5300SEIT | -- | 42 | 23 | No | 2016-10-14 | B2_s1_d2 | 0.72 | 7.7 | 13.6 | 822 | 26 | B2 | 11 | 0.02 | s1 | y | y | d2
TN_2016_0272 |  | 60523/10 | 279725B | AFUMEX EASY RZ1-K 0.6/1.0KV 1X1.5 | 8.1 | 19 | Vilanova | GFR325+400FEIT+5300SEIT | -- | 73.6 | 20.1 | No | 2016-10-17 | B2_s1_d2 | 0.96 | 7.6 | 17.2 | 636 | 67.8 | B2 | 29.6 | 0.06 | s1 | y | y | d2
TN_2016_0273 |  | 60548/10 | 291476M | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 12 | 13 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 70.7 | 21.7 | No | 2016-10-17 | B2_s1_d2 | 0.8 | 14.5 | 28.3 | 879 | 54.6 | B2 | 23.8 | 0.05 | s1 | y | y | d2
TN_2016_0274 |  | 60512/10 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.88 | 180 | Vilanova | 1602SEES | -- | 67.6 | 23.1 | No | 2016-10-17 | C_s1_d0 | 1.34 | 14.4 | 33 | 678 | 102.3 | C | 38.8 | 0.14 | s1 | n | n | d0
TN_2016_0275 |  | 60523/10 | 279725B | AFUMEX EASY RZ1-K 0.6/1.0KV 1X1.5 | 8.1 | 19 | Vilanova | GFR325+400FEIT+5300SEIT | -- | 70.6 | 19.4 | No | 2016-10-20 | B2_s1_d1 | 0.95 | 11.1 | 20.8 | 591 | 88.3 | B2 | 29.4 | 0.09 | s1 | y | n | d1
TN_2016_0276 |  | 60548/10 | 291476M | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 12 | 13 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 69.3 | 19.9 | No | 2016-10-20 | C_s1_d2 | 0.77 | 15.9 | 31.6 | 900 | 56.4 | C | 25 | 0.05 | s1 | y | y | d2
TN_2016_0277 |  | 60548/10 | 291476M | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 12 | 13 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 66.1 | 20.1 | No | 2016-10-20 | C_s1_d2 | 0.88 | 16.7 | 32.5 | 933 | 53.5 | C | 40.4 | 0.07 | s1 | y | y | d2
TN_2016_0278 |  | 60548/10 | 311720B | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 13.1 | 12 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 77.3 | 19.8 | No | 2016-10-23 | C_s1_d2 | 0.78 | 16.7 | 27.7 | 1143 | 39.8 | C | 18.1 | 0.04 | s1 | y | y | d2
TN_2016_0279 |  | 60548/10 | 311720B | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 13.1 | 12 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 71.1 | 22.7 | No | 2016-10-23 | C_s1_d2 | 0.72 | 21.3 | 32.3 | 1056 | 48.6 | C | 15 | 0.03 | s1 | y | y | d2
TN_2016_0280 |  | 60522/10 | 265503B | AFUMEX EASY RZ1-K 0.6/1.0KV 1X1.5 | 8.3 | 19 | Vilanova | GFR325+400FEIT+5300SEIT | -- | 70.3 | 23.7 | No | 2016-10-23 | B2_s1_d2 | 0.75 | 10.4 | 22.5 | 579 | 91 | B2 | 9.5 | 0.03 | s1 | y | y | d2
TN_2016_0281 |  | 60522/10 | 265503B | AFUMEX EASY RZ1-K 0.6/1.0KV 1X1.5 | 8.3 | 19 | Vilanova | GFR325+400FEIT+5300SEIT | -- | 70.4 | 23 | No | 2016-10-27 | B2_s1_d2 | 0.55 | 7.6 | 20.1 | 567 | 88.5 | B2 | 11.7 | 0.03 | s1 | y | y | d2
16100065 |  | CEL-0595-16 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.9 | 165 | CEIS | 1602SEES | -- | 80 | 18 | No | 2016-10-26 | B2_s1_d0 | 0.45 | 11 | 18.2 | 561 | 94.2 | B2 | 9.2 | 0.02 | s1 | n | n | d0
16100067 |  | CEL-0595-16 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X2.5 | 3.6 | 105 | CEIS | 1602SEES | -- | 64 | 21.7 | No | 2016-10-26 | B2_s1_d0 | 0.3 | 5.5 | 7.7 | 603 | 42.4 | B2 | 2.4 | 0 | s1 | n | n | d0
16100066 |  | CEL-0595-16 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X4 | 4.4 | 75 | CEIS | 1602SEES | -- | 74 | 19.6 | No | 2016-10-26 | B2_s1_d0 | 0.3 | 6.7 | 9 | 585 | 56.7 | B2 | 1.9 | 0 | s1 | n | n | d0
16100068 |  | CEL-0595-16 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X6 | 4.7 | 6 | CEIS | 1602SEES | -- | 53 | 23 | No | 2016-10-26 | B2_s1_d0 | 0.6 | 5.5 | 11.3 | 672 | 32.5 | B2 | 3.8 | 0.02 | s1 | n | n | d0
16100069 |  | CEL-0599-16 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X10 | 6.3 | 24 | CEIS | 1602SEES | -- | 40 | 26 | No | 2016-10-26 | B2_s1_d0 | 0.5 | 6.3 | 9.5 | 516 | 56.4 | B2 | 1.7 | 0.01 | s1 | n | n | d0
16100070 |  | CEL-0623 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X240 | 25 | 7 | CEIS | 1602SEES | -- | 51 | 23.5 | No | 2016-10-27 | B2_s1_d0 | 0.15 | 1.9 | 2.7 | 1296 | 0 | B2 | 0.9 | 0 | s1 | n | n | d0
TN_2016_0282 |  | 60672/10 | 315896R | AFUMEX EASY RZ1-K 0.6/1.0KV 3G16 | 18 | 8 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 77.6 | 20.7 | No | 2016-10-27 | C_s1_d1 | 0.72 | 17.8 | 34.5 | 1497 | 36 | C | 2.8 | 0.01 | s1 | y | n | d1
TN_2016_0283 |  | 60548/10 | 311713V | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 13.1 | 12 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 73.4 | 22.6 | No | 2016-10-27 | B2_s1_d1 | 0.45 | 9.9 | 15.7 | 1137 | 32.1 | B2 | 29.3 | 0.04 | s1 | y | n | d1
TN_2016_0284 |  | 60548/10 | 311713V | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 13.1 | 12 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 72.6 | 18.4 | No | 2016-11-04 | B2_s1_d2 | 0.48 | 14.9 | 21.8 | 1014 | 42.2 | B2 | 30 | 0.05 | s1 | y | y | d2
TN_2016_0285 |  | 60548/10 | 311713V | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 13.1 | 12 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 73 | 20.3 | No | 2016-11-04 | B2_s1_d2 | 0.45 | 12.9 | 22 | 969 | 42.6 | B2 | 30 | 0.1 | s1 | y | y | d2
TN_2016_0286 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 1X1.5 | 7.31 | 21 | Vilanova | GFR325+400FEIT+5300SEIT | -- | 69.4 | 21.9 | No | 2016-11-04 | B2_s2_d2 | 1.1 | 10.5 | 23.1 | 588 | 100 | B2 | 226 | 0.27 | s2 | y | y | d2
TN_2016_0287 |  | 60528/10 | 291470R | AFUMEX EASY RZ1-K 0.6/1.0KV 1X1.5 | 6.2 | 25 | Vilanova | GFR325+5300SEIT | -- | 49.7 | 14.3 | No | 2016-11-07 | B2_s1_d2 | 1.1 | 9.5 | 28.5 | 531 | 132 | B2 | 43.7 | 0.1 | s1 | y | y | d2
TN_2016_0288 |  | 60517/10 | 291471S | AFUMEX EASY RZ1-K 0.6/1.0KV 1X1.5 | 9 | 17 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 48.4 | 15.5 | No | 2016-11-07 | B2_s1_d1 | 0.75 | 7.6 | 18.5 | 684 | 69.6 | B2 | 5.8 | 0.02 | s1 | y | n | d1
TN_2016_0289 |  | 60529/10 | 311715W | AFUMEX EASY RZ1-K 0.6/1.0KV 1X4 | 7 | 21 | Vilanova | GFR325+5300SEIT | -- | 42.4 | 18.3 | No | 2016-11-07 | B2_s1_d2 | 0.96 | 11.2 | 29.1 | 597 | 108.5 | B2 | 29.7 | 0.21 | s1 | y | y | d2
TN_2016_0290 |  | 60518/10 | 315900V | AFUMEX EASY RZ1-K 0.6/1.0KV 1X4 | 9.4 | 17 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 49.2 | 16.5 | No | 2016-11-09 | B2_s1_d2 | 0.59 | 8.2 | 14.1 | 771 | 58 | B2 | 21.2 | 0.03 | s1 | y | y | d2
TN_2016_0291 |  | 60519/10 | 311709P | AFUMEX EASY RZ1-K 0.6/1.0KV 1X4 | 7.9 | 19 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 43.4 | 19.2 | No | 2016-11-09 | B2_s1_d1 | 0.65 | 8.6 | 19.6 | 690 | 67.6 | B2 | 9 | 0.03 | s1 | y | n | d1
TN_2016_0292 |  | 60524/10 | 311706L | AFUMEX EASY RZ1-K 0.6/1.0KV 1X4 | 9.4 | 17 | Vilanova | GFR325+400FEIT+5300SEIT | -- | 41.1 | 20.5 | No | 2016-11-09 | B2_s1_d2 | 0.57 | 14.7 | 21.1 | 717 | 69.3 | B2 | 6.6 | 0.04 | s1 | y | y | d2
TN_2016_0293 |  | 60525/10 | 311716X | AFUMEX EASY RZ1-K 0.6/1.0KV 1X4 | 7.8 | 19 | Vilanova | GFR325+400FEIT+5300SEIT | -- | 54.1 | 15.6 | No | 2016-11-10 | B2_s1_d2 | 0.75 | 7.6 | 21.7 | 591 | 82.2 | B2 | 13.2 | 0.02 | s1 | y | y | d2
TN_2016_0294 |  | 60526/10 | 315901W | AFUMEX EASY RZ1-K 0.6/1.0KV 1X16 | 12 | 13 | Vilanova | GFR325+400FEIT+5300SEIT | -- | 50.1 | 17.3 | No | 2016-11-10 | B2_s1_d2 | 0.75 | 8.6 | 14.1 | 735 | 53.4 | B2 | 0 | 0.01 | s1 | y | y | d2
TN_2016_0295 |  | 60527/10 | 315910F | AFUMEX EASY RZ1-K 0.6/1.0KV 1X16 | 10.7 | 14 | Vilanova | GFR325+400FEIT+5300SEIT | -- | 46.3 | 19.1 | No | 2016-11-10 | B2_s1_d2 | 0.55 | 8.8 | 15.7 | 648 | 49.7 | B2 | 16 | 0.03 | s1 | y | y | d2
TN_2016_0296 |  | 60530/10 | 315909E | AFUMEX EASY RZ1-K 0.6/1.0KV 1X16 | 9.8 | 15 | Vilanova | GFR325+5300SEIT | -- | 55.7 | 15.5 | No | 2016-11-11 | B2_s1_d2 | 0.75 | 9.1 | 24.4 | 966 | 57.5 | B2 | 29.7 | 0.06 | s1 | y | y | d2
TN_2016_0297 |  | 60520/10 | 315895P | AFUMEX EASY RZ1-K 0.6/1.0KV 1X16 | 11.7 | 13 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 59.2 | 17.4 | No | 2016-11-11 | B2_s1_d0 | 0.62 | 12 | 17.5 | 1053 | 36.2 | B2 | 27.5 | 0.05 | s1 | n | n | d0
TN_2016_0298 |  | 60521/10 | 315911G | AFUMEX EASY RZ1-K 0.6/1.0KV 1X16 | 10.7 | 14 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 45.6 | 20.4 | No | 2016-11-11 | B2_s1_d1 | 0.56 | 7.7 | 14.9 | 870 | 39.4 | B2 | 13.8 | 0.03 | s1 | y | n | d1
TN_2016_0299 |  | 60663/10 | 315902X | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.2 | 15 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 56.6 | 13.4 | No | 2016-11-15 | B2_s1_d2 | 0.55 | 12.5 | 21.6 | 840 | 64.5 | B2 | 16.5 | 0.03 | s1 | y | y | d2
TN_2016_0300 |  | 60069/10 | 315898T | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.6 | 14 | Vilanova | SXLPE+1420FEES+5300SEIT | -- | 52.3 | 16 | No | 2016-11-15 | B2_s1_d2 | 0.74 | 12.7 | 23.9 | 882 | 51.1 | B2 | 29.4 | 0.05 | s1 | y | y | d2
TN_2016_0301 |  | 60989/10 | 316100M | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.4 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 44 | 20.1 | No | 2016-11-15 | D_s2_d1 | 2.19 | 34.4 | 47.6 | 837 | 96.5 | D | 65.7 | 0.28 | s2 | y | n | d1
TN_2016_0302 |  | 60548/10 | 311713V | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 13.3 | 12 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 55.1 | 13.4 | No | 2016-11-16 | B2_s1_d0 | 0.74 | 12 | 24.8 | 771 | 52.7 | B2 | 49.4 | 0.12 | s1 | n | n | d0
TN_2016_0303 |  | -- | 324254A | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.4 | 14 | Vilanova | SXLPE+1420FEES+20AG | -- | 53.2 | 16.5 | No | 2016-11-16 | D_s1_d2 | 2.4 | 36.4 | 46 | 1191 | 90.5 | D | 23.5 | 0.14 | s1 | y | y | d2
TN_2016_0304 |  | 60990/10 | 316097J | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.1 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 49.9 | 19.3 | No | 2016-11-16 | E ou F_s2_d2 | 3.3 | 77.9 | 209.2 | 1455 | 181.1 | E ou F | 165.3 | 0.49 | s2 | y | y | d2
TN_2016_0305 |  | 60986/10 | 316089A | AFUMEX EASY RZ1-K 0.6/1.0KV 1X6 | 8.5 | 17 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 56.9 | 14.3 | No | 2016-11-17 | B2_s1_d2 | 0.93 | 10 | 23.2 | 654 | 65.7 | B2 | 30 | 0.06 | s1 | y | y | d2
TN_2016_0307 |  | 60988/10 | 316102P | AFUMEX EASY RZ1-K 0.6/1.0KV 1X6 | 8.2 | 19 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 46.4 | 19.7 | No | 2016-11-17 | C_s2_d1 | 1.95 | 21.7 | 36.8 | 693 | 109.6 | C | 64.5 | 0.13 | s2 | y | n | d1
TN_2016_0308 |  | -- | 12 - A48521 | FG7R 0.6/1KV G-SETTE PIU 1X240 PRYSMIAN (G) | 29.1 | 6 | Vilanova | G7+0900FPIT+2700SPIT | -- | 42 | 21.3 | No | 2016-11-17 | B2_s2_d1 | 0.7 | 12.8 | 25.3 | 1500 | 45.8 | B2 | 258.9 | 0.59 | s2 | y | n | d1
TN_2016_0309 |  | -- | 12 - G01842 | FG7R 0.6/1KV G-SETTE PIU 1X240 PRYSMIAN (G) | 27.8 | 6 | Vilanova | GFR325+2700SPIT | -- | 82.9 | 17.9 | No | 2016-11-21 | C_s2_d2 | 1.06 | 15.7 | 23.5 | 1182 | 35.9 | C | 339.2 | 0.5 | s2 | y | y | d2
TN_2016_0310 |  | -- | 12 - G01841 | FG7OR 0.6/1KV G-SETTE PIU 2X35 PRYSMIAN (G) | 24.5 | 7 | Vilanova | G7+0900FPIT+2700SPIT | -- | 65.4 | 20.7 | No | 2016-11-18 | B2_s3_d2 | 0.81 | 12.2 | 26 | 1431 | 44.9 | B2 | 533.2 | 0.62 | s3 | y | y | d2
TN_2016_0311 |  | -- | 12 - G01910 | FG7OR 0.6/1KV G-SETTE PIU 2X35 PRYSMIAN (G) | 24.6 | 7 | Vilanova | GFR325+0900FPIT+2700SPIT | -- | 56.1 | 20.9 | No | 2016-11-24 | B2_s2_d0 | 0.51 | 8.6 | 13.1 | 810 | 49.3 | B2 | 328.9 | 0.61 | s2 | n | n | d0
TN_2016_0312 |  | 60991/10 | 324251X | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.4 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 83.4 | 19.7 | No | 2016-11-21 | C_s1_d1 | 1.3 | 15.5 | 25.4 | 933 | 45.5 | C | 35.9 | 0.1 | s1 | y | n | d1
TN_2016_0313 |  | -- | 07 - D37503 | FG7OR 0.6/1KV G-SETTE PIU 1X6 PRYSMIAN (G) | 8.57 | 17 | Vilanova | G7+0900FPIT+2700SPIT | -- | 69.1 | 9.9 | No | 2016-11-25 | B2_s2_d1 | 0.68 | 4.8 | 17.2 | 570 | 75.7 | B2 | 174.9 | 0.69 | s2 | y | n | d1
TN_2016_0314 |  | -- | roll | PRYSMIAN (S) OPTIC KABEL VERTICASA 24FO (PROTO Nº4) | 11.39 | 13 | Vilanova | ECCOH5903 | -- | 71.1 | 22.6 | No | 2016-11-23 | C_s2_d2 | 1.87 | 28.1 | 52.1 | 888 | 96.7 | C | 89.8 | 0.13 | s2 | y | y | d2
TN_2016_0315 |  | -- | roll | PRYSMIAN (S) OPTIC KABEL VERTICASA 24FO (PROTO Nº1) | 11.7 | 13 | Vilanova | ECCOH5903 | -- | 75.7 | 20.8 | No | 2016-11-23 | D_s2_d2 | 2.05 | 26 | 48.5 | 864 | 104.3 | D | 93.2 | 0.16 | s2 | y | y | d2
TN_2016_0317 |  | -- | roll | PRYSMIAN (S) OPTIC KABEL VERTICASA 24FO (PROTO Nº3) | 11.85 | 13 | Vilanova | ECCOH5903 | -- | 74.1 | 21.7 | No | 2016-11-23 | C_s1_d2 | 1.7 | 24.3 | 38.5 | 783 | 82.6 | C | 40.8 | 0.08 | s1 | y | y | d2
TN_2016_0319 |  | -- | 07 - 739203 | FG7OR 0.6/1KV G-SETTE PIU 5G1.5 PRYSMIAN (G) | 13.85 | 11 | Vilanova | G7+0900FPIT+2700SPIT | -- | 56 | 15 | No | 2016-11-25 | C_s3_d0 | 1.7 | 20.1 | 32.3 | 780 | 68.2 | C | 707.5 | 1.11 | s3 | n | n | d0
TN_2016_0320 |  | -- | 07 - 739201 | FG7OR 0.6/1KV G-SETTE PIU 5G1.5 PRYSMIAN (G) | 12.36 | 13 | Vilanova | GFR325+2700SPIT | -- | 55.5 | 16.6 | No | 2016-11-25 | B2_s2_d2 | 0.86 | 9.5 | 20.1 | 678 | 57.6 | B2 | 320.7 | 0.82 | s2 | y | y | d2
TN_2016_0321 |  | -- | 07 - 739252 | FG7OR 0.6/1KV G-SETTE PIU 7G1.5 PRYSMIAN (G) | 14.6 | 10 | Vilanova | G7+0900FPIT+2700SPIT | -- | 52.9 | 17.7 | No | 2016-12-08 | C_s3_d0 | 1.3 | 21 | 35.5 | 1089 | 54.9 | C | 530.8 | 0.92 | s3 | n | n | d0
TN_2016_0322 |  | -- | 07 - D37491 | FG7OR 0.6/1KV G-SETTE PIU 7G1.5 PRYSMIAN (G) | 14.7 | 10 | Vilanova | GFR325+2700SPIT | -- | 58 | 14.9 | No | 2016-12-08 | B2_s2_d1 | 0.75 | 12 | 24.8 | 771 | 66.5 | B2 | 329.7 | 0.85 | s2 | y | n | d1
TN_2016_0323 |  | -- | 07-D37519 | N07VK RETOX 1X1.5MM2 PRYSMIAN (G) IEMMEQU ECOLOGY LINE PH FREE | 2.75 | 195 | Vilanova | 2600IPIT+SKIN28ABGPIT | -- | 68.7 | 11.8 | No | 2016-12-08 | C_s3_d0 | 1.17 | 8.4 | 29.3 | 447 | 203.4 | C | 378.6 | 1.65 | s3 | n | n | d0
TN_2016_0324 |  | -- | 07-D37551 | N07VK RETOX 1X1.5MM2 PRYSMIAN (G) IEMMEQU ECOLOGY LINE PH FREE | 2.85 | 180 | Vilanova | 28ABGPIT | -- | 60.7 | 13.3 | No | 2016-12-08 | B2_s2_d0 | 0.82 | 5.4 | 19.1 | 522 | 116.2 | B2 | 285.9 | 1.33 | s2 | n | n | d0
TN_2016_0325 |  | -- | 12 - C01947 | N07VK RETOX 1X240MM2 PRYSMIAN (G) IEMMEQU ECOLOGY LINE PH FREE | 25 | 7 | Vilanova | 28AAIPIT | -- | 66.7 | 18.9 | No | 2016-11-28 | B2_s2_d0 | 0.71 | 3.7 | 8.1 | 642 | 33.9 | B2 | 241.2 | 0.58 | s2 | n | n | d0
TN_2016_0327 |  | 60188/10 | 321624S | AL-AFUMEX RRFWZ1-AS 2X35 | 35 | 5 | Vilanova | SXLPE+BEDDINGGFR325+STEELTAPECORRUGATED+1643SEES | -- | 61.6 | 12.6 | No | 2016-12-11 | B2_s1_d2 | 0.68 | 7.4 | 8.9 | 594 | 32.1 | B2 | 0 | 0.01 | s1 | y | y | d2
TN_2016_0328 |  | -- | 330853Y | AFUMEX FIRS SZ1-K 0.6_1KV PH90 (AS+) 5G6MM2 | 15.8 | 9 | Vilanova | SILASTIC+SKIN41AA+1643SEES+5%LLDPE | -- | 60.5 | 12.4 | No | 2016-12-09 | C_s1_d2 | 0.92 | 18.8 | 41.1 | 756 | 91.6 | C | 46.6 | 0.12 | s1 | y | y | d2
|  |  | 330853Y | AFUMEX FIRS SZ1-K 0.6_1KV PH90 (AS+) 5G6MM2 | 16.34 | 9 | CEIS | SILASTIC+SKIN41AA+1643SEES+5%LLDPE | -- | 95 | 11.68 | No | 2017-02-07 | C_s1_d2 | 0.8 | 20.6 | 38.7 | 771 | 96.4 | C | 28.7 | 0.09 | s1 | n | y | d2
TN_2016_0329 |  | -- | 331128X | AFUMEX FIRS SZ1-K 0.6_1KV PH90 (AS+) 3G1.5MM2 | 9.25 | 17 | Vilanova | SILASTIC+SKIN41AA+1643SEES+5%LLDPE | -- | 55.3 | 14.5 | No | 2016-12-09 | C_s1_d2 | 0.91 | 14.4 | 45.6 | 549 | 188.5 | C | 26.9 | 0.09 | s1 | y | y | d2
|  | -- | 331128X | AFUMEX FIRS SZ1-K 0.6_1KV PH90 (AS+) 3G1.5MM2 | 9.36 | 17 | CEIS | SILASTIC+SKIN41AA+1643SEES+5%LLDPE | -- | 40 | 9.39 | No | 2017-01-26 | B2_s1_d2 | 0.8 | 10.8 | 28.7 | 540 | 140.5 | B2 | 13.2 | 0.04 | s1 | n | y | d2
TN_2016_0331 |  | 61010/10 | 311569M | 4X2X2.5MM2 C.62 TYPE E2 DHOZ 650/1100 V | 27.9 | 6 | Vilanova | GFR325+1643SEES | -- | 52.9 | 17 | No | 2016-12-09 | B2_s1_d2 | 0.72 | 14.9 | 28.6 | 906 | 47.4 | B2 | 37.5 | 0.06 | s1 | y | y | d2
TN_2016_0332 |  | -- | 296002S | AL-HEPRZ1(AS) 1X400MM2 12/20KV | 48 | 4 | Vilanova | HEPR+1420FEES+6000SEES | -- | 69.8 | 11.1 | No | 2016-12-11 | C_s1_d2 | 0.96 | 19 | 27.7 | 1071 | 38.2 | C | 10.5 | 0.03 | s1 | y | y | d2
TN_2016_0333 |  | -- | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X2.5 | 3.35 | 120 | Vilanova | 1602SEES+5%LLDPE | -- | 58.6 | 11.2 | No | 2016-12-13 | B2_s1_d0 | 1.19 | 11.6 | 28.4 | 660 | 97.2 | B2 | 43.7 | 0.17 | s1 | n | n | d0
|  |  | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X2.5 | 3.7 | 105 | CEIS | 1602SEES+5%LLDPE | -- | 86 | 12.03 | No | 2017-02-03 | B2_s1_d0 | 0.7 | 6 | 19.5 | 624 | 69.3 | B2 | 12.4 | 0.06 | s1 | n | n | d0
TN_2016_0334 |  | -- | 296002S | AL-HEPRZ1(AS) 1X400MM2 12/20KV | 48 | 4 | Vilanova | HEPR+1420FEES+6000SEES | -- | 57.6 | 12.9 | No | 2016-12-13 | C_s1_d2 | 0.95 | 15.2 | 23.4 | 1050 | 31.7 | C | 9 | 0.03 | s1 | y | y | d2
TN_2016_0335 |  | -- | 168796Z | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 38.35 | 5 | Vilanova | HEPR+1420FEES+6000SEES | -- | 56 | 15.4 | No | 2016-12-13 | B2_s1_d0 | 0.61 | 10.3 | 12.7 | 675 | 45.5 | B2 | 14.4 | 0.03 | s1 | n | n | d0
TN_2016_0336 |  | -- | 168796Z | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 38.35 | 5 | Vilanova | HEPR+1420FEES+6000SEES | -- | 57.6 | 18.5 | No | 2016-12-13 | C_s1_d1 | 0.69 | 17 | 19.2 | 1281 | 49.3 | C | 11.1 | 0.03 | s1 | y | n | d1
|  |  | 168796Z | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 39.07 | 5 | CEIS | HEPR+1420FEES+6000SEES |  | 62 | 13.19 | No | 2017-02-23 | B2_s1_d1 | 0.65 | 12 | 13.6 | 1500 | 37.6 | B2 | 6 | 0.02 | s1 | y | n | d1
TN_2016_0337 |  | -- | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X2.5 | 3.3 | 120 | Vilanova | 1602SEES | -- | 59.3 | 12.1 | No | 2016-12-20 | B2_s1_d0 | 0.82 | 10.7 | 18.2 | 663 | 82.7 | B2 | 10.5 | 0.06 | s1 | n | n | d0
TN_2016_0338 |  | 81787319 | 318226Y | AFUMEX FIRS SZ1-K 0.6_1KV PH90 (AS+) 1X95MM2 | 17.5 | 9 | Vilanova | SXLPEMICATAPE+1643SEES+5%LLDPE | -- | 59.1 | 12.4 | No | 2016-12-20 | C_s1_d2 | 1.2 | 24.6 | 51.4 | 1062 | 67.5 | C | 21.6 | 0.05 | s1 | n | y | d2
|  | 81787319 | 318226Y | AFUMEX FIRS SZ1-K 0.6_1KV PH90 (AS+) 1X95MM2 | 18 | 8 | CEIS | SXLPEMICATAPE+1643SEES+5%LLDPE | -- | 73 | 12.1 | No | 2017-02-13 | C_s1_d2 | 1.1 | 20 | 57.5 | 1137 | 68.7 | C | 13.6 | 0.04 | s1 | n | y | d2
TN_2016_0339 |  | 81853075 | 311653D | RHV 5KV 1X6MM2 VOLTALENE PRIMARIO BALIZAS | 17.3 | 9 | Vilanova | XLPE+COPPERTAPE+PVC1085SP | -- | 60.6 | 12.9 | No | 2016-12-20 | E ou F_s3_d2 | 3.3 | 125.9 | 495.3 | 1023 | 685.1 | E ou F | 1985.3 | 5.8 | s3 | n | y | d2
TN_2016_0340 |  | 81833171 | 328115X | AFUMEX-PANELES HO7Z-K GR 1X35MM2 | 10.2 | 15 | Vilanova | 41AASEES | -- | 71.3 | 10.2 | No | 2016-12-21 | D_s1_d2 | 2.6 | 30.2 | 47 | 939 | 88.3 | D | 30.6 | 0.05 | s1 | n | y | d2
TN_2016_0341 |  | 61010/10 | 332536C | 4X2X2.5MM2 C.62 TYPE E2 DHOZ 650/1100 V | 27.6 | 6 | Vilanova | GFR325+5300SEIT | -- | 76.8 | 12.2 | No | 2016-12-16 | C_s1_d2 | 1.11 | 24.2 | 43.4 | 1239 | 46.7 | C | 36.2 | 0.12 | s1 | n | y | d2
TN_2016_0342 |  | 61010/10 | 332558B | 4X2X2.5MM2 C.62 TYPE E2 DHOZ 650/1100 V | 28.2 | 6 | Vilanova | GFR325+1602SEES | -- | 71.9 | 13.2 | No | 2016-12-16 | B2_s1_d0 | 0.6 | 7.6 | 10.2 | 1500 | 21.3 | B2 | 18.4 | 0.04 | s1 | n | n | d0
TN_2016_0343 |  | 60995/10 | 331971N | AFUMEX EASY RZ1-K 0.6/1.0KV 1X240 | 28.6 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 65.2 | 11.4 | No | 2016-12-21 | B2_s1_d2 | 0.63 | 10.4 | 22.7 | 1500 | 22.8 | B2 | 16.1 | 0.04 | s1 | n | y | d2
|  | 60995/10 | 331971N | AFUMEX EASY RZ1-K 0.6/1.0KV 1X240 | 28 | 6 | CEIS | SXLPE+1420FEES+1602SEES | -- | 86 | 10.4 | No | 2017-02-13 | B2_s1_d2 | 0.8 | 7.2 | 18.3 | 1494 | 19.6 | B2 | 1.6 | 0.01 | s1 | n | y | d2
TN_2016_0344 |  | 60996/10 | 330907G | AFUMEX EASY RZ1-K 0.6/1.0KV 3X150+1X70 0.6/1KV | 46.6 | 4 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 62.3 | 12.9 | No | 2016-12-21 | B2_s1_d0 | 0.34 | 5 | 6.5 | 711 | 19.8 | B2 | 6.1 | 0.02 | s1 | n | n | d0
TN_2016_0345 |  | 61218/10 | 333386B | AFUMEX EASY RZ1-K 0.6/1.0KV 2X1.5 | 9.15 | 17 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 63.8 | 11.25 | No | 2016-12-22 | C_s1_d2 | 1.38 | 18.8 | 37 | 681 | 97.8 | C | 40 | 0.08 | s1 | n | y | d2
|  | 61218/10 | 333386B | AFUMEX EASY RZ1-K 0.6/1.0KV 2X1.5 | 10 | 15 | CEIS | SXLPE+1420FEES+1602SEES | -- | 94 | 8.42 | No | 2017-02-03 | B2_s1_d2 | 0.75 | 11.2 | 24.6 | 690 | 64.6 | B2 | 8 | 0.02 | s1 | n | y | d2
TN_2016_0346 |  | 61219/10 | 333370J | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.1 | 15 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 57.6 | 13.65 | No | 2016-12-22 | D_s1_d0 | 2.06 | 27.3 | 42.2 | 774 | 90.1 | D | 0.8 | 0.02 | s1 | n | n | d0
|  | 61219/10 | 333370J | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 11.19 | 14 | CEIS | SXLPE+1420FEES+1602SEES | -- | 40 | 10.45 | No | 2017-01-26 | C_s1_d2 | 0.9 | 18.4 | 26.5 | 843 | 59.9 | C | 15.6 | 0.03 | s1 | n | y | d2
TN_2016_0347 |  | 61220/10 | 333385A | AFUMEX EASY RZ1-K 0.6/1.0KV 4G1.5 | 10.7 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 54.6 | 15.65 | No | 2016-12-22 | C_s1_d1 | 1.72 | 25.9 | 33.7 | 1020 | 66.4 | C | 47.1 | 0.11 | s1 | y | n | d1
|  | 61220/10 | 333385A | AFUMEX EASY RZ1-K 0.6/1.0KV 4G1.5 | 10 | 15 | CEIS | SXLPE+1420FEES+1602SEES | -- | 93 | 8.1 | No | 2017-01-26 | B2_s1_d2 | 0.95 | 13.5 | 27 | 723 | 68.7 | B2 | 11.3 | 0.03 | s1 | n | y | d2
TN_2017_0348 |  | 60821/10 | roll | ES50Z1-K AFUMEX PLUS EX VILANOVA 1X0.75 MM2 | 2.37 | 255 | Vilanova | 1510+2%SILOXÀ | -- | 52.7 | 13.5 | No | 2017-01-10 | B2_s2_d0 | 1.12 | 8.5 | 19.7 | 765 | 51.1 | B2 | 63.1 | 0.09 | s2 | n | n | d0
|  | 60821/10 | roll | ES50Z1-K AFUMEX PLUS EX VILANOVA 1X0.75 MM2 | 2.36 | 255 | CEIS | 1510+2%SILOXÀ | -- | 55 | 6.87 | No | 2017-01-26 | B2_s1_d0 | 0.75 | 7 | 15.9 | 585 | 77.4 | B2 | 8.8 | 0.04 | s1 | n | n | d0
TN_2017_0349 |  | -- | -- | CEI 20-22 II IEEMMEQU PB FREE FG70R 0.6/1 KV G-SETTE 3G1.5 PRYSMIAN <G> 2016 EASY LINE | 9.88 | 15 | Vilanova | JACKET:27ATSPITFILLER09AEFPIT | -- | 60.2 | 10.2 | No | 2017-01-09 | C_s2_d0 | 1.15 | 12.7 | 39.5 | 606 | 160.5 | C | 293.8 | 1.03 | s2 | n | n | d0
TN_2017_0350 |  | 81842989 | 322378L | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.3 | 9 | Vilanova | XLPE+COPPERTAPE+1643SEES | -- | 48.7 | 15.1 | No | 2017-01-09 | D_s2_d2 | 3.3 | 24.4 | 192.7 | 912 | 314.9 | D | 34.4 | 0.3 | s2 | n | y | d2
TN_2017_0351 |  | 60820/10 | roll | ES50Z1-K AFUMEX PLUS EX VILANOVA 1X0.5 MM2 | 2.23 | 300 | Vilanova | 1510+2%SILOXÀ | -- | 54.9 | 12.6 | No | 2017-01-09 | C_s2_d0 | 1.8 | 19.9 | 47.5 | 702 | 131.6 | C | 63.1 | 0.11 | s2 | n | n | d0
|  | 60820/10 | roll | ES50Z1-K AFUMEX PLUS EX VILANOVA 1X0.5 MM2 | 2.17 | 300 | CEIS | 1510+2%SILOXÀ | -- | 60 | 5.63 | No | 2017-01-26 | B2_s1_d0 | 0.75 | 7.6 | 17.1 | 597 | 86.5 | B2 | 13.2 | 0.08 | s1 | n | n | d0
TN_2017_0352 |  | 60822/10 | roll | ES50Z1-K AFUMEX PLUS EX VILANOVA 1X1.0 MM2 | 2.54 | 225 | Vilanova | 1510+2%SILOXÀ | -- | 70.3 | 14.1 | No | 2017-01-12 | B2_s1_d0 | 1.23 | 11.6 | 28.2 | 549 | 129.1 | B2 | 31 | 0.12 | s1 | n | n | d0
|  | 60822/10 | roll | ES50Z1-K AFUMEX PLUS EX VILANOVA 1X1.0 MM2 | 2.59 | 210 | CEIS | 1510+2%SILOXÀ | -- | 45 | 7.32 | No | 2017-01-26 | B2_s1_d0 | 0.85 | 8 | 21.6 | 666 | 69 | B2 | 12.9 | 0.08 | s1 | n | n | d0
TN_2017_0353 |  | -- | -- | CEI 20-22 II IEEMMEQU PB FREE FG70R 0.6/1 KV G-SETTE 3G1.5 PRYSMIAN <G> 2016 EASY LINE | 9.88 | 15 | Vilanova | JACKET:27ATSPITFILLER09AEFPIT | -- | 70.7 | 10.1 | No | 2017-01-10 | C_s2_d0 | 1.15 | 14.5 | 37.6 | 699 | 129.2 | C | 296 | 1 | s2 | n | n | d0
TN_2017_0354 |  | -- | -- | CEI 20-22 II IEEMMEQU PB FREE FG70R 0.6/1 KV G-SETTE 3G1.5 PRYSMIAN <G> 2016 EASY LINE | 9.88 | 15 | Vilanova | JACKET:27ATSPITFILLER09AEFPIT | -- | 57.3 | 11.5 | No | 2017-01-10 | C_s2_d0 | 1.2 | 11.9 | 37.1 | 696 | 105.8 | C | 316 | 0.95 | s2 | n | n | d0
TN_2017_0355 |  | -- | 12 - A48521 | FG7R 0.6/1KV G-SETTE PIU 1X240 PRYSMIAN (G) | 29.1 | 6 | Vilanova | G7+0900FPIT+2700SPIT | -- | 61.5 | 16.5 | No | 2017-01-12 | B2_s2_d2 | 0.8 | 9.1 | 26 | 1494 | 38 | B2 | 247.6 | 0.49 | s2 | y | y | d2
TN_2017_0356 |  | -- | 12 - G01842 | FG7R 0.6/1KV G-SETTE PIU 1X240 PRYSMIAN (G) | 27.8 | 6 | Vilanova | GFR325+2700SPIT | -- | 60.8 | 18.4 | No | 2017-01-12 | C_s2_d2 | 1.14 | 17.5 | 32.5 | 1065 | 42.5 | C | 281 | 0.4 | s2 | y | y | d2
TN_2017_0357 |  | -- | 12 - G01841 | FG7OR 0.6/1KV G-SETTE PIU 2X35 PRYSMIAN (G) | 24.5 | 7 | Vilanova | G7+0900FPIT+2700SPIT | -- | 43.2 | 13.9 | No | 2017-01-13 | C_s3_d1 | 1.25 | 13.1 | 33.5 | 1497 | 45.3 | C | 515.5 | 0.83 | s3 | y | n | d1
TN_2017_0358 |  | -- | 12 - G01910 | FG7OR 0.6/1KV G-SETTE PIU 2X35 PRYSMIAN (G) | 24.6 | 7 | Vilanova | GFR325+0900FPIT+2700SPIT | -- | 36.9 | 15.1 | No | 2017-01-13 | B2_s2_d0 | 0.78 | 8.9 | 13.3 | 708 | 41.2 | B2 | 320.9 | 0.62 | s2 | n | n | d0
TN_2017_0359 |  | -- | 07 - D37503 | FG7OR 0.6/1KV G-SETTE PIU 1X6 PRYSMIAN (G) | 8.57 | 17 | Vilanova | G7+0900FPIT+2700SPIT | -- | 37.2 | 17.4 | No | 2017-01-13 | B2_s2_d1 | 0.8 | 7.1 | 27.3 | 576 | 99.9 | B2 | 170 | 0.66 | s2 | y | n | d1
TN_2017_0360 |  | -- | -- | FZ0MSU-SD-HF 2X6X5M2 G-652D 10 DRAKA 2013 | 9.8 | 15 | Vilanova | MEGOLONS-540 | -- | 32.6 | 6.3 | No | 2017-01-18 | E ou F_s2_d2 | 3.3 | 94.3 | 329.5 | 828 | 624 | E ou F | 111.4 | 0.47 | s2 | n | y | d2
TN_2017_361 |  | -- | 333858P | 3G1.5MM2 EVOLUCION (PROTOTIPO CPR CINTA INGNIFUGA + 1602 SEES) | 8.8 | 17 | Vilanova | SXLPE+1602SEES | -- | 28.8 | 9.1 | No | 2017-01-18 | E ou F_s2_d2 | 3.3 | 81.9 | 228.6 | 1077 | 295.6 | E ou F | 63.7 | 0.3 | s2 | n | y | d2
TN_2017_362 |  | -- | 335700S | AFUMEX EASY RZ1-K 0.6/1.0KV 3X150+1X70 0.6/1KV | 50 | 4 | Vilanova | SXLPE+20AG | -- | 24.7 | 11.5 | No | 2017-01-18 | B2_s1_d0 | 0.6 | 4.8 | 6.7 | 669 | 19.1 | B2 | 22.7 | 0.06 | s1 | n | n | d0
TN_2017_363 |  | -- | 335699R | AFUMEX EASY RZ1-K 0.6/1.0KV 3X150+1X70 0.6/1KV | 49 | 4 | Vilanova | SXLPE+1602SEES | -- | 40.5 | 7.1 | No | 2017-01-19 | B2_s1_d0 | 0.55 | 4.4 | 6.3 | 687 | 17.3 | B2 | 5.6 | 0.02 | s1 | n | n | d0
TN_2017_364 |  | -- | 334443A | 1X2X2.5 C62 TYPE E2 ROZ | 16.9 | 9 | Vilanova | SXLPE+FAINPLASTHFX-521 | -- | 40.9 | 8.3 | No | 2017-01-19 | E ou F_s2_d2 | 3.3 | 95.7 | 384.7 | 1071 | 498.8 | E ou F | 54.2 | 0.27 | s2 | n | y | d2
TN_2017_365 |  | -- | 335606P | 4X2X2.5MM2 C.62 TYPE E2 DHOZ 650/1100 V | 27.9 | 6 | Vilanova | SXLPE+FAINPLASTHFX-521 | -- | 39.1 | 12.7 | No | 2017-01-19 | E ou F_s2_d2 | 3.3 | 96.9 | 383.5 | 1251 | 405.3 | E ou F | 55.6 | 0.34 | s2 | n | y | d2
TN_2017_366 |  | -- | 334439W | 2X2X1.5MM2 C62 TYPE E2 RHOZ | 16.4 | 9 | Vilanova | SXLPE+FAINPLASTHFX-521 | -- | 65.4 | 10.4 | No | 2017-01-20 | E ou F_s2_d2 | 3.3 | 142.1 | 366.3 | 1020 | 508.7 | E ou F | 142.9 | 0.44 | s2 | n | y | d2
TN_2017_367 |  |  | F68767 | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.95 | 165 | Vilanova | 1602SEES | -- | 69.1 | 18.2 | No | 2017-02-15 | B2_s2_d0 | 0.85 | 6.8 | 20 | 564 | 86.9 | B2 | 50.4 | 0.11 | s2 | n | n | d0
TN_2017_368 |  |  | F68760 | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X2.5 | 3.68 | 105 | Vilanova | 1602SEES | -- | 30.9 | 16.1 | No | 2017-02-09 | B2_s1_d0 | 1.06 | 9.6 | 24.7 | 636 | 103.9 | B2 | 31.3 | 0.1 | s1 | n | n | d0
TN_2017_369 |  | OP61598 | Roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.98 | 165 | Vilanova | 1602SEES+5%LLDPE | -- | 54.4 | 12.1 | No | 2017-01-31 | B2_s1_d0 | 1.2 | 8.3 | 24.5 | 606 | 83.8 | B2 | 37.7 | 0.11 | s1 | n | n | d0
TN_2017_370 |  | OP61599 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.88 | 180 | Vilanova | PRUEBA21602SEES+5%DELLDPE+SKINDE1510SEES+2%DESILOXANE | -- | 80.6 | 12.6 | No | 2017-01-31 | C_s2_d0 | 1.25 | 15.8 | 31.6 | 630 | 118.4 | C | 64.1 | 0.15 | s2 | n | n | d0
TN_2017_371 |  | OP61600 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 3 | 165 | Vilanova | 1602AASEES | -- | 78.7 | 14.6 | No | 2017-01-31 | C_s2_d0 | 1.82 | 17.9 | 35.9 | 633 | 118 | C | 64.3 | 0.18 | s2 | n | n | d0
TN_2017_372 |  | OP61601 | roll | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.96 | 165 | Vilanova | 1602AASEES+5%LLDPE | -- | 76.3 | 15.6 | No | 2017-01-31 | D_s2_d0 | 3.3 | 43.5 | 66.2 | 762 | 169.2 | D | 63.8 | 0.11 | s2 | n | n | d0
TN_2017_373 |  | -- | 334443A | 1X2X2.5 C62 TYPE E2 ROZ | 16.9 | 9 | Vilanova | SXLPE+FAINPLASTHFX-521 | -- | 49.9 | 13.5 | No | 2017-01-24 | E ou F_s2_d2 | 3.3 | 139.6 | 440.9 | 1110 | 544.4 | E ou F | 79.7 | 0.42 | s2 | n | y | d2
TN_2017_374 |  | -- | 335606P | 4X2X2.5MM2 C.62 TYPE E2 DHOZ 650/1100 V | 27.9 | 6 | Vilanova | SXLPE+FAINPLASTHFX-521 | -- | 10.1 | 58.8 | No | 2017-01-24 | E ou F_s2_d2 | 3.3 | 136.3 | 441.9 | 1500 | 397.4 | E ou F | 105 | 0.41 | s2 | n | y | d2
TN_2017_375 |  |  | C25260 | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X4 | 4.15 | 75 | Vilanova | 1602SEES | -- | 65.8 | 11.1 | No | 2017-02-10 | B2_s1_d0 | 0.52 | 4.5 | 11.9 | 588 | 56.7 | B2 | 11.7 | 0.04 | s1 | n | n | d0
TN_2017_376 |  | -- | D24432 | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X6 | 4.73 | 60 | Vilanova | 1602SEES | -- | 62.3 | 14.6 | No | 2017-02-03 | B2_s1_d0 | 0.39 | 2.8 | 9.8 | 474 | 56.3 | B2 | 23.2 | 0.06 | s1 | n | n | d0
TN_2017_377 |  | -- | E53308 | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X10 | 6.6 | 21 | Vilanova | 1602SEES | -- | 58.7 | 16.4 | No | 2017-02-03 | B2_s1_d0 | 0.34 | 2.6 | 8.5 | 582 | 38.2 | B2 | 7.1 | 0.04 | s1 | n | n | d0
TN_2017_378 |  | -- | G86091 | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X10 | 6.75 | 21 | Vilanova | 1602SEES | -- | 73.4 | 16.8 | No | 2017-02-01 | B2_s1_d0 | 0.32 | 2.3 | 7.4 | 528 | 36.6 | B2 | 10.4 | 0.04 | s1 | n | n | d0
TN_2017_379 |  | -- | E58779 | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X240 | 26 | 6 | Vilanova | 1602SEES | -- | 75.4 | 15.5 | No | 2017-02-01 | B2_s1_d0 | 0.45 | 3.7 | 4.8 | 957 | 13.2 | B2 | 7.8 | 0.04 | s1 | n | n | d0
TN_2017_380 |  | -- | E62733 | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X240 | 25.5 | 6 | Vilanova | 1602SEES | -- | 80.2 | 13.6 | No | 2017-02-01 | B2_s1_d0 | 0.42 | 3.8 | 5.4 | 1458 | 8.3 | B2 | 13.7 | 0.05 | s1 | n | n | d0
TN_2017_381 |  | -- | roll | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G2.5MM2 | 11.37 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 60.5 | 13.2 | No | 2017-02-03 | D_s2_d2 | 2.15 | 34.2 | 56.8 | 1062 | 80.5 | D | 109 | 0.15 | s2 | n | y | d2
TN_2017_382 |  | -- | 337773V | PRYSMIAN SAP 90-10648-AAA 61238 6501100V LSC 4X2X2.5MM2 | 29.04 | 6 | Vilanova | GFR365+0400FEIT | -- | 56.8 | 11.4 | No | 2017-02-08 | C_s1_d2 | 1.4 | 28.7 | 45.5 | 1116 | 60.6 | C | 43.5 | 0.14 | s1 | n | y | d2
TN_2017_383 |  | -- | 60048757 | DRAKA 2017 CDS 4513 12FO G657 (AS) KT UFINET TELECOM 153179 | 10.18 | 15 | Vilanova | 1500SEES | -- | 31.7 | 17.4 | No | 2017-02-09 | D_s2_d2 | 3.3 | 37.5 | 365.6 | 645 | 1059.6 | D | 53.8 | 0.46 | s2 | n | y | d2
TN_2017_384 |  | -- | 60047451 | DRAKA 2016 CAS 4513 48FO G657 A2 KT UNIFET TELECOM 152434 | 10.4 | 15 | Vilanova | 1500SEES | -- | 51 | 12.7 | No | 2017-02-08 | D_s3_d2 | 3.3 | 40.4 | 360 | 675 | 993 | D | 71.3 | 2.16 | s3 | n | y | d2
TN_2017_385 |  | -- | 60022835 | DRAKA 48 2016 1GW 16FO ORANGE ESPANA | 7.49 | 21 | Vilanova | 1500SEES | -- | 64.1 | 12.1 | No | 2017-02-10 | D_s2_d2 | 3.3 | 52 | 280.8 | 579 | 1015.3 | D | 61.4 | 0.18 | s2 | n | y | d2
TN_2017_386 |  | -- | 337870A | AL-HEPRZ1(AS) 1X240MM2 18/30KV | 47.2 | 4 | Vilanova | HEPR+1420FEES+6000SEES | -- | 75.2 | 16.4 | No | 2017-02-15 | B2_s1_d0 | 0.9 | 7.9 | 9.5 | 882 | 21.2 | B2 | 49.8 | 0.09 | s1 | n | n | d0
|  | -- | 337870A | AL-HEPRZ1(AS) 1X240MM2 18/30KV | 48.06 | 4 | CEIS | HEPR+1420FEES+6000SEES | OD | 55 | 13.52 | No | 2017-02-23 | B2_s1_d1 | 0.7 | 9.8 | 10.9 | 924 | 32.6 | B2 | 4 | 0.01 | s1 | y | n | d1
TN_2017_387 |  | -- | 12-C01947 | N07V-K 1X240MM2 0.450.75KV CPR-28AB 20195777 | 25 | 7 | Vilanova | 28AAIPIT | -- | 66.1 | 19.2 | No | 2017-02-15 | B2_s2_d0 | 0.73 | 5 | 8.3 | 633 | 38.7 | B2 | 218.8 | 0.45 | s2 | n | n | d0
TN_2017_388 |  | -- | 333385A | AFUMEX EASY RZ1-K 0.6/1.0KV 4G1.5 | 10.7 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 71.4 | 18.5 | No | 2017-02-16 | C_s2_d2 | 1.94 | 29.6 | 40.4 | 987 | 78 | C | 54.8 | 0.09 | s2 | n | y | d2
TN_2017_389 |  | -- | Roll | RV-K 0.6/1KV 5G1.5MM2 2016 | 10.52 | 14 | Vilanova | SXLPE+1600GPFR | -- | 68.9 | 19 | No | 2017-02-16 | E ou F_s3_d2 | 3.3 | 20.5 | 367.2 | 507 | 1774 | E ou F | 356.8 | 9.34 | s3 | y | y | d2
TN_2017_390 |  | -- | T8-F65299 | PRYSMIAN FG16M16 1 KV 1X10 | 10.31 | 15 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 37.7 | 17.5 | No | 2017-02-16 | B2_s1_d1 | 0.6 | 10.7 | 19.5 | 903 | 35.4 | B2 | 16.9 | 0.04 | s1 | y | n | d1
TN_2017_391 |  | -- | 16-TLE62406 | PRYSMIAN FG16M16 1 KV 1X240 | 29.96 | 6 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 73.4 | 16.9 | No | 2017-02-17 | B2_s1_d1 | 0.35 | 3.4 | 5.9 | 771 | 14.8 | B2 | 5.7 | 0.03 | s1 | y | n | d1
TN_2017_392 |  | -- | T8-E53309 | PRYSMIAN FG16M16 1 KV 5G1.5 | 14.2 | 11 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 79.7 | 14.5 | No | 2017-02-17 | C_s1_d2 | 1.37 | 26.8 | 51.9 | 1218 | 63 | C | 42.9 | 0.14 | s1 | n | y | d2
TN_2017_393 |  | -- | T7-C80730 | PRYSMIAN FG16M16 1 KV 1X4 | 8.63 | 17 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 69 | 18.3 | No | 2017-02-17 | B2_s1_d1 | 0.8 | 9.4 | 23.1 | 750 | 52.4 | B2 | 24.5 | 0.04 | s1 | y | n | d1
17020001 |  | 16612 | roll | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.84 | 180 | Paron | 1602SEES | 1340 | 40.2 | 21.9 | No | 2017-02-02 | B2_s1_d0 | 0.5 | 6.4 | 10.3 | 867 | 38 | B2 | 13 | 0.02 | s1 | n | n | d0
EFR-17-BB-000304 |  | -- | roll | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.84 | 180 | Efectis | 1602SEES | -- | 38.9 | 15.47 | No | 2017-02-23 | B2_s1_d0 | 0.45 | 5.8 | 10.8 | 666 | 45 | B2 | 5.9 | 0.01 | s1 | n | n | d0
17020004 |  | 16599 | roll | HO7Z1-R 1X2.5MM2 | 3.84 | 90 | Paron | 1602SEES | 1305 | 41.1 | 21.9 | No | 2017-02-07 | B2_s1_d0 | 0.8 | 9.2 | 20.6 | 645 | 60 | B2 | 21 | 0.06 | s1 | n | n | d0
EFR-17-BB-000304D |  | -- | roll | HO7Z1-R 1X2.5MM2 | 3.84 | 90 | Efectis | 1602SEES | -- | 42.1 | 14.63 | No | 2017-02-24 | B2_s1_d0 | 1.08 | 9.1 | 19 | 681 | 69.2 | B2 | 14.8 | 0.04 | s1 | n | n | d0
17010008 |  | 16622 | drum | FR-N1X1G1 5G1.5MM² | 13 | 12 | Paron | SXLPE+0400FEIT+5300SEIT | 1547 | 22.9 | 20.8 | No | 2017-01-25 | B2_s1_d1 | 0.7 | 8.2 | 13.4 | 1092 | 28 | B2 | 13 | 0.02 | s1 | y | n | d1
EFR-17-BB-000304B |  | -- | drum | FR-N1X1G1 5G1.5MM² | 13 | 12 | Efectis | SXLPE+0400FEIT+5300SEIT | -- | 37.6 | 15.9 | No | 2017-02-23 | B2_s1_d0 | 0.73 | 6.8 | 9.8 | 1245 | 30.6 | B2 | 4.6 | 0.01 | s1 | n | n | d0
17010007 |  | 16622 | drum | FR-N1X1G1 1X25MM² | 12.2 | 13 | Paron | SXLPE+0400FEIT+5300SEIT | 1613 | 23 | 22 | No | 2017-01-25 | B2_s1_d2 | 0.55 | 6.8 | 12.3 | 1128 | 21 | B2 | 6 | 0.01 | s1 | y | y | d2
EFR-17-BB-000304C |  | -- | drum | FR-N1X1G1 1X25MM² | 12.2 | 13 | Efectis | SXLPE+0400FEIT+5300SEIT | -- | 39.5 | 16.52 | No | 2017-02-23 | B2_s1_d1 | 0.78 | 8.5 | 12.2 | 1080 | 36.9 | B2 | 3.6 | 0.01 | s1 | y | n | d1
EFR-17-BB-000304F |  | -- | drum | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X95 | 15.2 | 10 | Efectis | 1602SEES | -- | 37.9 | 14.84 | No | 2017-02-24 | B2_s1_d0 | 0.44 | 4.2 | 4.8 | 849 | 21.1 | B2 | 0 | 0 | s1 | n | n | d0
EFR-17-BB-000304E |  | -- | drum | HO7Z1-R 1X95MM2 | 14.9 | 10 | Efectis | 1602SEES | -- | 40 | 15 | No | 2017-02-24 | B2_s1_d0 | 0.53 | 5.3 | 7.5 | 669 | 31.8 | B2 | 1.7 | 0 | s1 | n | n | d0
TN_2017_394 |  | -- | 07-D37519 | N07VK RETOX 1X1.5MM2 PRYSMIAN (G) IEMMEQU ECOLOGY LINE PH FREE | 2.75 | 195 | Vilanova | 2600IPIT+SKIN28ABGPIT | -- | 54.5 | 19.8 | No | 2017-02-22 | C_s3_d0 | 1.3 | 9.1 | 28.2 | 435 | 226.9 | C | 368.1 | 1.61 | s3 | n | n | d0
TN_2017_395 |  | -- | 07-D37551 | N07VK RETOX 1X1.5MM2 PRYSMIAN (G) IEMMEQU ECOLOGY LINE PH FREE | 2.85 | 180 | Vilanova | 28ABGPIT | -- | 59.6 | 15.2 | No | 2017-02-22 | B2_s2_d1 | 0.89 | 5.7 | 14.3 | 492 | 134.9 | B2 | 242 | 0.97 | s2 | y | n | d1
TN_2017_396 |  | -- | T7-C80875 | PRYSMIAN FG16M16 1 KV 1X4 | 8.61 | 17 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 58.5 | 18.8 | No | 2017-02-22 | B2_s1_d2 | 0.86 | 10.5 | 25.8 | 681 | 78.2 | B2 | 47 | 0.06 | s1 | n | y | d2
TN_2017_397 |  | -- | 20-B79838 | PRYSMIAN FG16M16 1 KV 3X120+70 | 46.32 | 4 | Vilanova | SXLPE+0400FEIT+5300SEIT | -- | 56.9 | 17.6 | No | 2017-02-22 | B2_s1_d0 | 0.46 | 3.3 | 4.1 | 762 | 11.2 | B2 | 7 | 0.03 | s1 | n | n | d0
TN_2017_398 |  | -- | 07-B36961 | FG16R16 1X16MM² - 0.6/1 KV | 9.6 | 17 | Vilanova | SXLPE+09AE+27AT | -- | 80.9 | 15.8 | No | 2017-02-24 | C_s2_d0 | 0.7 | 17 | 19.4 | 630 | 165.3 | C | 186.1 | 0.74 | s2 | n | n | d0
TN_2017_399 |  | -- | TL-E64407 | FG16R16 1X300MM² - 0.6/1 KV | 32.24 | 6 | Vilanova | SXLPE+09AE+27AT | -- | 80.6 | 15.2 | No | 2017-02-24 | B2_s2_d1 | 0.74 | 8.7 | 13.9 | 1500 | 58.7 | B2 | 179.8 | 0.45 | s2 | y | n | d1
TN_2017_400 |  | -- | 16-E64416 | FG16OR16 3X120 + 70MM² - 0.6/1 KV | 45.36 | 4 | Vilanova | SXLPE+09AE+27AT | -- | 80.7 | 14.9 | No | 2017-02-24 | B2_s2_d0 | 0.7 | 7.3 | 8.8 | 639 | 38.5 | B2 | 184.5 | 0.31 | s2 | n | n | d0
TN_2017_401 |  | -- | T8-F68840 | FG16OR16 5G1.5MM² - 0.6/1 KV | 13.51 | 11 | Vilanova | SXLPE+09AE+27AT | -- | 67 | 18.8 | No | 2017-02-27 | C_s2_d1 | 0.8 | 19.5 | 28.8 | 888 | 251.2 | C | 242.1 | 0.57 | s2 | y | n | d1
TN_2017_402 |  | -- | 09-F92548 | FG16OR16 24G1.5 MM² - 0.6/1 KV | 22.55 | 7 | Vilanova | SXLPE+09AE+27AT | -- | 80.2 | 16.4 | No | 2017-02-24 | C_s2_d0 | 1.26 | 21.5 | 40.8 | 1473 | 80.4 | C | 339.6 | 0.46 | s2 | n | n | d0
17030001 |  | 16599 | drum | HO7Z1-R- 1X95MM² | 15.2 | 10 | Paron | 1602SEES | -- | 39.1 | 22.2 | No | 2017-03-01 | B2_s1_d0 | 0.35 | 3.7 | 4.7 | 546 | 20 | B2 | 6 | 0.01 | s1 | n | n | d0
17030002 |  | 16599 | drum | HO7Z1-R- 1X10MM² | 6.25 | 25 | Paron | 1602SEES | -- | 39.6 | 22.5 | No | 2017-03-01 | B2_s1_d1 | 0.5 | 2.8 | 9.7 | 561 | 38 | B2 | 6 | 0.06 | s1 | y | n | d1
17030003 |  | 16599 | drum | HO7Z1-R- 1X6.0MM² | 4.83 | 60 | Paron | 1602SEES | -- | 40.4 | 22.7 | No | 2017-03-01 | B2_s1_d0 | 0.45 | 3.8 | 7.6 | 606 | 28 | B2 | 8 | 0.01 | s1 | n | n | d0
TN_2017_403 |  | 81721875 |  | BLINDEX RC4Z1-K 0.6/1KV 2X1.5MM2 | 8.46 | 19 | Vilanova | 1643SEES+5%DELLDPE | -- | 53.4 | 13.2 | No | 2017-03-01 | D_s2_d2 | 3.3 | 53.7 | 89.8 | 744 | 243.8 | D | 71.7 | 0.11 | s2 | n | y | d2
TN_2017_404 |  | 81546939 |  | BLINDEX RC4Z1-K 0.6/1KV 4G1.5MM2 | 10 | 15 | Vilanova | 1643SEES+5%DELLDPE | -- | 49.1 | 15.3 | No | 2017-03-01 | E ou F_s2_d2 | 3.3 | 85.4 | 264.8 | 978 | 398.1 | E ou F | 105 | 0.48 | s2 | n | y | d2
TN_2017_405 |  | 60220 | 327675U | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.5 | 8 | Vilanova | 1602SEES | -- | 46.3 | 17.6 | No | 2017-03-01 | D_s2_d2 | 3 | 65.8 | 151.4 | 1215 | 165.4 | D | 140.5 | 0.34 | s2 | n | y | d2
TN_2017_406 |  | -- | roll | FO64 DRAKA CDS 4513 BA23915 | 11.51 | 13 | Vilanova | 1500SEES | -- | 40.3 | 19.4 | No | 2017-03-01 | E ou F_s2_d2 | 3.3 | 28.9 | 419.4 | 603 | 1384.1 | E ou F | 42.8 | 0.62 | s2 | n | y | d2
TN_2017_407 |  | 61986 | 344014D | AL AFUMEX RZ1 1X300 | 29.36 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 70.9 | 16 | No | 2017-03-03 | B2_s1_d0 | 0.4 | 3.2 | 4.9 | 657 | 13.9 | B2 | 30.9 | 0.05 | s1 | n | n | d0
|  | 61986 | 344014D | AL AFUMEX RZ1 1X300 | 29.24 | 6 | CEIS | SXLPE+1420FEES+1602SEES | -- | 60 | 10.15 | No | 2017-03-22 | B2_s1_d0 | 0.48 | 4.2 | 7.9 | 1380 | 12 | B2 | 2.2 | 0 | s1 | n | n | d0
TN_2017_408 |  | 61985 | 333848D | AL AFUMEX RZ1 1X16 | 10.09 | 15 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 70.2 | 16.4 | No | 2017-03-03 | D_s2_d2 | 3.3 | 67.9 | 104.5 | 1257 | 145.9 | D | 91.2 | 0.16 | s2 | n | y | d2
TN_2017_409 |  | 61608 | 342554S | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X35 | 9.83 | 15 | Vilanova | 1602SEES+5%LLDPE | -- | 68 | 17.2 | No | 2017-03-03 | B2_s1_d0 | 0.37 | 6.4 | 8.2 | 702 | 31.8 | B2 | 23.4 | 0.04 | s1 | n | n | d0
TN_2017_410 |  | 61608 | 342550M | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X35 | 10.6 | 14 | Vilanova | 1602SEES | -- | 68.7 | 17.3 | No | 2017-03-03 | B2_s1_d0 | 0.46 | 4.2 | 9.6 | 759 | 24.2 | B2 | 14.1 | 0.04 | s1 | n | n | d0
TN_2017_411 |  | 61987 | 333449Y | AFUMEX RZ1 1KV 3G1.5 CL1 PORTUGAL | 9.87 | 15 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 69.4 | 17.3 | No | 2017-03-03 | D_s2_d1 | 2.15 | 34.3 | 54.9 | 918 | 104.1 | D | 51.4 | 0.08 | s2 | y | n | d1
|  | 61987 | 333449Y | AFUMEX RZ1 1KV 3G1.5 CL1 PORTUGAL | 10 | 15 | CEIS | SXLPE+1420FEES+1602SEES | -- | 76 | 2.2 | No | 2017-03-23 | B2_s1_d1 | 0.85 | 12 | 25 | 717 | 61.2 | B2 | 12.9 | 0.03 | s1 | y | n | d1
TN_2017_412 |  | 61988 | 335452X | AFUMEX RZ1 1KV 3G1.5 CL1 PORTUGAL | 8.71 | 17 | Vilanova | SXLPE+1602SEES | -- | 64.5 | 17.3 | No | 2017-03-06 | D_s2_d2 | 3.3 | 64.9 | 117.7 | 741 | 279.6 | D | 85 | 0.16 | s2 | n | y | d2
TN_2017_413 |  | 61989 | 333844Z | AFUMEX RZ1 1KV 3G2.5 CL1 PORTUGAL | 11.21 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 56.7 | 20.2 | No | 2017-03-06 | D_s2_d1 | 1.57 | 31.5 | 45.3 | 1131 | 67.9 | D | 54.4 | 0.09 | s2 | y | n | d1
TN_2017_414 |  | 61990 | 288835E | AFUMEX RZ1 1KV 3G2.5 CL1 PORTUGAL | 10.43 | 15 | Vilanova | SXLPE+1602SEES | -- | 51 | 22.3 | No | 2017-03-06 | D_s2_d2 | 3.3 | 69.4 | 122.8 | 1074 | 203.6 | D | 105.9 | 0.18 | s2 | n | y | d2
17030004 |  | 16599 | drum | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X6 | 4.8 | 60 | Paron | 1602SEES | -- | 34.2 | 22.5 | No | 2017-03-03 | B2_s1_d0 | 0.3 | 3.7 | 7.6 | 684 | 30 | B2 | 6 | 0.01 | s1 | n | n | d0
17030005 |  | 16599 | drum | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X10 | 6.29 | 25 | Paron | 1602SEES | -- | 35.7 | 22.7 | No | 2017-03-03 | B2_s1_d0 | 0.25 | 3 | 9.1 | 540 | 38 | B2 | 5 | 0.01 | s1 | n | n | d0
17030006 |  | 16599 | drum | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X95 | 15.2 | 10 | Paron | 1602SEES | -- | 36.8 | 23.5 | No | 2017-03-03 | B2_s1_d0 | 0.46 | 3.6 | 5.1 | 948 | 13 | B2 | 9 | 0.01 | s1 | n | n | d0
17030007 |  | 16650 | drum | DRAKA DROP CLIENTE 1FO 6657 A2 OF 236384 MEO SERVICOS DE COMUNICACOES E MULTIMÉDIA S.A. | 3.9 | 90 | Paron | MODULE5200SMIT-GAINE1700SEES | -- | 37.4 | 21.7 | No | 2017-03-07 | B2_s1_d1 | 0.92 | 11.5 | 23 | 621 | 79 | B2 | 12 | 0.02 | s1 | y | n | d1
17030008 |  | 16650 | drum | DRAKA DROP CLIENTE EXTERIOR 1FO G657 A2 OF 243105 MEO SERVICOS DE COMUNICACOES E MULTIMÉDIA S.A. | 4.6 | 60 | Paron | MODULEPA12-GAINE1700SEFR | -- | 37.7 | 21.9 | No | 2017-03-07 | B2_s1_d0 | 0.9 | 11.7 | 25.1 | 606 | 83 | B2 | 9 | 0.02 | s1 | n | n | d0
17030009 |  | 16650 | drum | MC - 36/6 - 9.5/125 - SH - K209B - PRYSMIAN - 04/2016 | 13.9 | 11 | Paron | GAINERAVASAFEZH-LSF6F | -- | 37.6 | 22 | No | 2017-03-07 | B2_s1_d2 | 0.55 | 9 | 14.8 | 846 | 33 | B2 | 27 | 0.05 | s1 | y | y | d2
17030010 |  | 16681 | drum | K25 750V 1X1.5 -SH-NF F 55-625-255 | 3 | 165 | Paron | ISOLATIONID3100FR/GAINESV3300FR | -- | 48.7 | 23.1 | No | 2017-03-09 | D_s2_d2 | 3.3 | 56.5 | 180.8 | 855 | 327 | D | 105 | 0.33 | s2 | y | y | d2
17030011 |  | 16681 | drum | K25 750V 1X2.5 -SH-NF F 55-625-255 | 3.5 | 120 | Paron | ISOLATIONID3100FR/GAINESV3300FR | -- | 49.4 | 24.5 | No | 2017-03-09 | D_s2_d2 | 3.3 | 50.4 | 128.9 | 1047 | 178 | D | 140 | 0.4 | s2 | y | y | d2
TN_2017_415 |  | 61991 | 333845A | AFUMEX RZ1-K 1KV 3G4 CL1 PORTUGAL | 11.58 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 38.8 | 18.4 | No | 2017-03-07 | C_s1_d2 | 1.21 | 16.6 | 35.5 | 891 | 62.3 | C | 30.7 | 0.06 | s1 | n | y | d2
TN_2017_416 |  | 61992 | 333849E | AFUMEX RZ1-K 1KV 3G4 CL1 PORTUGAL | 11.38 | 14 | Vilanova | SXLPE+1602SEES | -- | 35.7 | 20.5 | No | 2017-03-07 | D_s2_d2 | 3.3 | 66.1 | 107.7 | 900 | 184.8 | D | 65.1 | 0.12 | s2 | n | y | d2
TN_2017_417 |  | 61991 | 333845A | AFUMEX RZ1 1KV 3G4 CL1 PORTUGAL | 11.58 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 68.1 | 19.4 | No | 2017-03-09 | C_s1_d2 | 0.85 | 15.9 | 31.6 | 858 | 57.5 | C | 37.1 | 0.07 | s1 | n | y | d2
|  | 61991 | 333845A | AFUMEX RZ1 1KV 3G4 CL1 PORTUGAL | 12 | 13 | CEIS | SXLPE+1420FEES+1602SEES | -- | 76 | 3.91 | No | 2017-01-23 | B2_s1_d1 | 0.7 | 14.2 | 26.9 | 876 | 47 | B2 | 12.1 | 0.03 | s1 | y | n | d1
TN_2017_418 |  | 60188 | 338702E | AL AFUMEX RRFWZ1 2X35 MM2 | 22.92 | 5 | Vilanova | 1602SEES | -- | 64.7 | 20.4 | No | 2017-03-09 | B2_s1_d2 | 0.72 | 7.2 | 9.4 | 1500 | 14.9 | B2 | 12.8 | 0.03 | s1 | n | y | d2
17030012 |  | 16681 | drum | K25 750V 1X6.0 -SH-NF F 55-625-255 | 5.4 | 30 | Paron | ISOLATIONID3100FR/GAINESV3300FR | -- | 38.4 | 22.8 | No | 2017-03-13 | D_s2_d2 | 3.3 | 20.4 | 38.8 | 729 | 126 | D | 123 | 0.23 | s2 | y | y | d2
17030015 |  | 16622 | drum | FR-N1X1G1 12X1.5 MM² | 16.3 | 9 | Paron | SXLPE+0400FEIT+20AKSEES | -- | 39.7 | 24.1 | No | 2017-03-15 | B2_s1_d1 | 0.73 | 10.4 | 21.7 | 1437 | 21 | B2 | 14 | 0.03 | s1 | y | n | d1
17030016 |  | 16622 | drum | FR-N1X1G1 12X1.5 MM² | 16.3 | 9 | Paron | SXLPE+0400FEIT+20AJSEES | -- | 39.4 | 24.6 | No | 2017-03-15 | B2_s1_d2 | 0.7 | 7.2 | 16 | 1407 | 16 | B2 | 12 | 0.03 | s1 | y | y | d2
TN_2017_419 |  | 62154 | -- | HO7Z1Z1 1X2.5MM2 | 3.54 | 105 | Vilanova | GFR365 | -- | 62.8 | 18.4 | No | 2017-03-13 | D_s2_d2 | 3.3 | 69.8 | 201.7 | 717 | 498.1 | D | 61.2 | 0.18 | s2 | y | y | d2
TN_2017_420 |  | -- | 347549W | RETENAX FLAM RV 20X2.5MM2 | 26.55 | 6 | Vilanova | XLPE+6010SEES+GFR365 | -- | 57.5 | 20 | No | 2017-03-13 | D_s1_d2 | 1.9 | 37.4 | 110.3 | 1500 | 95.9 | D | 7.6 | 0.04 | s1 | y | y | d2
TN_2017_421 |  | -- | drum | DRAKA 2017 1FO 10D 7A2 INT MOVISTAR | 4.21 | 75 | Vilanova | LSOH | -- | 65.1 | 18 | No | 2017-03-14 | D_s2_d1 | 3.3 | 68.2 | 120.5 | 912 | 247 | D | 143.1 | 0.2 | s2 | y | n | d1
TN_2017_422 |  | 61968 | 348212S | AFUMEX FIRS SZ1-K 1X2.5MM2 | 7.4 | 21 | Vilanova | SILASTIC+1420FEES+1602SEES | -- | 70.9 | 13.1 | No | 2017-03-15 | B2_s1_d2 | 1.14 | 9.8 | 26.7 | 621 | 86.7 | B2 | 33.3 | 0.06 | s1 | y | y | d2
|  | 61968 | 348212S | AFUMEX FIRS SZ1-K 1X2.5MM2 | 8 | 19 | CEIS | SILASTIC+1420FEES+1602SEES | -- | 38 | 15.67 | No | 2017-03-30 | B2_s1_d2 | 0.8 | 8.5 | 24 | 612 | 86 | B2 | 5.6 | 0.02 | s1 | n | y | d2
TN_2017_423 |  | 61970 | 347717D | AFUMEX FIRS SZ1-K 1X25MM2 | 12.59 | 12 | Vilanova | SILASTIC+1420FEES+1602SEES | -- | 65 | 17.5 | No | 2017-03-15 | C_s2_d2 | 1.17 | 15.1 | 26.7 | 792 | 61.1 | C | 165.3 | 0.2 | s2 | y | y | d2
|  | 61970 | 347717D | AFUMEX FIRS SZ1-K 1X25MM2 | 13 | 12 | CEIS | SILASTIC+1420FEES+1602SEES | -- | 32 | 17.48 | No | 2017-03-31 | B2_s1_d2 | 0.55 | 8.5 | 17 | 843 | 47 | B2 | 9.4 | 0.02 | s1 | n | y | d2
TN_2017_424 |  | 61972 | 347538J | AFUMEX FIRS SZ1-K 5G1.5MM2 | 12.55 | 12 | Vilanova | SILASTIC+1420FEES+1602SEES | -- | 49.8 | 22.1 | No | 2017-03-14 | C_s2_d2 | 0.93 | 22.6 | 39.8 | 909 | 93.3 | C | 59.8 | 0.09 | s2 | y | y | d2
|  | 61972 | 347538J | AFUMEX FIRS SZ1-K 5G1.5MM2 | 13 | 12 | CEIS | SILASTIC+1420FEES+1602SEES | -- | 43 | 16.87 | No | 2017-03-29 | B2_s1_d2 | 0.7 | 11.7 | 18.6 | 741 | 49.1 | B2 | 10.7 | 0.02 | s1 | n | y | d2
TN_2017_425 |  | 61998 | 345458Y | AFUMEX FIRS SZ1-K 5G35MM2 | 32.47 | 6 | Vilanova | SILASTIC+1420FEES+1602SEES | -- | 61 | 19.4 | No | 2017-03-15 | B2_s2_d2 | 0.76 | 13 | 18.8 | 1221 | 28.6 | B2 | 72.2 | 0.14 | s2 | y | y | d2
|  | 61998 | 345458Y | AFUMEX FIRS SZ1-K 5G35MM2 | 33 | 6 | CEIS | SILASTIC+1420FEES+1602SEES | -- | 50 | 14.2 | No | 2017-03-29 | B2_s1_d2 | 0.7 | 10.7 | 15.7 | 1476 | 24.3 | B2 | 13.5 | 0.04 | s1 | n | y | d2
TN_2017_426 |  | 62000 | 334925Z | AFUMEX MRZ1-K (AS+) 1X35MM2 | 14.2 | 11 | Vilanova | SXLPE+MICAS+1420FEES+1602SEES | -- | 55.8 | 20.7 | No | 2017-03-15 | C_s1_d1 | 1.35 | 20.4 | 34.7 | 984 | 51.3 | C | 34.1 | 0.08 | s1 | y | n | d1
|  | 62000 | 334925Z | AFUMEX MRZ1-K (AS+) 1X35MM2 | 14.11 | 11 | CEIS | SXLPE+MICAS+1420FEES+1602SEES | -- | 60 | 9.75 | No | 2017-03-23 | B2_s1_d1 | 1.08 | 13.2 | 27 | 960 | 42.4 | B2 | 8.7 | 0.02 | s1 | y | n | d1
TN_2017_427 |  | 62001 | 347119D | AFUMEX MRZ1-K (AS+) 1X240MM2 | 28.78 | 6 | Vilanova | SXLPE+MICAS+1420FEES+1602SEES | -- | 62.4 | 12.2 | No | 2017-03-17 | B2_s1_d2 | 0.73 | 8.7 | 22.8 | 1470 | 21.3 | B2 | 6.5 | 0.05 | s1 | n | y | d2
|  | 62001 | 347119D | AFUMEX MRZ1-K (AS+) 1X240MM2 | 28.86 | 6 | CEIS | SXLPE+MICAS+1420FEES+1602SEES | -- | 60 | 10.94 | No | 2017-03-22 | B2_s1_d2 | 0.52 | 6.4 | 16.9 | 1431 | 15 | B2 | 4.1 | 0.01 | s1 | n | y | d2
TN_2017_428 |  | 62973 | 347685U | AFUMEX FIRS SZ1-K 5G1.5MM2 | 11.5 | 13 | Vilanova | SILASTIC+1602SEES | -- | 51.4 | 21.6 | No | 2017-03-15 | C_s1_d2 | 1.59 | 22.8 | 39.7 | 747 | 93.8 | C | 47.2 | 0.11 | s1 | y | y | d2
TN_2017_429 |  | 61999 | 345405R | AFUMEX FIRS SZ1-K 5G35MM2 | 31.19 | 6 | Vilanova | SILASTIC+1602SEES | -- | 53.8 | 17 | No | 2017-03-17 | C_s2_d2 | 0.84 | 16.9 | 39.2 | 1470 | 33.6 | C | 83.5 | 0.26 | s2 | n | y | d2
TN_2017_430 |  | 61971 | 347540L | AFUMEX FIRS SZ1-K 1X25MM2 | 11.13 | 14 | Vilanova | SILASTIC+1602SEES | -- | 47.6 | 19.6 | No | 2017-03-17 | B2_s1_d2 | 0.74 | 8.5 | 24 | 687 | 70.5 | B2 | 38.2 | 0.07 | s1 | n | y | d2
TN_2017_431 |  | -- | -- | RED ELEC RHZ1-RA-2OL (AS) 1X2000MM2 127/220KV +T375AL | 124.5 | 2 | Vilanova | XLPE+FOILAL+6000SEES | -- | 58.5 | 19 | No | 2017-03-16 | B2_s1_d2 | 1.32 | 11.1 | 14.4 | 906 | 29.3 | B2 | 1.1 | 0.01 | s1 | y | y | d2
|  | -- | -- | RED ELEC RHZ1-RA-2OL (AS) 1X2000MM2 127/220KV +T375AL | 124.5 | 2 | CEIS | XLPE+FOILAL+6000SEES | -- | 67 | 5.22 | No | 2017-03-23 | B2_s1_d2 | 1.05 | 11.1 | 14.2 | 1338 | 28.2 | B2 | 6.4 | 0.02 | s1 | n | y | d2
17030017 |  | 16622 | drum | FR-N1X1G1 12X1.5 MM² | 16.8 | 9 | Paron | SXLPE+0400FEIT+1700SEES | -- | 35.4 | 22.8 | No | 2017-03-16 | B2_s1_d2 | 0.7 | 9.8 | 21.7 | 1338 | 21 | B2 | 12 | 0.03 | s1 | y | y | d2
17030018 |  | 16622 | drum | FR-N1X1G1 12X1.5 MM² | 16.8 | 9 | Paron | SXLPE+0400FEIT+DFH9740 | -- | 38.9 | 22.5 | No | 2017-03-16 | B2_s1_d2 | 0.7 | 9.3 | 22.7 | 1398 | 21 | B2 | 12 | 0.03 | s1 | y | y | d2
TN_2017_432 |  | 62123 | 348263X | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 9.9 | 15 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 57 | 18.8 | No | 2017-03-20 | D_s2_d2 | 2.12 | 30.6 | 47.2 | 834 | 95.8 | D | 53.1 | 0.1 | s2 | n | y | d2
|  | 62123 | 348263X | AFUMEX EASY RZ1-K 0.6/1.0KV 3G1.5 | 10.37 | 15 | CEIS | SXLPE+1420FEES+1602SEES | -- | 60 | 19.9 | No | 2017-05-10 | C_s1_d1 | 0.95 | 15.2 | 24.7 | 858 | 60.4 | C | 14.6 | 0.04 | s1 | y | n | d1
TN_2017_433 |  | 61966 | 348014B | AFUMEX CLASS ATEX RZ1HZ1-K 1KV 5G2.5 | 16.97 | 9 | Vilanova | SXLPE+1602SEES+1602SEES | -- | 53.9 | 20.7 | No | 2017-03-20 | C_s2_d2 | 0.94 | 17.4 | 31.9 | 1131 | 38.9 | C | 72.4 | 0.13 | s2 | n | y | d2
TN_2017_434 |  | 61963 | 351626C | AFUMEX CLASS ATEX RZ1HZ1-K 1KV 5G2.5 | 16.82 | 9 | Vilanova | SXLPE+1602SEES | -- | 50 | 21.6 | No | 2017-03-20 | B2_s2_d2 | 0.82 | 12 | 23 | 1158 | 27.2 | B2 | 58 | 0.11 | s2 | n | y | d2
|  | 61963 | 351626C | AFUMEX CLASS ATEX RZ1HZ1-K 1KV 5G2.5 | 17.37 | 9 | CEIS | SXLPE+1602SEES | -- | 55 | 17.9 | No | 2017-05-10 | B2_s1_d2 | 0.9 | 13.8 | 27.3 | 1212 | 30 | B2 | 9.3 | 0.03 | s1 | n | y | d2
17030019 |  | 16670 | drum | DRAKA 1 OF G657 OF 245159 | 4.7 | 60 | Paron | 1700SEITNOIR+55AASEIT | -- | 37.2 | 23.6 | No | 2017-03-20 | B2_s1_d1 | 0.95 | 14.2 | 25.6 | 615 | 86 | B2 | 16 | 0.04 | s1 | y | n | d1
17030020 |  | 16568 | roll | DRAKA 03 HULT MBZH 7G1.5 MM² 0.6/1 KV KEMA-KEUR HALOGEN FREE | 13 | 12 | Paron | LSOH | -- | 34.3 | 23.8 | No | 2017-03-20 | B2_s1_d1 | 0.65 | 11.2 | 17.5 | 1032 | 32 | B2 | 13 | 0.03 | s1 | y | n | d1
17030021 |  | 16568 | roll | CABLE HALOGEN FREE (ARMOURED MULTICOLORE 37X1.5MM². Ø#26MM) | 26.5 | 6 | Paron | LSOH | -- | 31.7 | 24.3 | No | 2017-03-20 | B2_s1_d1 | 0.7 | 7.1 | 13.5 | 1500 | 28 | B2 | 9 | 0.03 | s1 | y | n | d1
TN_2017_435 |  | -- | 348271F | AFUMEX EASY RZ1-K 0.6/1.0KV 4G1.5 | 11.17 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 70 | 16.5 | No | 2017-03-21 | D_s2_d2 | 2.2 | 36.2 | 50.4 | 1134 | 89.3 | D | 74 | 0.11 | s2 | y | y | d2
|  | -- | 348271F | AFUMEX EASY RZ1-K 0.6/1.0KV 4G1.5 | 10.87 | 14 | CEIS | SXLPE+1420FEES+1602SEES | -- | 27 | 25.8 | No | 2017-05-10 | C_s1_d2 | 1.4 | 21.4 | 29.5 | 786 | 65.4 | C | 14.9 | 0.03 | s1 | y | y | d2
TN_2017_436 |  | -- | 348278N | AFUMEX EASY RZ1-K 0.6/1.0KV 2X1.5 | 9.78 | 15 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 66.9 | 18.1 | No | 2017-03-21 | C_s1_d0 | 1.57 | 19.7 | 35.3 | 789 | 74.4 | C | 49.6 | 0.1 | s1 | n | n | d0
|  | -- | 348278N | AFUMEX EASY RZ1-K 0.6/1.0KV 2X1.5 | 9.97 | 15 | CEIS | SXLPE+1420FEES+1602SEES | -- | 50 | 19.4 | No | 2017-05-10 | B2_s1_d1 | 0.85 | 10.4 | 21.1 | 798 | 47.9 | B2 | 8.6 | 0.02 | s1 | y | n | d1
TN_2017_437 |  | -- | 184981S | AFUMEX GULD RZ1-K 1 KV 5G2.5 | 10.86 | 14 | Vilanova | SXLPE+1643SEES+5%DELLDPE | -- | 63.3 | 19.6 | No | 2017-03-21 | D_s2_d2 | 3.3 | 63.2 | 89.5 | 939 | 152.7 | D | 111.8 | 0.21 | s2 | y | y | d2
|  | -- | 184981S | AFUMEX GULD RZ1-K 1 KV 5G2.5 | 10.99 | 14 | CEIS | SXLPE+1643SEES+5%DELLDPE | -- | 30 | 37.7 | No | 2017-06-15 | C_s1_d2 | 1.25 | 21.9 | 44.3 | 723 | 104.8 | C | 12.1 | 0.02 | s1 | n | y | d2
17030022 |  | 16681 | drum | 1800-S-1X240MM²-SH-NF F 55-625-255 | 29.4 | 6 | Paron | SV3200FR | -- | 38.3 | 21.3 | No | 2017-03-22 | B2_s1_d2 | 0.55 | 6.6 | 10.4 | 1500 | 22 | B2 | 13 | 0.02 | s1 | y | y | d2
17030023 |  | 16681 | drum | 1800-S-1*16-SH-NF F 55-625-255 | 14 | 11 | Paron | SV3200FR | -- | 39.3 | 21.3 | No | 2017-03-22 | B2_s1_d2 | 1 | 14.8 | 27.3 | 1005 | 44 | B2 | 47 | 0.09 | s1 | y | y | d2
TN_2017_438 |  | 20132648 | 292230S | AFUMEX EASY RZ1-K 0.6/1.0KV 1X6 | 7.06 | 21 | Vilanova | SXLPE+6000SEES | -- | 74.6 | 12.3 | No | 2017-03-28 | _ _
TN_2017_439 |  | 20132698 | 330828W | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 10.88 | 14 | Vilanova | SXLPE+6000SEES | -- | 70.6 | 14.8 | No | 2017-03-28 | _ _
TN_2017_440 |  |  |  | DRAKA COMTEQ 24FO 2007 | 13.4 | 12 | Vilanova | PENDING | -- | 65.4 | 17.1 | No | 2017-03-28 | E ou F_s2_d2 | 3.3 | 112 | 258.8 | 1002 | 377.8 | E ou F | 164 | 0.34 | s2 | n | y | d2
TN_2017_441 |  |  |  | DRAKA COMTEQ 96FO 2006 | 13.89 | 11 | Vilanova | PENDING | -- | 61.3 | 18.9 | No | 2017-03-28 | E ou F_s2_d0 | 3.3 | 112.6 | 202.4 | 1158 | 238.1 | E ou F | 150 | 0.35 | s2 | n | n | d0
17030024 |  | 16681 | drum | 1800-S-1X95MM²-SH-NF F 55-625-255-2017-11-METRIQUE- | 22.7 | 7 | Paron | SV3200FR | -- | 39.9 | 21.7 | No | 2017-03-30 | B2_s1_d1 | 0.55 | 7.2 | 9.2 | 1104 | 20 | B2 | 14 | 0.03 | s1 | y | n | d1
TN_2017_442 |  | 20132706 | 249720K | AFUMEX EASY RZ1-K 0.6/1.0KV 5G50 | 32.61 | 6 | Vilanova | PENDING | -- | 59.5 | 19 | No | 2017-03-30 | C_s1_d2 | 0.88 | 15.1 | 36.7 | 1500 | 30.6 | C | 29.3 | 0.07 | s1 | n | y | d2
TN_2017_443 |  | 20132659 | 332773K | AFUMEX EASY RZ1-K 0.6/1.0KV 1X240 | 25.92 | 6 | Vilanova | PENDING | -- | 58.1 | 20.5 | No | 2017-03-30 | D_s2_d2 | 3.3 | 55.7 | 97 | 1476 | 115.3 | D | 99 | 0.26 | s2 | n | y | d2
TN_2017_444 |  | 20066684 | 146300X | VHOVMV-K 500V 10X2X1.5MM2 | 25.98 | 6 | Vilanova | PVC | -- | 77 | 16.7 | No | 2017-03-31 | C_s3_d0 | 0.72 | 17.4 | 19.7 | 999 | 100.3 | C | 711.9 | 0.89 | s3 | n | n | d0
TN_2017_445 |  | 61961 | 340356C | AFUMEX CLASS ATEX RZ1HZ1-K 1KV 1X240 | 35.68 | 5 | Vilanova | SXLPE+1602SEES+1602SEES | -- | 71.2 | 18.9 | No | 2017-03-31 | B2_s1_d1 | 0.74 | 7.2 | 10.2 | 1500 | 24.8 | B2 | 23 | 0.06 | s1 | y | n | d1
TN_2017_446 |  | 20066688 | 176744N | ESP 2205-1CEPSA V0VMV-K 500V 1X2X1.5 | 12.12 | 13 | Vilanova | PVC | -- | 63 | 12.6 | No | 2017-04-03 | C_s3_d0 | 0.84 | 15.4 | 25.9 | 564 | 264.3 | C | 465.8 | 1.92 | s3 | n | n | d0
TN_2017_447 |  | 20066774 | 337820W | VH0VMV-K 500V 20X2X1.5MM2 | 31.6 | 6 | Vilanova | PVC | -- | 61.3 | 13.4 | No | 2017-04-03 | C_s3_d0 | 0.9 | 18.1 | 22 | 939 | 63.8 | C | 909.2 | 1.16 | s3 | n | n | d0
TN_2017_448 |  | 61960 | 345898B | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 1X240 | 35.41 | 5 | Vilanova | SXLPE+T20R+1602SEES | -- | 55.5 | 17.2 | No | 2017-04-03 | B2_s1_d0 | 0.47 | 7.1 | 8.4 | 1233 | 22.9 | B2 | 22.9 | 0.05 | s1 | n | n | d0
|  | 61960 | 345898B | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 1X240 | 35.71 | 5 | CEIS | SXLPE+T20R+1602SEES | -- | 55 | 19.6 | No | 2017-05-10 | B2_s1_d0 | 0.65 | 5.7 | 8 | 1167 | 16.6 | B2 | 1.7 | 0 | s1 | n | n | d0
TN_2017_449 |  | 20067210 | 252747A | VH0VMV-K 500V 2X2X1.5MM2 | 17.9 | 8 | Vilanova | PVC | -- | 51.4 | 19.7 | No | 2017-04-03 | B2_s3_d0 | 0.79 | 12.8 | 22 | 645 | 142.2 | B2 | 524.3 | 1.58 | s3 | n | n | d0
TN_2017_450 |  | 61969 |  | SZ1-(AS+) UNIPOLAR 1X2.5MM2 | 5.98 | 25 | Vilanova | 1602SEES | -- | 59.6 | 15.9 | No | 2017-04-05 | C_s1_d2 | 1.2 | 16.9 | 36 | 564 | 238.1 | C | 31.6 | 0.07 | s1 | n | y | d2
TN_2017_451 |  | 62565 | 348276L | AL-RZ1 1X16MM² | 10.18 | 15 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 58.2 | 16.5 | No | 2017-04-05 | B2_s1_d2 | 0.99 | 14 | 21.9 | 927 | 45.2 | B2 | 37.5 | 0.06 | s1 | n | y | d2
|  | 62565 | 348276L | AL-RZ1 1X16MM² | 10.42 | 16 | CEIS | SXLPE+1420FEES+1602SEES | -- | 60 | 16.5 | No | 2017-05-10 | B2_s1_d1 | 0.55 | 7.6 | 14.6 | 708 | 38.4 | B2 | 5.7 | 0.02 | s1 | y | n | d1
TN_2017_452 |  |  | 239256L | RVMV-K 3G6MM2 | 17.31 | 9 | Vilanova | PENDING | -- | 61 | 16.9 | No | 2017-04-03 | D_s3_d2 | 1.62 | 30.7 | 44.5 | 897 | 74.5 | D | 554.9 | 0.96 | s3 | n | y | d2
TN_2017_453 |  |  | 261061M | RVMV-K 4X2.5MM² | 15.54 | 10 | Vilanova | PENDING | -- | 63.7 | 17.6 | No | 2017-04-05 | D_s3_d2 | 2.07 | 30.7 | 52.5 | 1035 | 84.3 | D | 682.7 | 1.17 | s3 | n | y | d2
TN_2017_454 |  | 62501 | 348272G | AFUMEX EASY RZ1-K 0.6/1.0KV 3G2.5 | 11.26 | 14 | Vilanova | 1420FEES95%/ADDITIVE5%BEDDINGAFUMEXCPR+1602SHEATHAFUMEXCPR | -- | 69.1 | 17.2 | No | 2017-04-06 | B2_s1_d0 | 1.15 | 14.4 | 24 | 828 | 45.5 | B2 | 14.1 | 0.03 | s1 | n | n | d0
TN_2017_455 |  | 62593 | 353620V | AFUMEX FIRS MRZ1-K (AS+) 1KV 1X2.5MM2 | 8.7 | 17 | Vilanova | SXLPE+1420FEES+5300SEIT | -- | 59.5 | 18.3 | No | 2017-04-06 | C_s1_d1 | 0.9 | 11 | 30.4 | 678 | 86.4 | C | 23.2 | 0.06 | s1 | y | n | d1
|  | 62593 | 353620V | AFUMEX FIRS MRZ1-K (AS+) 1KV 1X2.5MM2 | 8.95 | 17 | CEIS | SXLPE+1420FEES+5300SEIT | -- | 36 | 21.9 | No | 2017-04-06 | B2_s1_d0 | 0.75 | 11.2 | 22.8 | 753 | 56.9 | B2 | 5.3 | 0.01 | s1 | n | n | d0
TN_2017_456 |  | 62594 | 348293E | AFUMEX FIRS MRZ1-K (AS+) 1KV 1X25MM2 | 13.09 | 12 | Vilanova | SXLPE+1420FEES+5300SEIT | -- | 53.2 | 20.3 | No | 2017-04-06 | C_s1_d0 | 0.8 | 16.5 | 27 | 918 | 43.8 | C | 20.6 | 0.04 | s1 | n | n | d0
|  | 62594 | 348293E | AFUMEX FIRS MRZ1-K (AS+) 1KV 1X25MM2 | 13.31 | 12 | CEIS | SXLPE+1420FEES+5300SEIT | -- | 45 | 20.7 | No | 2017-04-06 | B2_s1_d0 | 0.8 | 11.3 | 21.9 | 945 | 45 | B2 | 4.4 | 0.01 | s1 | n | n | d0
TN_2017_457 |  | 62790 | 355092V | AFUMEX FIRS MRZ1-K (AS+) 1KV 1X240MM2 | 28.71 | 6 | Vilanova | SXLPE+1420FEES+5300SEIT | -- | 68.2 | 14.1 | No | 2017-04-07 | B2_s1_d0 | 0.49 | 4.8 | 7.1 | 717 | 17.4 | B2 | 10.2 | 0.03 | s1 | n | n | d0
|  | 62790 | 355092V | AFUMEX FIRS MRZ1-K (AS+) 1KV 1X240MM2 | 28.14 | 6 | CEIS | SXLPE+1420FEES+5300SEIT | -- | 50 | 18 | No | 2017-04-06 | B2_s1_d0 | 0.45 | 7.3 | 9.1 | 1494 | 25.4 | B2 | 1 | 0 | s1 | n | n | d0
TN_2017_458 |  | 62595 | 353623Y | AFUMEX FIRS MRZ1-K (AS+) 1KV 5G1.5MM2 | 13.03 | 12 | Vilanova | SXLPE+1420FEES+5300SEIT | -- | 64.9 | 14.8 | No | 2017-04-07 | C_s1_d0 | 0.74 | 15.1 | 26.3 | 1068 | 39 | C | 21 | 0.05 | s1 | n | n | d0
|  | 62595 | 353623Y | AFUMEX FIRS MRZ1-K (AS+) 1KV 5G1.5MM2 | 14.47 | 11 | CEIS | SXLPE+1420FEES+5300SEIT | -- | 45 | 19.3 | No | 2017-04-06 | B2_s1_d0 | 0.85 | 14.9 | 26.7 | 936 | 42.3 | B2 | 9.2 | 0.03 | s1 | n | n | d0
TN_2017_459 |  | 62596 | 352305R | AFUMEX FIRS MRZ1-K (AS+) 1KV 5G35MM2 | 32.28 | 6 | Vilanova | SXLPE+1420FEES+5300SEIT | -- | 58.5 | 17.3 | No | 2017-04-07 | B2_s1_d0 | 0.51 | 6 | 7 | 996 | 22.7 | B2 | 28.6 | 0.05 | s1 | n | n | d0
|  | 62596 | 352305R | AFUMEX FIRS MRZ1-K (AS+) 1KV 5G35MM2 | 31.79 | 6 | CEIS | SXLPE+1420FEES+5300SEIT | -- | 40 | 21.6 | No | 2017-04-06 | B2_s1_d0 | 0.65 | 4.6 | 6.9 | 1053 | 15.8 | B2 | 1.2 | 0 | s1 | n | n | d0
TN_2017_460 |  | 62596 | 348291G | AFUMEX FIRS MRZ1-K (AS+) 1KV 5G35MM2 | 32.1 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 54.5 | 18.9 | No | 2017-04-07 | B2_s1_d2 | 0.7 | 5.9 | 13.2 | 1476 | 16.5 | B2 | 16.1 | 0.06 | s1 | n | y | d2
TN_2017_461 |  | 62791 | 356579L | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 19.29 | 8 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 52.4 | 20.2 | No | 2017-04-07 | D_s2_d2 | 3.3 | 48 | 139.8 | 1491 | 118.1 | D | 95.4 | 0.23 | s2 | n | y | d2
TN_2017_462 |  | 62791 | 355055E | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 19.4 | 8 | Vilanova | SXLPE+1420FEES+5300SEIT | -- | 75.3 | 16.2 | No | 2017-04-12 | D_s2_d2 | 3.3 | 39.2 | 89.4 | 1320 | 87.8 | D | 67.7 | 0.19 | s2 | n | y | d2
TN_2017_463 |  | 62595 | 352304P | AFUMEX FIRS SZ1-K 1KV 5G1.5MM2 | 13.99 | 11 | Vilanova | BEDDINGAFUMEXCPR+SHEATHAFUMEXCPR | -- | 62.3 | 15.5 | No | 2017-04-11 | C_s1_d0 | 1.02 | 18.3 | 36 | 945 | 55.8 | C | 39.7 | 0.1 | s1 | n | n | d0
TN_2017_464 |  | 62593 | 348289A | AFUMEX FIRS SZ1-K 1KV (AS+) 1X2.5MM2 | 8.44 | 19 | Vilanova | BEDDINGAFUMEXCPR+SHEATHAFUMEXCPR | -- | 77.4 | 15.6 | No | 2017-04-12 | C_s1_d0 | 1.48 | 17.4 | 40.2 | 708 | 103.6 | C | 35.5 | 0.07 | s1 | n | n | d0
TN_2017_465 |  | 62594 | 352310W | AFUMEX FIRS SZ1-K 1KV (AS+) 1X25MM2 | 13.28 | 12 | Vilanova | BEDDINGAFUMEXCPR+SHEATHAFUMEXCPR | -- | 70.8 | 18.6 | No | 2017-04-12 | B2_s1_d1 | 0.84 | 13 | 22.1 | 1011 | 38.2 | B2 | 13.5 | 0.04 | s1 | y | n | d1
TN_2017_466 |  | 62790 | 353618T | AFUMEX FIRS SZ1-K 1KV (AS+) 1X240MM2 | 28.46 | 6 | Vilanova | BEDDINGAFUMEXCPR+SHEATHAFUMEXCPR | -- | 67.2 | 19.8 | No | 2017-04-12 | B2_s1_d0 | 0.52 | 11.5 | 18.9 | 1497 | 32.9 | B2 | 24.1 | 0.05 | s1 | n | n | d0
TN_2017_467 |  | -- | -- | CABLES RCT ARA-Z1 RZ1-K (AS) 0.6/1KV 3G1.5 | 10.07 | 15 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 58.6 | 21.2 | No | 2017-04-12 | D_s2_d0 | 2.8 | 35.5 | 51.8 | 951 | 111.2 | D | 81.7 | 0.14 | s2 | n | n | d0
TN_2017_468 |  |  |  | AFUMEX EASY RZ1-K 0.6/1.0KV 3G2.5 | 11.4 | 14 | Vilanova | 1420FEESBEDDINGAFUMEXCPR+1602SHEATHAFUMEXCPRWITHNANOFILLERS | -- | 73.7 | 15.19 | No | 2017-04-13 | C_s2_d1 | 1.5 | 22.7 | 34.8 | 852 | 69.4 | C | 79.9 | 0.11 | s2 | y | n | d1
TN_2017_469 |  | -- | -- | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G1.5MM2 | 10.43 | 15 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 71.6 | 16.2 | No | 2017-04-13 | D_s2_d2 | 2.03 | 32.1 | 38.6 | 1149 | 91.9 | D | 101.3 | 0.14 | s2 | n | y | d2
TN_2017_470 |  | -- | -- | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G2.5MM2 | 10.11 | 15 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 69.5 | 18.1 | No | 2017-04-13 | D_s2_d0 | 3.2 | 47 | 58.2 | 927 | 127.9 | D | 84.8 | 0.15 | s2 | n | n | d0
TN_2017_471 |  | -- | TH C33894 | PRYSMIAN FG16M16 1 KV 1X240 | 29.91 | 6 | Vilanova | SXLPE+04AKIT+5300SEIT | -- | 66 | 20.4 | No | 2017-04-13 | B2_s1_d0 | 0.3 | 3.1 | 4.4 | 684 | 14.4 | B2 | 39.7 | 0.06 | s1 | n | n | d0
TN_2017_472 |  | -- | TH D70831 | PRYSMIAN FG16M16 1 KV 1X240 | 30.48 | 6 | Vilanova | SXLPE+04AKIT+5300SEIT | -- | 62.7 | 21.8 | No | 2017-04-13 | B2_s1_d0 | 0.4 | 2.9 | 4.1 | 612 | 13.1 | B2 | 28.1 | 0.07 | s1 | n | n | d0
TN_2017_473 |  | -- | 12 B66008 | PRYSMIAN FG16M16 1 KV 1X240 | 30.11 | 6 | Vilanova | SXLPE+04AKIT+5300SEIT | -- | 78 | 15.8 | No | 2017-04-18 | B2_s1_d1 | 0.56 | 5 | 7.3 | 1440 | 18.8 | B2 | 10 | 0.03 | s1 | y | n | d1
TN_2017_474 |  | 62565 | 348276L | AL-RZ1 1X16MM2 | 10.18 | 15 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 76.7 | 16.6 | No | 2017-04-18 | C_s1_d1 | 0.94 | 21 | 28.2 | 954 | 64.6 | C | 39.2 | 0.06 | s1 | y | n | d1
TN_2017_475 |  | 61963 | 351626C | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 5G2.5 | 16.82 | 9 | Vilanova | SXLPE+T20R+1602SEES | -- | 74.1 | 18.8 | No | 2017-04-18 | B2_s2_d2 | 0.86 | 12.9 | 26.1 | 1230 | 28.1 | B2 | 52 | 0.09 | s2 | n | y | d2
17040005 |  | 16681 | -- | 1000-1X6MM²-SH-NF F55-625-255 | 7.9 | 19 | Paron | SW3800FR | -- | 31.9 | 21.5 | No | 2017-04-18 | B2_s1_d2 | 0.4 | 4 | 11.6 | 609 | 38 | B2 | 18 | 0.06 | s1 | y | y | d2
17040006 |  | 16681 | -- | 1000-3G10MM²-SH-NF F 55-625-255 | 17.48 | 9 | Paron | SW3800FR | -- | 27.2 | 22.3 | No | 2017-04-18 | B2_s1_d2 | 0.55 | 4 | 7.2 | 1374 | 9 | B2 | 8 | 0.02 | s1 | y | y | d2
TN_2017_476 |  | -- | 12THE57444 | PRYSMIAN FG16M16 1 KV 1X240 | 29.95 | 6 | Vilanova | SXLPE+04AKIT+5300SEIT | -- | 49.7 | 16.4 | No | 2017-04-19 | B2_s1_d1 | 0.4 | 3.6 | 4.4 | 834 | 14.2 | B2 | 26.5 | 0.05 | s1 | y | n | d1
TN_2017_477 |  | -- | 12THE57736 | PRYSMIAN FG16M16 1 KV 1X240 | 29.8 | 6 | Vilanova | SXLPE+04AKIT+5300SEIT | -- | 50.9 | 17.3 | No | 2017-04-19 | B2_s1_d0 | 0.4 | 3.9 | 6.1 | 1500 | 13.7 | B2 | 12.3 | 0.03 | s1 | n | n | d0
TN_2017_478 |  | -- | 345898B | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 1X240 | 35.41 | 5 | Vilanova | SXLPE+T20R+1602SEES | -- | 47.9 | 18 | No | 2017-04-19 | B2_s1_d0 | 0.48 | 6.3 | 8.3 | 1365 | 16.7 | B2 | 10.3 | 0.04 | s1 | n | n | d0
17040007 |  | 16681 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 | 3.01 | 165 | Paron | SV3600FR | -- | 23.8 | 20 | No | 2017-04-20 | D_s2_d0 | 3.3 | 48.8 | 112.4 | 1041 | 155 | D | 102 | 0.17 | s2 | n | n | d0
TN_2017_479 |  | 20213066 | T7-B01073 | FS17 1X1MM2 | 2.61 | 210 | Vilanova | 2600IPIT+28AASKIN | -- | 57.3 | 13.3 | No | 2017-04-20 | D_s2_d0 | 1.8 | 9.1 | 38.3 | 432 | 349.3 | D | 350.1 | 1.5 | s2 | n | n | d0
TN_2017_480 |  | -- | -- | FG16OR16 2X1.5 MM² - 0.6/1 KV | 10.01 | 15 | Vilanova | SXLPE+0500FPIT+2000SPIT | -- | 55.3 | 14 | No | 2017-04-20 | B2_s2_d0 | 0.74 | 6.9 | 22.1 | 612 | 94.5 | B2 | 150.5 | 0.55 | s2 | n | n | d0
TN_2017_481 |  | -- | -- | FG16OR16 2X1.5 MM² - 0.6/1 KV | 10.01 | 15 | Vilanova | SXLPE+0500FPIT+2000SPIT | -- | 47.5 | 16.7 | No | 2017-04-20 | B2_s2_d0 | 0.75 | 6.2 | 19.7 | 612 | 92.9 | B2 | 158.4 | 0.55 | s2 | n | n | d0
TN_2017_485 |  | -- | -- | FG16OR16 2X1.5 MM² - 0.6/1 KV | 10.01 | 15 | Vilanova | SXLPE+0500FPIT+2000SPIT | -- | 71 | 13.8 | No | 2017-04-24 | B2_s2_d0 | 0.75 | 8.8 | 18.4 | 651 | 88.7 | B2 | 165.1 | 0.57 | s2 | n | n | d0
TN_2017_486 |  | 62596 | 352305R | AFUMEX FIRS MRZ1-K (AS+) 1KV 5G35MM2 | 32.1 | 6 | Vilanova | SXLPE+1420FEES+5300SEIT | -- | 69.5 | 14.7 | No | 2017-04-24 | B2_s1_d1 | 0.55 | 5.2 | 7.8 | 1413 | 16.2 | B2 | 19.7 | 0.05 | s1 | y | n | d1
TN_2017_487 |  | 62596 | 348291G | AFUMEX FIRS MRZ1-K (AS+) 1KV 5G35MM2 | 32.28 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 69.1 | 17.6 | No | 2017-04-24 | B2_s1_d0 | 0.5 | 6 | 7.3 | 1371 | 22.8 | B2 | 15.4 | 0.04 | s1 | n | n | d0
TN_2017_488 |  | 20044885 | -- | AFUMEX PANELES ES07Z-R (AS) 750V 1X10 MM2 | 6.45 | 25 | Vilanova | SXLPE+15ABSEES | -- | 66.3 | 18.9 | No | 2017-04-24 | D_s2_d2 | 3.3 | 49.6 | 225.4 | 681 | 596.7 | D | 97.3 | 0.35 | s2 | n | y | d2
TN_2017_489 |  | 20044901 | -- | AFUMEX PANELES HO7ZR (AS) 750V 1X2.5MM2 | 3.75 | 105 | Vilanova | SXLPE+15ABSEES | -- | 63 | 20.3 | No | 2017-04-24 | _ _
17040008 |  | 16745 | -- | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.83 | 180 | Paron | 1602SEES | -- | 28.7 | 21.1 | No | 2017-04-26 | B2_s1_d0 | 0.85 | 9.4 | 21.8 | 792 | 51 | B2 | 13 | 0.03 | s1 | n | n | d0
17040009 |  | 16745 | -- | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.83 | 180 | Paron | 1602SEES | -- | 25.1 | 22.2 | No | 2017-04-26 | B2_s1_d0 | 0.95 | 8.1 | 17.2 | 894 | 31 | B2 | 14 | 0.03 | s1 | n | n | d0
17040010 |  | 16681 | -- | K27-100/170-21-0.9-04-2017-PRYSMIAN 255 | 24.7 | 7 | Paron | SW3800FR | -- | 30.2 | 20 | No | 2017-04-28 | B2_s1_d0 | 0.55 | 7.3 | 9.5 | 1038 | 21 | B2 | 24 | 0.03 | s1 | n | n | d0
17040011 |  | 16681 | -- | K22 2X1.6-SH-NF F 55-622-PRYSMIAN 255 | 13.6 | 11 | Paron | SW3800FR | -- | 31 | 20.9 | No | 2017-04-28 | B2_s1_d1 | 0.25 | 5.1 | 6.9 | 1023 | 20 | B2 | 11 | 0.02 | s1 | y | n | d1
TN_2017_490 |  |  | TA221680G | DRAKA 2017 24FO G652D | 11.01 | 14 | Vilanova | TUBOSSINGRASA+RELLENOSAFUMEX+1602SEES | -- | 74.8 | 15.7 | No | 2017-05-03 | C_s1_d0 | 1.35 | 12.9 | 32.9 | 633 | 124.6 | C | 28.9 | 0.08 | s1 | n | n | d0
TN_2017_491 |  |  | TA15K1204 | DRAKA 2017 48FO G652D | 12.64 | 12 | Vilanova | TUBOSSINGRASA+RELLENOSAFUMEX+1602SEES | -- | 72.4 | 16.6 | No | 2017-05-03 | C_s1_d0 | 1 | 14.1 | 31.8 | 711 | 86.4 | C | 43.2 | 0.12 | s1 | n | n | d0
TN_2017_492 |  |  | TA16K0023 | DRAKA 2017 24FO G652D | 12.91 | 12 | Vilanova | TUBOSSINGRASA+RELLENOSAFUMEX+1602SEES | -- | 67.8 | 18.1 | No | 2017-05-03 | C_s1_d0 | 1.17 | 14.7 | 31.3 | 729 | 93.3 | C | 27.1 | 0.04 | s1 | n | n | d0
TN_2017_493 |  |  | TA16K0051 | DRAKA 2017 16FO G652D | 11.15 | 14 | Vilanova | TUBOSSINGRASA+RELLENOSAFUMEX+1602SEES | -- | 67.7 | 18.9 | No | 2017-05-03 | D_s2_d2 | 3.3 | 55.6 | 70.5 | 951 | 134.9 | D | 61.1 | 0.1 | s2 | n | y | d2
TN_2017_494 |  |  | TA16K0078 | DRAKA 2017 512FO 10D KT MOVISTAR | 19.76 | 8 | Vilanova | TUBOSSINGRASA+RELLENOSAFUMEX+1602SEES | -- | 67.2 | 19.9 | No | 2017-05-03 | _ _
TN_2017_495 |  | 62596 | 348291G | AFUMEX FIRS MRZ1-K (AS+) 1KV 5G35MM2 | 32.28 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 84.7 | 14.7 | No | 2017-05-04 | B2_s1_d0 | 0.44 | 6.2 | 7.7 | 759 | 22 | B2 | 13 | 0.03 | s1 | n | n | d0
TN_2017_496 |  | 62596 | 352305R | AFUMEX FIRS MRZ1-K (AS+) 1KV 5G35MM2 | 32.1 | 6 | Vilanova | SXLPE+1420FEES+5300SEIT | -- | 83.7 | 15.5 | No | 2017-05-04 | B2_s1_d0 | 0.53 | 4.4 | 5.7 | 729 | 16.9 | B2 | 9.3 | 0.03 | s1 | n | n | d0
TN_2017_497 |  |  |  | FS17 1X1MM2 | 2.65 | 210 | Vilanova | 28AABASE+28AASKIN | -- | 78.5 | 17.9 | No | 2017-05-04 | B2_s2_d0 | 1.15 | 6.2 | 22.1 | 495 | 143.3 | B2 | 353.6 | 1.38 | s2 | n | n | d0
TN_2017_498 |  | 62565 | 348276L | AL-RZ1 1X16MM2 | 10.18 | 15 | Vilanova | SXLPE+1420FEES+1602SEES | -- | 72.6 | 19.01 | No | 2017-05-04 | C_s2_d2 | 1.3 | 17.6 | 33.6 | 711 | 86.7 | C | 59.5 | 0.13 | s2 | n | y | d2
17050001 |  | 16681 | -- | K27-100/170-21-0.9-ARME-05-2017-PRYSMIAN 255+METRIQUE | 30 | 6 | Paron | SW3800FR | -- | 48.4 | 21.4 | No | 2017-05-04 | B2_s1_d2 | 0.57 | 4.9 | 7.2 | 654 | 21 | B2 | 5 | 0.01 | s1 | n | y | d2
TN_2017_499 |  | 61998 | 345458Y | AFUMEX FIRS SZ1-K 5G35MM2 | 32.47 | 6 | Vilanova | SILASTIC+1420FEES+1602SEES | -- | 56.8 | 22.1 | No | 2017-05-08 | B2_s1_d2 | 0.7 | 8.2 | 12.9 | 1482 | 18.3 | B2 | 24.4 | 0.07 | s1 | n | y | d2
TN_2017_500 |  |  | TA30279 | DRAKA 2017 48FO G652D | 11.07 | 14 | Vilanova | 1602SEES | -- | 65 | 21.9 | No | 2017-05-09 | D_s2_d0 | 3 | 27.1 | 53.3 | 702 | 165.9 | D | 79.9 | 0.12 | s2 | n | n | d0
TN_2017_501 |  |  | TA16K0074 | DRAKA 2017 128FO G652 | 16.3 | 9 | Vilanova | DRYTUBES+RELLENOSAFUMEX+1602SEES | -- | 72.5 | 15.6 | No | 2017-05-09 | E ou F_s3_d2 | 3.3 | 75.9 | 185.6 | 1458 | 160.2 | E ou F | 213.2 | 1491 | s3 | n | y | d2
TN_2017_502 |  | 63417 | 332510W | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.96 | 8 | Vilanova | 1602SEES+5%NANOFILLERS | -- | 68.2 | 19.7 | No | 2017-05-09 | E ou F_s2_d2 | 3.3 | 95 | 266.5 | 1422 | 238.5 | E ou F | 125.4 | 0.29 | s2 | n | y | d2
TN_2017_503 |  | 63417 | 361726F | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.52 | 8 | Vilanova | 1602SEES+5%NANOFILLERS | -- | 60.5 | 21.9 | No | 2017-05-09 | D_s2_d2 | 1.18 | 27.2 | 99.5 | 1116 | 128.6 | D | 125.4 | 0.46 | s2 | n | y | d2
TN_2017_504 |  | 63417 | 363469A | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.69 | 8 | Vilanova | COPPERTAPEOVERLAP50%+MICATAPE+GFR365+5%NANOFILLERS | -- | 58.7 | 22.7 | No | 2017-05-09 | _ _
TN_2017_505 |  | 63417 | 361726F | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.52 | 8 | Vilanova | 1602SEES+5%NANOFILLERS | -- | 70.8 | 18.9 | No | 2017-05-10 | _ _
TN_2017_506 |  | 63417 | 363456L | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.51 | 8 | Vilanova | COPPERTAPEOVERLAP50%+GFR365+5%NANOFILLERS | -- | 62 | 22.3 | No | 2017-05-10 | D_s2_d2 | 3.3 | 21.2 | 220.3 | 771 | 467.7 | D | 29.5 | 0.42 | s2 | n | y | d2
TN_2017_507 |  |  |  | FS17 1X1MM2 | 2.65 | 210 | Vilanova | 28AABASE+28AASKIN | -- | 71.1 | 18.2 | No | 2017-05-15 | B2_s3_d0 | 1.15 | 5.9 | 20.2 | 492 | 126.8 | B2 | 371.3 | 1.53 | s3 | n | n | d0
TN_2017_508 |  |  | 362456Z | VARINET KRZ1KZ1-K 1KV 3X2.5/2.5MM2 | 13.79 | 11 | Vilanova | 1643SEES | -- | 67.9 | 19.6 | No | 2017-05-15 | _ _
TN_2017_509 |  |  | TA8534 | DRAKA 2017 IGN 16GO ORANGE ESPANA | 7.5 | 19 | Vilanova | GRASA+CYGSALHC-1800/R | -- | 54.4 | 23.8 | No | 2017-05-15 | D_s2_d2 | 3.3 | 49.1 | 118.2 | 942 | 232.4 | D | 83.9 | 0.23 | s2 | n | y | d2
TN_2017_510 |  |  | 123042S | EVOLUCION 1KV RZ1-K (AS) 1X6MM2 | 6.94 | 21 | Vilanova | 15ABSEES+4100 | -- | 49.2 | 24.6 | No | 2017-05-15 | D_s2_d2 | 3.3 | 54.3 | 261 | 774 | 552.3 | D | 64.3 | 0.21 | s2 | n | y | d2
TN_2017_511 |  |  | 197453Y | VARINET RZ1-KZ1-K 1KV 3X240/150 | 65 | 3 | Vilanova | 1643SEES | -- | 53 | 24.1 | No | 2017-05-16 | B2_s1_d0 | 0.65 | 5.9 | 7.5 | 1176 | 16.8 | B2 | 5.8 | 0.02 | s1 | n | n | d0
TN_2017_512 |  |  |  | H05Z-K 500V 1MM2 | 2.57 | 225 | Vilanova | PENDING | -- | 66.1 | 14.5 | No | 2017-05-19 | E ou F_s2_d1 | 3.3 | 79.8 | 246.4 | 774 | 556.4 | E ou F | 76.6 | 0.25 | s2 | y | n | d1
TN_2017_513 |  |  |  | H05Z-K 500V 0.50MM2 | 2.23 | 300 | Vilanova | PENDING | -- | 63.3 | 16.1 | No | 2017-05-19 | E ou F_s2_d1 | 3.3 | 75.7 | 242 | 723 | 593.4 | E ou F | 59.5 | 0.2 | s2 | y | n | d1
TN_2017_514 |  |  |  | HO7Z-K 750V 1X50 | 12.04 | 13 | Vilanova | PENDING | -- | 51 | 19.5 | No | 2017-05-19 | D_s1_d2 | 2.63 | 15.3 | 31 | 675 | 82.8 | D | 28.4 | 0.06 | s1 | n | y | d2
TN_2017_515 |  |  | T7-F85957 | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.63 | 11 | Vilanova | S-XLPE+04ALFEIT+5300SEIT | -- | 70.4 | 22.8 | No | 2017-05-22 | B2_s1_d1 | 0.82 | 11.7 | 21.3 | 1110 | 26.3 | B2 | 13.9 | 0.03 | s1 | y | n | d1
TN_2017_516 |  |  | T7-F85812 | FG16OR16 7G2.5 MM² - 0.6/1 KV | 15.81 | 9 | Vilanova | S-XLPE+0500FPIT+2000SPIT | -- | 68 | 23.2 | No | 2017-05-22 | B2_s2_d0 | 0.7 | 6.1 | 11.6 | 948 | 35.5 | B2 | 119.8 | 0.28 | s2 | n | n | d0
TN_2017_517 |  |  | T8-F67998 | FG16OR16 24G1.5 MM² - 0.6/1 KV | 23.6 | 7 | Vilanova | S-XLPE+0500FPIT+2000SPIT | -- | 74 | 19 | No | 2017-05-23 | C_s2_d0 | 1.15 | 15.2 | 30.4 | 1479 | 52.2 | C | 246.3 | 0.38 | s2 | n | n | d0
TN_2017_518 |  |  | T7-F85950 | FG16R16 1X70MM² - 0.6/1 KV | 17.84 | 8 | Vilanova | S-XLPE+0500FPIT+2000SPIT | -- | 69.1 | 19.1 | No | 2017-05-23 | B2_s2_d2 | 0.85 | 11.6 | 23.4 | 1155 | 33.7 | B2 | 119.1 | 0.23 | s2 | n | y | d2
TN_2017_519 |  |  | T7-F85952 | FG16OM16 7G2.5 MM² - 0.6/1 KV | 16.02 | 9 | Vilanova | S-XLPE+04ALFEIT+5300SEIT | -- | 60.7 | 23.1 | No | 2017-05-23 | B2_s1_d2 | 0.55 | 9.8 | 18.9 | 1389 | 21.8 | B2 | 13.6 | 0.03 | s1 | n | y | d2
TN_2017_520 |  |  | T8-F68004 | FG16OM16 16G2.5 MM² - 0.6/1 KV | 21.28 | 7 | Vilanova | S-XLPE+04ALFEIT+5300SEIT | -- | 59.8 | 23.7 | No | 2017-05-23 | B2_s1_d0 | 0.34 | 1.7 | 3.4 | 1500 | 6 | B2 | 0.2 | 0 | s1 | n | n | d0
TN_2017_521 |  |  | TA6966 | DRAKA 2016 64FO 10D KUT MOVISTAR | 15.44 | 10 | Vilanova | CIGSA+TUBOSGRASA | -- | 56.1 | 24.7 | No | 2017-05-23 | _ _
TN_2017_522 |  |  | TA2921 | DRAKA 2016 CDS 3 365A 12 FO 6.657A2 UT UFINET TELECOM | 7.9 | 19 | Vilanova | 1500+TUBOSGRASA | -- | 65 | 20.3 | No | 2017-05-24 | D_s2_d1 | 3.3 | 49.9 | 219.3 | 681 | 610.7 | D | 86.4 | 0.3 | s2 | y | n | d1
TN_2017_523 |  |  | TA3700 | R TELEFONO-INTERNET-TV DRAKA 2015 64FO G-657 A2 | 11.23 | 14 | Vilanova | CIGSA+TUBOSGRASA | -- | 61 | 22 | No | 2017-05-24 | D_s2_d2 | 3.3 | 67.3 | 155.8 | 1041 | 211 | D | 111.8 | 0.26 | s2 | n | y | d2
TN_2017_524 |  |  | TA15K1363 | DRAKA M 2016 ING 96 FO ORANGE ESPANA | 13.08 | 12 | Vilanova | CIGSA+TUBOSGRASA | -- | 51.9 | 25.2 | No | 2017-05-24 | E ou F_s2_d2 | 3.3 | 82.2 | 190.2 | 1095 | 257.6 | E ou F | 149.2 | 0.53 | s2 | n | y | d2
TN_2017_525 |  |  | T8-F68002 | FG16OM16 24G1.5 MM² - 0.6/1 KV | 22.87 | 7 | Vilanova | S-XLPE+04ALFEIT+5300SEIT | -- | 49.2 | 25.8 | No | 2017-05-24 | B2_s1_d2 | 0.45 | 2 | 4.3 | 1500 | 7.1 | B2 | 13.6 | 0.02 | s1 | n | y | d2
TN_2017_526 |  |  | T8-F67999 | FG16OR16 16G2.5 MM² - 0.6/1 KV | 21.64 | 7 | Vilanova | S-XLPE+0500FPIT+2000SPIT | -- | 48.5 | 26.6 | No | 2017-05-24 | C_s2_d1 | 1.2 | 16.6 | 31.9 | 1326 | 45.2 | C | 259.7 | 0.43 | s2 | y | n | d1
TN_2017_527 |  |  | 365932C | AFUMEX GULD RZ1-K 1 KV 3G1.5 | 7.84 | 19 | Vilanova | 1643SEES | -- | 61 | 20.1 | No | 2017-05-29 | D_s2_d2 | 3.3 | 62.4 | 233.8 | 888 | 397.7 | D | 77.9 | 0.28 | s2 | n | y | d2
|  |  | 365932C | AFUMEX GULD RZ1-K 1 KV 3G1.5 | 7.75 | 19 | CEIS | 1643SEES | -- | 30 | 39.2 | No | 2017-06-15 | E ou F_s2_d2 | 3.2 | 71.4 | 223.6 | 837 | 423.9 | E ou F | 60.1 | 0.24 | s2 | n | y | d2
TN_2017_528 |  |  | 335177Y | RHVMV 3X185 2017 | 75 | 3 | Vilanova | 6010+PVC2400 | -- | 50.3 | 24 | No | 2017-05-29 | B2_s3_d2 | 0.8 | 8.9 | 9.7 | 621 | 58.8 | B2 | 683.6 | 1.21 | s3 | n | y | d2
TN_2017_529 |  |  | T8-F67998 | FG16OR16 24G1.5 MM² - 0.6/1 KV | 23.6 | 7 | Vilanova | S-XLPE+0500FPIT+2000SPIT | -- | 51.4 | 24.7 | No | 2017-05-29 | C_s2_d2 | 1.3 | 18.6 | 37.3 | 1485 | 68.3 | C | 185.6 | 0.53 | s2 | n | y | d2
TN_2017_530 |  |  | T7-F85950 | FG16R16 1X70MM² - 0.6/1 KV | 17.84 | 8 | Vilanova | S-XLPE+0500FPIT+2000SPIT | -- | 51.5 | 25.2 | No | 2017-05-29 | B2_s2_d1 | 1.15 | 12.4 | 25.3 | 1176 | 36.6 | B2 | 145.6 | 0.33 | s2 | y | n | d1
TN_2017_531 |  |  | T7-F85952 | FG16OM16 7G2.5 MM² - 0.6/1 KV | 16.02 | 9 | Vilanova | S-XLPE+04ALFEIT+5300SEIT | -- | 66.7 | 21.9 | No | 2017-05-30 | B2_s1_d2 | 0.75 | 8.5 | 19.7 | 1377 | 18.3 | B2 | 16.9 | 0.03 | s1 | n | y | d2
TN_2017_532 |  |  | T7-F85812 | FG16OR16 7G2.5 MM² - 0.6/1 KV | 15.81 | 9 | Vilanova | S-XLPE+0500FPIT+2000SPIT | -- | 64.4 | 21 | No | 2017-05-30 | B2_s2_d0 | 0.75 | 9.3 | 19.7 | 861 | 58.7 | B2 | 166.5 | 0.34 | s2 | n | n | d0
TN_2017_533 |  |  | T7-F85957 | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.63 | 11 | Vilanova | S-XLPE+04ALFEIT+5300SEIT | -- | 69.6 | 21.3 | No | 2017-05-30 | B2_s1_d0 | 0.75 | 9 | 13.9 | 1329 | 24.1 | B2 | 6.1 | 0.02 | s1 | n | n | d0
TN_2017_534 |  |  | T8-F68002 | FG16OM16 24G1.5 MM² - 0.6/1 KV | 22.87 | 7 | Vilanova | S-XLPE+04ALFEIT+5300SEIT | -- | 70.4 | 21.5 | No | 2017-05-30 | B2_s1_d0 | 0.35 | 3.8 | 5.4 | 1494 | 14.5 | B2 | 0 | 0 | s1 | n | n | d0
TN_2017_535 |  |  | T8-F67999 | FG16OR16 16G2.5 MM² - 0.6/1 KV | 21.64 | 7 | Vilanova | S-XLPE+0500FPIT+2000SPIT | -- | 63.6 | 22.9 | No | 2017-05-30 | C_s2_d1 | 1.14 | 15.8 | 33.9 | 1353 | 39.4 | C | 213.5 | 0.38 | s2 | y | n | d1
TN_2017_536 |  |  | T8-F68004 | FG16OM16 16G2.5 MM² - 0.6/1 KV | 21.28 | 7 | Vilanova | S-XLPE+04ALFEIT+5300SEIT | -- | 64.7 | 19.3 | No | 2017-05-31 | B2_s1_d2 | 0.5 | 4 | 8.7 | 1500 | 14.5 | B2 | 0.6 | 0.01 | s1 | n | y | d2
TN_2017_537 |  |  | FE15307564 | ADIF DRAKA 17 96FO MN-TKEST | 20.76 | 7 | Vilanova | CYGSALHC-1800/R | -- | 61.7 | 20.3 | No | 2017-05-31 | _ _
TN_2017_538 |  |  | TA7641 | R TELEFONO_INTERNET_TELEVISION DRAKA 2017 4FO G-657A2 | 6.12 | 25 | Vilanova | 1500SEES | -- | 48.9 | 23.7 | No | 2017-05-31 | E ou F_s1_d1 | 3.3 | 56.7 | 333.5 | 555 | 1344.8 | E ou F | 43.8 | 0.17 | s1 | y | n | d1
TN_2017_539 |  |  | FE15307597 | ADIF DRAKA 17 96FO MN-TKEST | 21.41 | 7 | Vilanova | MEGOLONS-540 | -- | 45.8 | 24.6 | No | 2017-05-31 | _ _
TN_2017_540 |  |  | T8 F68037 | PRYSMIAN FG16M16 1 KV1 1X50 | 16.45 | 9 | Vilanova | TNT+04AL+5300 | -- | 65 | 19.1 | No | 2017-06-01 | B2_s1_d1 | 0.42 | 6.4 | 10.2 | 1500 | 22.8 | B2 | 0 | 0 | s1 | y | n | d1
TN_2017_541 |  |  | 348000L | HO7Z-K 750V 1X25 | 9.21 | 17 | Vilanova | GFR-325 | -- | 60.3 | 20.3 | No | 2017-06-01 | D_s1_d2 | 3.3 | 26.1 | 33.8 | 852 | 77.1 | D | 25.9 | 0.05 | s1 | n | y | d2
TN_2017_542 |  |  | T8 F69041 | PRYSMIAN FG16M16 1 KV 1X50 | 16.44 | 9 | Vilanova | CARTA+04AL+5300 | -- | 58.1 | 23.4 | No | 2017-06-01 | B2_s1_d2 | 0.37 | 5.5 | 7.4 | 1260 | 23.2 | B2 | 0.5 | 0.01 | s1 | n | y | d2
TN_2017_543 |  |  | T8 F68024 | PRYSMIAN FG16M16 1 KV 1X16 | 11.34 | 14 | Vilanova | SXLPE+CARTA+04ALFEIT+5300SEIT | -- | 48.4 | 25 | No | 2017-06-01 | B2_s1_d0 | 0.57 | 7.8 | 15.5 | 861 | 44.7 | B2 | 5.5 | 0.02 | s1 | n | n | d0
TN_2017_544 |  |  | T8 F68024 | PRYSMIAN FG16M16 1 KV 1X16 | 11.34 | 14 | Vilanova | SXLPE+CARTA+04ALFEIT+5300SEIT | -- | 87.1 | 18.5 | No | 2017-06-05 | B2_s1_d1 | 0.47 | 9.1 | 15.1 | 894 | 41.4 | B2 | 17.4 | 0.03 | s1 | y | n | d1
TN_2017_545 |  |  | 50 m | ADIF DRAKA 17 96FO MN TKEST | 21.25 | 7 | Vilanova | 1602SEES | -- | 85.6 | 19.4 | No | 2017-06-05 | E ou F_s2_d2 | 3.3 | 93.5 | 245.1 | 1392 | 226.6 | E ou F | 136 | 0.22 | s2 | n | y | d2
TN_2017_546 |  |  | 10 A39934 | FG16R16 1X16MM² - 0.6/1 KV | 10.9 | 14 | Vilanova | TALCO+0500FPIT+2000SPIT | -- | 80.6 | 20.5 | No | 2017-06-05 | B2_s2_d0 | 0.74 | 5.6 | 13.7 | 753 | 80.8 | B2 | 86 | 0.33 | s2 | n | n | d0
TN_2017_547 |  |  | 50 m | ADIF DRAKA 32FO MN TKEST | 16.09 | 9 | Vilanova | 1602SEES | -- | 80.9 | 20.1 | No | 2017-06-05 | D_s2_d2 | 1.8 | 36 | 50.4 | 1020 | 96.3 | D | 71.6 | 0.12 | s2 | n | y | d2
TN_2017_548 |  |  | T8F68033 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.95 | 12 | Vilanova | S-XLPE+TALCUM+0500FPIT+2000SPIT | -- | 76.5 | 21.8 | No | 2017-06-05 | B2_s2_d2 | 0.9 | 11.9 | 27.6 | 747 | 64.9 | B2 | 169.2 | 0.47 | s2 | n | y | d2
TN_2017_549 |  | 63773 | 368300B | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 1X240 | 34.63 | 5 | Vilanova | XLPE+1602+LANTORTAPE50MM25%+1602SEES | -- | 79.2 | 19.6 | No | 2017-06-06 | B2_s1_d0 | 0.37 | 4 | 4.9 | 1137 | 12.7 | B2 | 1.5 | 0.02 | s1 | n | n | d0
|  |  | 368300B | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 1X240 | 34.78 | 5 | CEIS | XLPE+1602+LANTORTAPE50MM25%+1602SEES | -- | 30 | 36.62 | No | 2017-06-15 | B2_s1_d0 | 0.45 | 5.4 | 7.1 | 1218 | 18.5 | B2 | 0.7 | 0 | s1 | n | n | d0
TN_2017_550 |  | 63772 | 368271V | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 5G2.5 | 16.85 | 9 | Vilanova | XLPE+1602+LANTORTAPE30MM25%+1602SEES | -- | 77.6 | 21 | No | 2017-06-06 | B2_s1_d1 | 0.69 | 10.6 | 18.5 | 1227 | 57.9 | B2 | 0.8 | 0.01 | s1 | y | n | d1
|  |  | 368271V | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 5G2.5 | 16.77 | 9 | CEIS | XLPE+1602+LANTORTAPE50MM25%+1602SEES | -- | 30 | 40.06 | No | 2017-06-15 | B2_s1_d1 | 0.75 | 12.5 | 23.8 | 1122 | 29 | B2 | 10.4 | 0.03 | s1 | y | n | d1
TN_2017_551 |  | 63774 | 368337S | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.75 | 8 | Vilanova | XLPE+COPPERTAPE50%+LANTORTAPE50MM25%+1602SEES | -- | 69.5 | 23.2 | No | 2017-06-06 | E ou F_s2_d2 | 3.3 | 71.9 | 143.8 | 1416 | 155.3 | E ou F | 132.7 | 0.27 | s2 | n | y | d2
TN_2017_552 |  | 63527 | 368282G | RVMV-K 1KV 3G2.5MM2 | 14.77 | 10 | Vilanova | XLPE+6010+LANTORTAPE30MM25%+GFR365 | -- | 64.5 | 24.3 | No | 2017-06-06 | D_s1_d2 | 3.3 | 69.4 | 145.1 | 1452 | 127.6 | D | 7.7 | 0.02 | s1 | n | y | d2
TN_2017_553 |  | 63528 | 368303E | RVMV-K 1KV 3G50MM2 | 21.54 | 7 | Vilanova | XLPE+6010+LANTORTAPE30MM25%+GFR365 | -- | 61.3 | 25.4 | No | 2017-06-06 | C_s2_d2 | 1.35 | 26.8 | 44.3 | 1176 | 60.9 | C | 267.9 | 0.36 | s2 | n | y | d2
TN_2017_554 |  | 63529 | 368327F | RVMV-K 1KV 3G10MM2 | 33.18 | 6 | Vilanova | XLPE+6010+LANTORTAPE50MM25%+GFR365 | -- | 72 | 21.2 | No | 2017-06-07 | C_s1_d2 | 1.14 | 16.9 | 31 | 1470 | 32.7 | C | 1.1 | 0.01 | s1 | n | y | d2
TN_2017_555 |  | 63775 | 368292T | RVMV-K 1KV 3G2.5MM2 | 15.62 | 9 | Vilanova | XLPE+6010+ARMADO+LANTORTAPE30MM25%+6010AA | -- | 661 | 22.8 | No | 2017-06-07 | D_s1_d2 | 1.85 | 31.6 | 52 | 1086 | 66.2 | D | 17.7 | 0.05 | s1 | n | y | d2
TN_2017_556 |  | 63775 | 368294V | RVMV-K 1KV 3G2.5MM2 | 15.17 | 10 | Vilanova | XLPE+6010+ARMADO+6010AA | -- | 64.2 | 22.7 | No | 2017-06-07 | E ou F_s1_d2 | 3.3 | 97.2 | 186.7 | 1380 | 173.7 | E ou F | 19.8 | 0.06 | s1 | n | y | d2
TN_2017_557 |  | 63776 | 366615V | RVMV-K 1KV 3G10 MM2 | 22.08 | 7 | Vilanova | XLPE+6010+LANTORTAPE30MM25%+6010AA | -- | 55.9 | 23.9 | No | 2017-06-07 | C_s2_d2 | 1.05 | 17.8 | 23.5 | 1398 | 48.7 | C | 145.9 | 0.25 | s2 | n | y | d2
TN_2017_558 |  |  | FE15307598 | CYGSA ADIF TKEST 32F | 15.25 | 10 | Vilanova | CYGSA | -- | 83.2 | 21 | No | 2017-06-08 | _ _
TN_2017_559 |  |  | FE15307565 | MEGALON TKEST 32F | 15.56 | 9 | Vilanova | MEGOLONS-540 | -- | 76.7 | 22.4 | No | 2017-06-08 | C_s2_d2 | 1.54 | 25 | 38.8 | 882 | 70.6 | C | 87.2 | 0.13 | s2 | n | y | d2
TN_2017_560 |  | 63776 | 366600D | RVMV-K 1KV 3G10 MM2 | 21.9 | 7 | Vilanova | XLPE+6010+ARMADO+6010AA | -- | 70.8 | 23.7 | No | 2017-06-08 | C_s2_d2 | 1.28 | 17.2 | 25.8 | 729 | 72.5 | C | 308 | 0.44 | s2 | n | y | d2
TN_2017_561 |  | 63777 | 368289P | RVMV-K 1KV 3G50 MM2 | 32.3 | 6 | Vilanova | XLPE+6010+ARMADO+6010AA | -- | 73.3 | 24.4 | No | 2017-06-08 | C_s1_d2 | 0.97 | 17.8 | 29.2 | 1476 | 47.7 | C | 0 | 0 | s1 | n | y | d2
TN_2017_562 |  |  | T8F68029 | FG16R16 1X10MM² - 0.6/1 KV | 9.88 | 15 | Vilanova | S-XLPE+TALCUM+0500FPIT+2000SPIT | -- | 83.5 | 20.6 | No | 2017-06-09 | B2_s2_d0 | 0.7 | 4.8 | 12.7 | 669 | 58.7 | B2 | 92.3 | 0.32 | s2 | n | n | d0
TN_2017_563 |  | 63774 | 366601E | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18 | 8 | Vilanova | XLPE+COPPERTAPE50%+MICATAPE40MM25%+LANTORTAPE30MM25+1602SEES | -- | 81.5 | 21.6 | No | 2017-06-09 | C_s2_d2 | 0.97 | 19.6 | 43.7 | 1494 | 37.7 | C | 53.7 | 0.15 | s2 | n | y | d2
TN_2017_564 |  | 63775 | 366611R | RVMV-K 1KV 3G2.5 MM2 | 14.53 | 10 | Vilanova | XLPE+6010+ARMADO+TAPELANDOR30MM25%+6010AB | -- | 70.1 | 23.8 | No | 2017-06-09 | D_s1_d2 | 1.85 | 33 | 50.7 | 1035 | 72 | D | 5.7 | 0.03 | s1 | n | y | d2
TN_2017_565 |  | 63775 | 366604H | RVMV-K 1KV 3G2.5 MM2 | 14.69 | 10 | Vilanova | XLPE+6010SEES+ARMADO+6010AB | -- | 68 | 24.4 | No | 2017-06-09 | D_s1_d2 | 2.23 | 47.4 | 65.3 | 1329 | 98.1 | D | 0.3 | 0.01 | s1 | n | y | d2
TN_2017_566 |  | 63776 | 368301C | RVMV-K 1KV 3G10 MM2 | 21.54 | 7 | Vilanova | XLPE+6010SEES+LANTORTAPE30MM25%+6010AB | -- | 51.6 | 22.1 | No | 2017-06-12 | C_s2_d2 | 1.34 | 21.9 | 31.7 | 1245 | 56 | C | 226.2 | 0.39 | s2 | n | y | d2
TN_2017_567 |  | -- | -- | FR-N1X1G1 12X1.5 MM² | 16.52 | 9 | Vilanova | SXLPE+SCAPATAPE+0400FEIT+5300SEIT | -- | 46.5 | 26 | No | 2017-06-12 | B2_s1_d0 | 0.36 | 3.2 | 6.6 | 1455 | 13.5 | B2 | 2.1 | 0.02 | s1 | n | n | d0
17060001 |  | 16821 | -- | K27-100/170-21-0.9-ARME-05-2017-PRYSMIAN 255+METRIQUE | 30 | 6 | Paron | SILICONE+20AKSEIT | -- | 53 | 23.6 | No | 2017-06-08 | B2_s1_d0 | 0.42 | 4.2 | 5.3 | 645 | 15 | B2 | 11 | 0.02 | s1 | n | n | d0
17060002 |  | 16821 | -- | K27-100/170-21-0.9-ARME-05-2017-PRYSMIAN 255+METRIQUE | 30 | 6 | Paron | SILICONE+SW3800FR | -- | 48 | 25.8 | No | 2017-06-08 | B2_s1_d0 | 0.27 | 4.3 | 5.7 | 693 | 19 | B2 | 13 | 0.02 | s1 | n | n | d0
17060003 |  | 16821 | -- | 1800-S-1X240MM²-SH-NF F 55-625-255 | 32.2 | 6 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 47.7 | 21.5 | No | 2017-06-13 | B2_s1_d0 | 0.52 | 5.5 | 6.8 | 978 | 18 | B2 | 3 | 0 | s1 | n | n | d0
17060004 |  | 16821 | -- | 750-19X1.5-SH-NF F 55-625-255 | 21.7 | 7 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 47.7 | 22 | No | 2017-06-13 | B2_s1_d0 | 0.3 | 4 | 6.3 | 789 | 17 | B2 | 4 | 0.01 | s1 | n | n | d0
17060005 |  | 16821 | -- | 1000-3G10MM²-SH-NF F 55-625-255 | 17.4 | 9 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 45.7 | 23.8 | No | 2017-06-13 | B2_s1_d2 | 0.7 | 8.8 | 18 | 1380 | 18 | B2 | 11 | 0.04 | s1 | y | y | d2
17060006 |  | 16821 | -- | HO7Z1-K- 1X10MM² EN VERSION IRRADIÉE (20MRAD) | 6.2 | 25 | Paron | 1602SEES | -- | 42.5 | 24.8 | No | 2017-06-13 | B2_s1_d0 | 0.82 | 5 | 15.6 | 633 | 54 | B2 | 21 | 0.09 | s1 | n | n | d0
17060007 |  | 16821 | -- | 1000-3G10MM²-SH-NF F 55-625-255 | 17.4 | 9 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 68.8 | 26.9 | No | 2017-06-15 | B2_s1_d2 | 0.65 | 7.9 | 15 | 1500 | 21 | B2 | 11 | 0.03 | s1 | y | y | d2
17060008 |  | 16821 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 ( IRRADIÉ) | 2.86 | 165 | Paron | 5300SEIT | -- | 65.9 | 27.1 | No | 2017-06-15 | B2_s1_d0 | 0.67 | 5 | 11.7 | 690 | 36 | B2 | 5 | 0.01 | s1 | n | n | d0
17060009 |  | 16821 | -- | 1800-S-1X400MM²-SH-NF F 55-625-255 | 37.7 | 5 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 61 | 28.2 | No | 2017-06-15 | B2_s1_d0 | 0.53 | 4.2 | 5.2 | 1230 | 12 | B2 | 5 | 0.01 | s1 | n | n | d0
TN_2017_568 |  |  | T8 F69041 | PRYSMIAN FG16M16 1 KV 1X50 | 16.44 | 9 | Vilanova | CARTA+04AL+5300 | -- | 61.4 | 22.2 | No | 2017-06-13 | B2_s1_d1 | 0.44 | 4.3 | 9.8 | 1497 | 16.9 | B2 | 2.1 | 0.01 | s1 | y | n | d1
TN_2017_569 |  | 63416 | 349592S | RVMV-K 2X35 MM² | 33.72 | 5 | Vilanova | HEPR+GRI141+ARMAOURED+GRI141 | -- | 59.3 | 23.4 | No | 2017-06-13 | B2_s1_d0 | 0.52 | 7.3 | 10.6 | 1209 | 14 | B2 | 7.3 | 0.02 | s1 | n | n | d0
TN_2017_570 |  |  | T8 F68037 | PRYSMIAN FG16M16 1 KV 1X50 | 16.45 | 9 | Vilanova | TNT+04AL+5300 | -- | 49.7 | 26.6 | No | 2017-06-13 | B2_s1_d0 | 0.42 | 3.4 | 5.5 | 558 | 21.2 | B2 | 7.3 | 0.01 | s1 | n | n | d0
TN_2017_571 |  | 63778 | 349568R | RRFWZ1 2X35 MM² | 35.83 | 5 | Vilanova | XLPE+GFR325+CORRUGATED+LANTORTAPE+1602 | -- | 48.4 | 27.8 | No | 2017-06-13 | _s1_d0 |  | 6.8 | 9.3 | 1500 | 22.9 |  | 1.9 | 0.01 | s1 | n | n | d0
17060010 |  | 16821 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 ( IRRADIÉ) | 2.86 | 165 | Paron | 20AKSEIT | -- | 57.2 | 26.3 | No | 2017-06-20 | B2_s1_d0 | 0.7 | 5.8 | 13.6 | 735 | 37 | B2 | 13 | 0.03 | s1 | n | n | d0
17060011 |  | 16819 | -- | ORANGE DRAKA 20/2017 L1041/1 MM 12FO UNI G652D OHC | 6.2 | 25 | Paron | 1700SEIT | -- | 53 | 26 | No | 2017-06-20 | D_s1_d2 | 3 | 27.3 | 62.1 | 633 | 218 | D | 44 | 0.08 | s1 | y | y | d2
17010008 |  | 16622 | drum | FR-N1X1G1 5G1.5MM² | 13 | 12 | ISSEP | SXLPE+0400FEIT+5300SEIT | -- | 47 | 26 | No | 2017-06-21 | B2_s1_d2 | 0.78 | 8.7 | 15.8 | 1209 | 26.7 | B2 | 10.3 | 0.02 | s1 | y | y | d2
17010012 |  | 16821 | drum | K25 750V 1X1.5 -SH-NF F 55-625-255 ( IRRADIÉ) | 2.86 | 165 | Paron | 1602SEES | -- | 55.2 | 28.8 | No | 2017-06-22 | B2_s1_d0 | 1.1 | 9.3 | 25.4 | 753 | 65 | B2 | 21 | 0.06 | s1 | n | n | d0
17010013 |  | 16821 | drum | K22 2X1.6-SH-NF F 55-622-PRYSMIAN 255 | 13.6 | 11 | Paron | SW3800FR | -- | 28.9 | 30.5 | No | 2017-06-22 | B2_s1_d1 | 0.2 | 1.9 | 3.1 | 555 | 10 | B2 | 6 | 0.01 | s1 | y | n | d1
17010014 |  | 16821 | drum | K25 750V 1X1.5 -SH-NF F 55-625-255 ( IRRADIÉ) | 2.86 | 165 | Paron | SW3800FR | -- | 65.4 | 25.1 | No | 2017-06-27 | B2_s1_d0 | 0.9 | 7.1 | 20.5 | 831 | 39 | B2 | 34 | 0.07 | s1 | n | n | d0
17010015 |  | 16838 | drum | PRYSMIAN 255-EAXECEGB-F2-8.7/15 KV -1*240/25-36MM-09-2015 | 39.2 | 5 | Paron | SW3800FR | -- | 67.3 | 26 | No | 2017-06-27 | B2_s1_d0 | 0.55 | 4.4 | 6.3 | 786 | 17 | B2 | 13 | 0.02 | s1 | n | n | d0
TN_2017_572 |  |  |  | FR-N1X1G1 12X1.5 MM² | 16.51 | 9 | Vilanova | ISOLÉIX1100FRGAINE0400FEIT+20AKSEES | -- | 83.8 | 23.7 | No | 2017-06-20 | B2_s1_d2 | 0.5 | 9.1 | 20.9 | 1500 | 20.5 | B2 | 0.9 | 0.01 | s1 | n | y | d2
TN_2017_573 |  |  |  | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 5G35MM² | 29.34 | 6 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 83 | 25 | No | 2017-06-20 | B2_s1_d0 | 0.43 | 5.2 | 8.7 | 705 | 23 | B2 | 2.2 | 0.01 | s1 | n | n | d0
TN_2017_574 |  |  |  | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 1X240 | 26.31 | 6 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 74.7 | 26.5 | No | 2017-06-20 | C_s1_d2 | 0.9 | 11.6 | 36.6 | 1500 | 30.5 | C | 0.2 | 0.01 | s1 | n | y | d2
TN_2017_575 |  |  |  | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 1X240MM² | 27.05 | 6 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 64.8 | 28.5 | No | 2017-06-20 | B2_s1_d2 | 0.74 | 8.3 | 23 | 1491 | 26.9 | B2 | 0 | 0 | s1 | n | y | d2
TN_2017_576 |  |  |  | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 5G35MM² | 29.73 | 6 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 73.3 | 23.8 | No | 2017-06-21 | B2_s1_d0 | 0.5 | 6.6 | 8.7 | 735 | 24.9 | B2 | 4.7 | 0.01 | s1 | n | n | d0
TN_2017_577 |  |  | 365932C | AFUMEX GULD RZ1-K 1 KV 3G1.5 | 7.84 | 19 | Vilanova | 1643SEES | -- | 67 | 27.1 | No | 2017-06-21 | D_s2_d2 | 3.3 | 69.9 | 256.4 | 804 | 508.8 | D | 66.1 | 0.25 | s2 | n | y | d2
TN_2017_578 |  |  | 366601E | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18 | 8 | Vilanova | XLPE+COPPERTAPE50%+MICATAPE40MM25%+LANTORTAPE30MM25+1602SEES | -- | 65.5 | 28.7 | No | 2017-06-21 | C_s1_d2 | 0.97 | 23.4 | 43.7 | 1497 | 45.6 | C | 33.4 | 0.1 | s1 | n | y | d2
|  |  | 366601E | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.05 | 8 | CEIS | XLPE+COPPERTAPE50%+MICATAPE40MM25%+LANTORTAPE30MM25+1602SEES | -- | 40 | 30.71 | No | 2017-06-15 | D_s1_d2 | 1.35 | 32.6 | 70.3 | 1467 | 60.3 | D | 43.8 | 0.15 | s1 | n | y | d2
TN_2017_579 |  |  |  | TOP CABLE TOXFREE ZH C RZ1-K (AS) 1KV 3G2.5 | 11.31 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 73.1 | 24 | No | 2017-06-23 | C_s2_d0 | 1.48 | 19.2 | 32.7 | 858 | 58.6 | C | 68.1 | 0.13 | s2 | n | n | d0
TN_2017_580 |  |  |  | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G2.5MM2 | 10.76 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 73.3 | 24.8 | No | 2017-06-23 | D_s1_d2 | 3 | 33.1 | 49.3 | 1386 | 68.3 | D | 46.5 | 0.1 | s1 | n | y | d2
TN_2017_581 |  |  |  | TOP CABLE TOXFREE ZH C RZ1-K (AS) 1KV 3G1.5 | 10.7 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 63.4 | 28.3 | No | 2017-06-23 | B2_s1_d0 | 0.58 | 9.1 | 16.1 | 720 | 42.3 | B2 | 10.2 | 0.03 | s1 | n | n | d0
TN_2017_582 |  |  |  | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G1.5MM2 | 10.11 | 15 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 80.9 | 23.5 | No | 2017-06-26 | D_s2_d2 | 3.3 | 42.2 | 78.4 | 1497 | 75.6 | D | 88.4 | 0.16 | s2 | n | y | d2
TN_2017_583 |  |  | 10 A39934 | FG16R16 1X16MM² - 0.6/1 KV | 10.9 | 14 | Vilanova | TALCO+0500FPIT+2000SPIT | -- | 72 | 24.9 | No | 2017-06-27 | B2_s2_d0 | 0.62 | 5.8 | 12.3 | 747 | 55.2 | B2 | 97 | 0.3 | s2 | n | n | d0
TN_2017_584 |  |  | T8F68026 | FG16OR16 2X1.5 MM² - 0.6/1 KV | 9.41 | 17 | Vilanova | S-XLPE+TALCUM+0500FPIT+2000SPIT | -- | 74 | 25 | No | 2017-06-27 | B2_s2_d0 | 1.25 | 9.5 | 26.9 | 585 | 95.3 | B2 | 298.1 | 0.89 | s2 | n | n | d0
TN_2017_585 |  |  | T8F68033 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.95 | 12 | Vilanova | S-XLPE+TALCUM+0500FPIT+2000SPIT | -- | 70.9 | 27 | No | 2017-06-27 | B2_s2_d2 | 0.93 | 11.7 | 28 | 720 | 66.6 | B2 | 188.4 | 0.56 | s2 | n | y | d2
TN_2017_586 |  | 63777 | 366610P | RVMV-K 3G50 MM² (2RH) | 33.17 | 6 | Vilanova | XLPE+6010SEES+ARMOURED+LANTORTAPE50MM25%+6010AB | -- | 69.6 | 27.2 | No | 2017-06-27 | B2_s1_d2 | 0.7 | 9.5 | 14.7 | 1494 | 24 | B2 | 2.3 | 0.01 | s1 | n | y | d2
TN_2017_587 |  | 63777 | 368295W | RVMV-K 3G50 MM² (2RH) | 33.55 | 5 | Vilanova | XLPE+6010SEES+ARMOURED+6010AB | -- | 67.9 | 27.7 | No | 2017-06-27 | B2_s1_d2 | 0.84 | 14.3 | 22 | 1497 | 57.2 | B2 | 5.5 | 0.02 | s1 | n | y | d2
TN_2017_588 |  | 63777 | 366608M | RVMV-K 3G50 MM² (2RH) | 33.54 | 5 | Vilanova | XLPE+6010SEES+ARMOURED+LANTORTAPE50MM25%+6010AA | -- | 80.2 | 23.4 | No | 2017-06-28 | B2_s1_d2 | 0.93 | 9.1 | 12.8 | 1500 | 26.5 | B2 | 1 | 0 | s1 | n | y | d2
TN_2017_589 |  |  | 293275L | REF3Z1-K (S) 2X95 MM² ADIF | 33.36 | 5 | Vilanova | RAVALENE+6000 | -- | 55.5 | 26 | No | 2017-06-28 | D_s2_d2 | 2.05 | 39.4 | 123.4 | 1497 | 103.4 | D | 97.2 | 0.17 | s2 | n | y | d2
TN_2017_590 |  |  | D40904 | RFI 2017 CAT 8041222-TE 2X(2X0.94) H5MFM | 19.58 | 8 | Vilanova | PENDING | -- | 49.6 | 27.2 | No | 2017-06-28 | D_s1_d2 | 2.1 | 44.6 | 83.2 | 1140 | 99 | D | 34.5 | 0.12 | s1 | n | y | d2
TN_2017_591 |  |  | 349593T | REF3Z1-K ALUMINIO ADIF 2X50 MM² ADIF | 28.84 | 6 | Vilanova | RAVALENE+6000 | -- | 40.5 | 28.8 | No | 2017-06-28 | D_s1_d2 | 3.3 | 45 | 236.3 | 1002 | 336.6 | D | 25.5 | 0.18 | s1 | n | y | d2
17070001 |  | 16864 | -- | 1000-1X6MM²-SH-NF F55-625-255 | 8 | 19 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 65.7 | 25.1 | No | 2017-07-10 | B2_s1_d0 | 0.67 | 5.2 | 9.8 | 504 | 58 | B2 | 9 | 0.02 | s1 | n | n | d0
17070002 |  | 16864 | -- | 750-5G35-SH-NF F 55-625-255 | 34 | 5 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 59.9 | 24.4 | No | 2017-07-10 | B2_s1_d1 | 0.45 | 2.5 | 4 | 618 | 12 | B2 | 1 | 0 | s1 | y | n | d1
17070003 |  | 16864 | -- | 750-5G35-SH-NF F 55-625-255 | 34 | 5 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 55 | 26.5 | No | 2017-07-10 | B2_s1_d2 | 0.4 | 3.4 | 4.4 | 600 | 12 | B2 | 3 | 0.01 | s1 | y | y | d2
17070004 |  | 16859 | -- | RED ELEC RHZ1-RA-2OL (AS) 1X2000MM2 127/220KV +T375AL | 122 | 2 | Paron | XLPE+TUBEAL+6000SEESGRIS+SKINSC | -- | 61.3 | 23.8 | No | 2017-07-12 | B2_s1_d2 | 0.85 | 8.7 | 13.1 | 861 | 27.6 | B2 | 9.9 | 0.02 | s1 | y | y | d2
17070005 |  | 16864 | -- | 1000-3X95MM²+1X50MM²-SH-NF F55-625-255 | 40 | 5 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 61.4 | 24.3 | No | 2017-07-12 | B2_s1_d0 | 0.55 | 2.5 | 3.6 | 873 | 7 | B2 | 4 | 0.01 | s1 | n | n | d0
17070006 |  | 16864 | -- | 750-5G50-SH-NF F 55-625-255 | 37.4 | 5 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 57.9 | 23.9 | No | 2017-07-13 | B2_s1_d0 | 0.4 | 4 | 4.6 | 1128 | 13 | B2 | 3 | 0 | s1 | n | n | d0
17070007 |  | 16864 | -- | 1000-SS-1X95MM²-SH-NF F 55-625-255-2017/28 | 23.6 | 7 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 58.8 | 25.5 | No | 2017-07-13 | B2_s1_d2 | 0.7 | 3.1 | 9.7 | 1494 | 9 | B2 | 4 | 0.03 | s1 | y | y | d2
TN_2017_592 |  |  | 376975F | AFUMEX CLASS RZ1-K (AS) 1KV 12G1.5 | 15.74 | 9 | Vilanova | SXLPE+LANTORTAPE+1420FEES+1602SEES | -- | 79.7 | 23.1 | No | 2017-07-10 | C_s2_d2 | 1.36 | 23.1 | 46.6 | 1431 | 44.4 | C | 56.7 | 0.08 | s2 | n | y | d2
TN_2017_593 |  |  |  | HO7Z-K 750V 1X1.5 | 2.97 | 165 | Vilanova | PENDINGTOCONFIRM | -- | 78.6 | 23.9 | No | 2017-07-10 | E ou F_s1_d1 | 3.3 | 81.6 | 265.8 | 723 | 653.1 | E ou F | 23.2 | 0.08 | s1 | y | n | d1
TN_2017_594 |  |  | C56254 | FG7H1M2 1X500 12/20 KV | 58.1 | 4 | Vilanova | ID7900-SV27AHIT | -- | 70.6 | 26.6 | No | 2017-07-10 | B2_s1_d2 | 0.35 | 8.3 | 22.8 | 1500 | 19 | B2 | 14.6 | 0.08 | s1 | n | y | d2
TN_2017_595 |  |  |  | HO7Z-K 750V 1X2.5 | 3.53 | 120 | Vilanova | PENDINGTOCONFIRM | -- | 70.4 | 26.9 | No | 2017-07-10 | E ou F_s1_d2 | 3.3 | 81.3 | 249.6 | 828 | 520.6 | E ou F | 43.5 | 0.11 | s1 | n | y | d2
TN_2017_596 |  |  |  | HO7Z-K 750V 1X4 | 4.22 | 75 | Vilanova | PENDINGTOCONFIRM | -- | 66.6 | 28.2 | No | 2017-07-10 | E ou F_s1_d1 | 3.3 | 72.9 | 203.9 | 867 | 361.3 | E ou F | 40.3 | 0.09 | s1 | y | n | d1
TN_2017_597 |  |  |  | HO7Z1-K (AS) 750V TOXFREE | 2.95 | 165 | Vilanova | LSOH | -- | 78.3 | 24 | No | 2017-07-11 | C_s2_d1 | 2 | 19.9 | 32.8 | 936 | 82.9 | C | 50.1 | 0.1 | s2 | y | n | d1
TN_2017_598 |  |  | 376342T | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.38 | 8 | Vilanova | COPPERTAPE50%+MICATAPE50%+LANTORTAPE25%+1420+1602SEES | -- | 76.1 | 24.7 | No | 2017-07-11 | C_s1_d2 | 1.28 | 19.3 | 48 | 1488 | 40.6 | C | 28.2 | 0.09 | s1 | n | y | d2
TN_2017_599 |  | OP63408 | 375199A | 2X2.5 MM2 RVMV-K | 20.58 | 7 | Vilanova | 41AA+ARMOURED+GRI141MUD | -- | 65.5 | 25.7 | No | 2017-07-11 | C_s2_d2 | 0.86 | 16.6 | 31.5 | 1359 | 30.9 | C | 55.9 | 0.09 | s2 | n | y | d2
TN_2017_600 |  | OP 63415 | 370576A | 2X35 MM2 RVMV-K | 32.12 | 6 | Vilanova | 41AA+ARMOURED+GRI141MUD | -- | 65.6 | 28.1 | No | 2017-07-11 | B2_s1_d2 | 0.48 | 8.7 | 14.4 | 1476 | 16 | B2 | 18.3 | 0.04 | s1 | n | y | d2
TN_2017_601 |  |  | E71840 | FG9 1X2.5 | 3.85 | 90 | Vilanova | IRI368 | -- | 64.5 | 28.5 | No | 2017-07-11 | D_s1_d2 | 3.3 | 55.8 | 183.7 | 846 | 336.4 | D | 43.1 | 0.1 | s1 | n | y | d2
TN_2017_602 |  |  | OF764 | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 73.8 | 27.5 | No | 2017-07-14 | C_s1_d2 | 1.01 | 15.6 | 31.2 | 1497 | 31.2 | C | 9.6 | 0.02 | s1 | n | y | d2
TN_2017_603 |  |  |  | AFUMEX CLASS RZ1-K (AS) 1KV 4G1.5 | 11.44 | 14 | Vilanova | 1420+PENDINGTOCONFIRM | -- | 77.3 | 23.3 | No | 2017-07-18 | C_s1_d2 | 1.25 | 19.3 | 25.2 | 882 | 53 | C | 25.6 | 0.06 | s1 | n | y | d2
TN_2017_604 |  |  |  | MIGUELEZ AFIRENAS H07Z1-K 1X1.5MM2 | 2.83 | 180 | Vilanova | COMPETITORSAMPLE | -- | 75 | 24.3 | No | 2017-07-18 | C_s2_d1 | 1.75 | 23.2 | 40.6 | 735 | 98.2 | C | 57.3 | 0.13 | s2 | y | n | d1
TN_2017_605 |  |  | OF18 | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 70.8 | 26.8 | No | 2017-07-18 | B2_s2_d2 | 1.06 | 14.5 | 26.8 | 1467 | 29.8 | B2 | 71.8 | 0.09 | s2 | n | y | d2
17070008 |  | 16864 | -- | 1000-4X240MM²-SH-NF F55-625-255 | 64.4 | 3 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 57.1 | 26 | No | 2017-07-18 | B2_s1_d0 | 0.35 | 2.4 | 3.3 | 1167 | 2 | B2 | 4 | 0.01 | s1 | n | n | d0
17070009 |  | 16864 | -- | 750-2X2.15MM2-SH-NF F 55-625-255 | 10.8 | 14 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 53.5 | 27.8 | No | 2017-07-18 | B2_s1_d2 | 0.7 | 8.6 | 13.7 | 858 | 34 | B2 | 22 | 0.03 | s1 | y | y | d2
17070010 |  | 16864 | -- | FR-N1X1G1 5G1.5MM² | 12.6 | 12 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 48.4 | 29.6 | No | 2017-07-18 | B2_s2_d2 | 1.05 | 14.5 | 24 | 1197 | 45 | B2 | 64 | 0.22 | s2 | y | y | d2
TN_2017_606 |  |  |  | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.93 | 165 | Vilanova | LSOH | -- | 69.2 | 27.7 | No | 2017-07-18 | D_s1_d1 | 2.9 | 34.3 | 50.2 | 819 | 117.1 | D | 30.6 | 0.05 | s1 | y | n | d1
TN_2017_607 |  | OP61981 | 372234C | VOLTALENE RH5Z1 (AS) 20KV 1X95K AL | 30.8 | 6 | Vilanova | XLPE+ALFOIL+6000SEESRED | -- | 63.1 | 29.2 | No | 2017-07-18 | E ou F_s1_d2 | 3.3 | 89.7 | 314.2 | 1491 | 263.8 | E ou F | 26.3 | 0.19 | s1 | n | y | d2
TN_2017_608 |  | OP 63411 | 376331F | PRYSMIAN SAP 63411 AFUMEX DZ 6001KV 2X4MM2 | 21.02 | 7 | Vilanova | 41AA+ARMADURA+GRI141MUD | -- | 80.9 | 24.1 | No | 2017-07-19 | B2_s1_d2 | 0.69 | 14.2 | 27.9 | 1449 | 24.3 | B2 | 34.5 | 0.06 | s1 | n | y | d2
TN_2017_609 |  | OP 61982 | 367414N | VOLTALENE RH5Z1 (AS) 30KV 1X400K AL | 45.58 | 4 | Vilanova | XLPE+ALFOIL+6000SEESRED | -- | 77.9 | 25.1 | No | 2017-07-19 | D_s1_d2 | 1.6 | 42.3 | 59.8 | 1071 | 80.2 | D | 12.7 | 0.04 | s1 | n | y | d2
TN_2017_610 |  |  |  | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 68.9 | 27.6 | No | 2017-07-19 | C_s1_d2 | 1.07 | 14.5 | 31.1 | 1494 | 32.7 | C | 0.3 | 0.01 | s1 | n | y | d2
17070011 |  | 16864 | -- | 1800-S-1*16-SH-NF F 55-625-255 | 15.3 | 10 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 54.5 | 26.5 | No | 2017-07-20 | B2_s1_d2 | 0.85 | 11.9 | 26.7 | 1095 | 34 | B2 | 33 | 0.09 | s1 | y | y | d2
17070012 |  | 16864 | -- | 1800-S-1X240MM²-SH-NF F 55-625-255 | 31.4 | 6 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 51.5 | 26.9 | No | 2017-07-20 | B2_s1_d0 | 0.55 | 2.9 | 3.6 | 696 | 10 | B2 | 4 | 0.01 | s1 | n | n | d0
17070013 |  | 16864 | -- | 1000-1X240MM²-SH-NF F55-625-255 | 31.5 | 6 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 45.9 | 27.3 | No | 2017-07-20 | B2_s1_d0 | 0.4 | 2.2 | 3.6 | 693 | 9 | B2 | 3 | 0 | s1 | n | n | d0
TN_2017_611 |  |  |  | AFUMEX CLASS RZ1-K (AS) 1KV 4G2.5 | 11.98 | 13 | Vilanova | 1420+PENDINGTOCONFIRM | -- | 60.2 | 28.9 | No | 2017-07-19 | D_s1_d1 | 2.08 | 32.6 | 50 | 1287 | 62.8 | D | 31.4 | 0.06 | s1 | y | n | d1
TN_2017_612 |  | OP 61983 | 381843X | VOLTALENE RH5Z1 (AS) 30KV 1X150K AL | 36.42 | 5 | Vilanova | XLPE+ALFOIL+6000SEESRED | -- | 59.1 | 29.6 | No | 2017-07-19 | D_s1_d2 | 3.3 | 61.3 | 189.8 | 1185 | 214.4 | D | 16.7 | 0.08 | s1 | n | y | d2
TN_2017_613 |  |  |  | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 62.9 | 28.8 | No | 2017-01-20 | C_s1_d2 | 1.25 | 28.1 | 42.1 | 1491 | 70.4 | C | 13.6 | 0.03 | s1 | n | y | d2
TN_2017_614 |  |  |  | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 74.9 | 24.2 | No | 2017-07-21 | B2_s1_d2 | 1 | 7.7 | 18 | 1500 | 22.7 | B2 | 13.9 | 0.03 | s1 | n | y | d2
TN_2017_615 |  |  |  | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 74.9 | 24.2 | No | 2017-07-21 | B2_s1_d2 | 1.02 | 8.5 | 16.8 | 1320 | 19.8 | B2 | 19 | 0.02 | s1 | n | y | d2
17070014 |  | 16864 | -- | 750-2X2.15MM2-SH-NF F 55-625-255 | 10.8 | 14 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 63.3 | 22.2 | No | 2017-07-25 | B2_s1_d1 | 0.7 | 8.2 | 12.8 | 828 | 34 | B2 | 32 | 0.05 | s1 | y | n | d1
17070015 |  | 16864 | -- | 1000-SS-1X95MM²-SH-NF F 55-625-255-2017/28 | 23.6 | 5 | Paron | ID3100FR/SV3300FR+5300SEIT | -- | 64 | 22 | No | 2017-07-25 | B2_s1_d2 | 0.67 | 4.5 | 13.3 | 1500 | 11 | B2 | 7 | 0.04 | s1 | y | y | d2
17070016 |  | 16864 | -- | 1000-SS-1X95MM²-SH-NF F 55-625-255-2017-11-METRIQUE-CE6467 M/ESS-883 | 22.7 | 7 | Paron | ID3100FR/SV3300FR+5300SEIT | -- | 65.3 | 22 | No | 2017-07-25 | B2_s1_d2 | 0.53 | 6.2 | 9 | 1011 | 17 | B2 | 13 | 0.03 | s1 | y | y | d2
17070017 |  | 16864 | -- | 750-5G35-SH-NF F 55-625-255 | 34 | 5 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 60.4 | 23.4 | No | 2017-07-25 | B2_s1_d0 | 0.55 | 1.7 | 3.2 | 717 | 9 | B2 | 2 | 0 | s1 | n | n | d0
TN_2017_616 |  |  | 345739D | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.23 | 14 | Vilanova | SXLPE+15ABSEES | -- | 82.7 | 21.8 | No | 2017-07-24 | E ou F_s2_d2 | 3.3 | 90.6 | 288.2 | 969 | 430.9 | E ou F | 64.6 | 0.16 | s2 | n | y | d2
TN_2017_617 |  |  | OF764 | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 68 | 25 | No | 2017-07-24 | B2_s1_d2 | 1.03 | 6.2 | 12.4 | 1413 | 13.5 | B2 | 0.1 | 0 | s1 | n | y | d2
TN_2017_618 |  |  | 383161E | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 40.64 | 5 | Vilanova | HEPR+1420FEES+6000SEES | -- | 55.9 | 23.9 | No | 2017-07-25 | C_s1_d2 | 1.36 | 25.8 | 39.2 | 1245 | 45.8 | C | 7.4 | 0.02 | s1 | n | y | d2
TN_2017_619 |  |  | 374325A | AL-HEPRZ1(AS) 1X400MM2 12/20KV | 45.62 | 4 | Vilanova | HEPR+1420FEES+6000SEES | -- | 54.7 | 24 | No | 2017-07-25 | B2_s1_d2 | 0.96 | 13.5 | 16.3 | 1494 | 32.2 | B2 | 5.5 | 0.01 | s1 | n | y | d2
TN_2017_620 |  |  |  | DRAKA 2017 1FO 10D 7A2 INT MOVISTAR 162060 | 4.31 | 75 | Vilanova | PENDINGMGARCIA | -- | 51.8 | 25.2 | No | 2017-07-25 | E ou F_s1_d1 | 3.3 | 72.4 | 158.5 | 816 | 312.2 | E ou F | 44.1 | 0.13 | s1 | y | n | d1
TN_2017_621 |  |  | 383127T | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 43.45 | 5 | Vilanova | XLPE+1420FEES+6000SEES | -- | 55.4 | 22.5 | No | 2017-07-26 | C_s1_d2 | 1.43 | 28.4 | 40.2 | 1176 | 51.2 | C | 9.8 | 0.06 | s1 | n | y | d2
TN_2017_622 |  |  | 382244H | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 51.91 | 4 | Vilanova | XLPE+1420FEES+6000SEES | -- | 53.1 | 22.9 | No | 2017-07-26 | C_s1_d2 | 1.21 | 23.4 | 38.6 | 1380 | 38.2 | C | 4.3 | 0.01 | s1 | n | y | d2
TN_2017_623 |  |  | 338151C | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 50.7 | 25.9 | No | 2017-07-26 | C_s1_d2 | 1.5 | 24.8 | 42.7 | 1497 | 40.3 | C | 16.3 | 0.02 | s1 | n | y | d2
TN_2017_624 |  |  | 338151C | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 56.7 | 25.9 | No | 2017-07-26 | B2_s1_d2 | 1.3 | 9.9 | 20 | 1494 | 16.7 | B2 | 12.3 | 0.04 | s1 | n | y | d2
17070018 |  |  | -- | FR-N1 X1G1-U- 5G6MM² | 17.4 | 9 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 57.2 | 22.6 | No | 2017-07-28 | B2_s1_d2 | 0.75 | 9.8 | 24 | 1416 | 22 | B2 | 9 | 0 | s1 | y | y | d2
TN_2017_625 |  |  | OF764 | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 74.3 | 22.3 | No | 2017-07-27 | B2_s1_d2 | 1.07 | 6.1 | 16.6 | 1500 | 13.8 | B2 | 9.1 | 0.02 | s1 | n | y | d2
TN_2017_626 |  |  | OF764 | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 72.7 | 22.9 | No | 2017-07-27 | B2_s1_d2 | 1.22 | 12.4 | 26.7 | 1458 | 23.3 | B2 | 4.4 | 0.01 | s1 | n | y | d2
TN_2017_627 |  |  | 338151C | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 70.2 | 26.2 | No | 2017-07-27 | B2_s1_d2 | 1.23 | 9.5 | 20 | 1497 | 18.6 | B2 | 8.3 | 0.01 | s1 | n | y | d2
TN_2017_629 |  |  | 382231U | RHZ1-OL (AS) 1X500MM AL-VOLTALENE 12_20KV | 51.91 | 4 | Vilanova | XLPE+1420FEES+6000SEES | -- | 84.7 | 24.5 | No | 2017-07-28 | C_s1_d2 | 1.3 | 23.5 | 35.4 | 1218 | 40.3 | C | 2.7 | 0.01 | s1 | n | y | d2
TN_2017_633 |  |  | 338151C | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 96.34 | 2 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 76.8 | 27.1 | No | 2017-07-28 | B2_s1_d2 | 1.21 | 5.5 | 10.9 | 1491 | 11.6 | B2 | 1.9 | 0.01 | s1 | n | y | d2
TN_2017_634 |  |  | 62OD12351 | DRAKA 32 FO ORANGE | 10.22 | 15 | Vilanova | PENDINGMGARCIA | -- | 72 | 28.2 | No | 2017-07-28 | D_s2_d2 | 3.3 | 44.9 | 94.5 | 1083 | 166 | D | 72.8 | 0.13 | s2 | n | y | d2
TN_2017_635 |  |  | 62OD16K0132 | DRAKA 64 FO ORANGE | 11.11 | 14 | Vilanova | PENDINGMGARCIA | -- | 67.9 | 29.4 | No | 2017-07-28 | D_s2_d2 | 3.3 | 53.1 | 174.4 | 849 | 319.6 | D | 80.5 | 0.25 | s2 | n | y | d2
TN_2017_636 |  |  |  | INDOOR CABLE ORANGE 3 MM | 2.86 | 180 | Vilanova | PENDINGMGARCIA | -- | 74.3 | 24.6 | No | 2017-07-31 | C_s1_d0 | 1.27 | 15.4 | 31.1 | 687 | 115.4 | C | 15.5 | 0.04 | s1 | n | n | d0
TN_2017_637 |  |  | 383161E | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 40.64 | 5 | Vilanova | HEPR+1420FEES+6000SEES | -- | 68.8 | 28.4 | No | 2017-07-31 | C_s1_d2 | 1.22 | 24.7 | 37.9 | 1260 | 42.1 | C | 14.4 | 0.03 | s1 | n | y | d2
TN_2017_638 |  |  | 382244H | AL-HEPRZ1(AS) 1X630MM2 12/20KV | 54.62 | 4 | Vilanova | HEPR+1420FEES+6000SEES | -- | 69.5 | 29.1 | No | 2017-07-31 | C_s1_d2 | 1.56 | 28.4 | 50.4 | 1476 | 47.3 | C | 5.4 | 0.01 | s1 | n | y | d2
TN_2017_639 |  |  | 383127T | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 43.45 | 5 | Vilanova | XLPE+1420FEES+6000SEES | -- | 68 | 29.9 | No | 2017-07-31 | D_s1_d2 | 1.51 | 32 | 53.1 | 1197 | 59.2 | D | 12.7 | 0.02 | s1 | n | y | d2
TN_2017_640 |  |  | 383127T | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 43.45 | 5 | Vilanova | XLPE+1420FEES+6000SEES | -- | 76.3 | 27.4 | No | 2017-08-01 | C_s1_d2 | 1.25 | 24.4 | 36.2 | 1332 | 41.7 | C | 27.8 | 0.04 | s1 | n | y | d2
TN_2017_641 |  |  | 383127T | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 43.45 | 5 | Vilanova | XLPE+1420FEES+6000SEES | -- | 78.9 | 27.5 | No | 2017-08-01 | D_s1_d2 | 1.67 | 32 | 48.3 | 1155 | 57.3 | D | 10.6 | 0.09 | s1 | n | y | d2
TN_2017_642 |  |  | 382231U | RHZ1-OL (AS) 1X500MM AL-VOLTALENE 12_20KV | 51.91 | 4 | Vilanova | XLPE+1420FEES+6000SEES | -- | 76.9 | 30.22 | No | 2017-08-01 | C_s1_d2 | 1.4 | 26.9 | 51.7 | 1494 | 45.2 | C | 0 | 0 | s1 | n | y | d2
TN_2017_643 |  |  | 07-F85584 | AFUMEX GOLD 1KV 5G1.5 IEMMEQU | 16.09 | 9 | Vilanova | CARTA+0600FEIT+5300SEIT | -- | 72.3 | 24.5 | No | 2017-08-02 | C_s1_d2 | 1.2 | 22.1 | 37.6 | 1281 | 40.2 | C | 20.1 | 0.04 | s1 | n | y | d2
TN_2017_644 |  |  | T7-F85790 | FG16ORG16 TOP 1KV 3G2.5 | 11.21 | 14 | Vilanova | TALCO+05ABFPIT+2000SPIT | -- | 66.1 | 28.2 | No | 2017-08-02 | B2_s2_d0 | 0.9 | 10.8 | 23.7 | 636 | 79 | B2 | 153.1 | 0.47 | s2 | n | n | d0
TN_2017_645 |  |  | 07-F85634 | AFUMEX GOLD 1KV 5G1.5 IEMMEQU | 15.58 | 9 | Vilanova | SKINLSOH+CARTA+0600FEIT+5300SEIT | -- | 64.1 | 29.1 | No | 2017-08-02 | C_s1_d1 | 0.9 | 16.4 | 29.5 | 1266 | 31.8 | C | 12.6 | 0.03 | s1 | y | n | d1
TN_2017_646 |  |  | 07-F85594 | AFUMEX GOLD 1KV 5G1.5 IEMMEQU | 16.02 | 9 | Vilanova | SCAPA+0600FEIT+5300SEIT | -- | 61.9 | 30.8 | No | 2017-08-02 | C_s1_d2 | 0.81 | 18.8 | 29.8 | 1194 | 42.2 | C | 12.9 | 0.04 | s1 | n | y | d2
TN_2017_647 |  |  | Gron | RED ELEC RHZ1-RA-2OL (AS) 1X2000MM2 127/220KV +T375AL | 121 | 2 | Vilanova | XLPE+TUBEAL+6000SEESGRIS+SKINSC | -- | 58.7 | 28.2 | No | 2017-08-03 | B2_s1_d0 | 0.81 | 8.5 | 12.4 | 744 | 30 | B2 | 3.5 | 0.01 | s1 | n | n | d0
TN_2017_648 |  |  | 241546A | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 77 | 3 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 49.2 | 31 | No | 2017-08-03 | C_s1_d2 | 1 | 23 | 37.1 | 1500 | 44.6 | C | 7 | 0.01 | s1 | n | y | d2
TN_2017_649 |  |  | Gron | RED ELEC RHZ1-RA-2OL (AS) 1X2000MM2 127/220KV +T375AL | 121 | 2 | Vilanova | XLPE+TUBEAL+6000SEESGRIS+SKINSC | -- | 46.1 | 22.7 | No | 2017-08-03 | B2_s1_d2 | 0.89 | 11.6 | 16 | 687 | 41.7 | B2 | 31.6 | 0.04 | s1 | n | y | d2
TN_2017_650 |  |  | 241546A | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 77 | 3 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | -- | 72.3 | 26.2 | No | 2017-08-04 | B2_s1_d2 | 1.25 | 11 | 19.4 | 1497 | 23.6 | B2 | 7.4 | 0.02 | s1 | n | y | d2
TN_2017_651 |  |  | 383134A | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 43.97 | 5 | Vilanova | XLPE+1420FEES+6000SEES | -- | 59.9 | 28.8 | No | 2017-08-04 | D_s1_d2 | 1.56 | 33.9 | 51.6 | 1134 | 62 | D | 7 | 0.02 | s1 | n | y | d2
TN_2017_652 |  |  | 383132Y | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44.23 | 5 | Vilanova | XLPE+1420FEES+6000SEES | -- | 58.7 | 66.1 | No | 2017-08-04 | C_s1_d2 | 1.38 | 22.8 | 39.1 | 1401 | 42.1 | C | 26.3 | 0.03 | s1 | n | y | d2
|  |  | 383132Y | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44.31 | 5 | CEIS | XLPE+1420FEES+6000SEES | -- | 35 | 24.9 | No | 2017-08-10 | C_s1_d2 | 1.4 | 21.6 | 36 | 1401 | 35.8 | C | 5.7 | 0.01 | s1 | n | y | d2
EFR-17-BB-0028553A |  |  | -- | 1000-SS-1X95MM²-SH-NF F 55-625-255-2017 | -- | -- | Efectis | ID3100FR/SV3300FR+5300SEIT | -- | 58 | 28.14 | No | 2017-07-31 | B2_s1_d0 | 0.85 | 13.5 | 18.9 | 1425 | 37.6 | B2 | 18.3 | 0.04 | s1 | n | n | d0
EFR-17-BB-0028553B |  |  | -- | 1800-S-1X240MM²-SH-NF F 55-625-255 | -- | -- | Efectis | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 56.7 | 29.5 | No | 2017-07-31 | B2_s1_d0 | 0.65 | 8.2 | 9.1 | 900 | 30 | B2 | 4.8 | 0.01 | s1 | n | n | d0
17090001 |  |  | -- | FR-N1 X1G1-U- 5G6MM² | 17.4 | 9 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 45.2 | 25.4 | No | 2017-09-06 | B2_s1_d2 | 0.7 | 9.1 | 18.3 | 1494 | 17 | B2 | 11 | 0.02 | s1 | y | y | d2
17090002 |  | 16903 | -- | TRIFILS HO7Z1 - U - 1.50 MM² DE CHARVIEU | 6 | 75 | Paron | 1602SEES | -- | 49.2 | 24.4 | No | 2017-09-12 | B2_s1_d1 | 1 | 4 | 19 | 525 | 104 | B2 | 10 | 0.03 | s1 | y | n | d1
TN_2017_653 |  |  | 10-H14892 | PRYSMIAN FG16M16 1 KV 1X25 | 14.13 | 11 | Vilanova | TNT+0400FEIT+5300SEIT | CD | 77.4 | 22.8 | No | 2017-08-30 | B2_s1_d1 | 0.77 | 10.7 | 17.2 | 1236 | 27.9 | B2 | 13.5 | 0.02 | s1 | y | n | d1
TN_2017_654 |  | 81963544 |  | AFUMEX CLASS RZ1-K (AS) 1KV 4G10 | 17.97 | 8 | Vilanova | SXLPE+1420FEES+1602SEES | OD | 78.9 | 22.9 | No | 2017-08-30 | B2_s1_d0 | 0.76 | 13.9 | 25.6 | 1464 | 30.8 | B2 | 0 | 0 | s1 | n | n | d0
TN_2017_655 |  |  | 08-D41640 | PRYSMIAN FG16M16 1 KV 1X16 | 12.04 | 13 | Vilanova | SXLPE+CARTA+0400FEIT+5300SEIT | CD | 77 | 23.9 | No | 2017-08-30 | B2_s1_d0 | 0.52 | 9 | 13.9 | 948 | 41.6 | B2 | 15.6 | 0.02 | s1 | n | n | d0
TN_2017_656 |  | 82185593 |  | AFUMEX CLASS RZ1-K (AS) 1KV 1X35 | 14.21 | 11 | Vilanova | SXLPE+1420FEES+1602SEES | OD | 81 | 23.9 | No | 2017-08-31 | C_s1_d2 | 1.47 | 25.3 | 36.3 | 1041 | 54 | C | 8.6 | 0.04 | s1 | n | y | d2
TN_2017_657 |  | 81215521 |  | AFUMEX EASY RZ1-K 0.6/1.0KV 1X6 | 7.19 | 21 | Vilanova | SXLPE+1420FEES+1602SEES | OD | 68 | 21.7 | No | 2017-09-01 | D_s2_d2 | 3.3 | 59.5 | 300.5 | 705 | 746.4 | D | 54.2 | 0.17 | s2 | n | y | d2
TN_2017_658 |  | 82087638 |  | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 11.4 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | OD | 57 | 23.9 | No | 2017-09-01 | D_s2_d0 | 2.12 | 26.4 | 37.2 | 819 | 71.7 | D | 54.9 | 0.1 | s2 | n | n | d0
TN_2017_659 |  |  | 08-D41644 | PRYSMIAN FG16M16 1 KV 1X35 | 14.73 | 10 | Vilanova | CARTA+0400FEIT+5300SEIT | CD | 62.2 | 26 | No | 2017-09-01 | B2_s1_d2 | 0.56 | 6.5 | 8.6 | 1206 | 20.5 | B2 | 6.4 | 0.01 | s1 | n | y | d2
TN_2017_660 |  |  | T7-F83166 | FG16R16 1X6 MM² - 0.6/1 KV | 8.04 | 19 | Vilanova | S-XLPE+2000SPIT | CD | 77.9 | 24.7 | No | 2017-09-04 | C_s2_d2 | 1.45 | 19.4 | 40.4 | 525 | 189.6 | C | 268.2 | 0.94 | s2 | n | y | d2
TN_2017_661 |  |  | 08-D41571 | FG16R16 1X16MM² - 0.6/1 KV | 11.53 | 13 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 73 | 25.9 | No | 2017-09-04 | B2_s2_d0 | 0.71 | 7.8 | 13.8 | 723 | 95.6 | B2 | 89.6 | 0.31 | s2 | n | n | d0
TN_2017_662 |  | 64255 | 366595Y | RVMV-K 1KV 3G50MM2 | 32.99 | 6 | Vilanova | SXLPE+6010+ARMOUR+LANTORTAPELONGITUDINAL+1420FEES+6010SEES | OD | 75.1 | 22.1 | No | 2017-09-05 | B2_s1_d2 | 0.88 | 12 | 17.9 | 1500 | 36 | B2 | 10.4 | 0.02 | s1 | n | y | d2
TN_2017_663 |  | 64256 | 342010A | RVMV-K 1KV 3G10MM2 | 24.19 | 7 | Vilanova | SXLPE+6010+ARMOUR+LANTORTAPELONGITUDINAL+1420FEES+6010SEES | OD | 75 | 22.2 | No | 2017-09-05 | C_s2_d2 | 1 | 24.2 | 32.1 | 1224 | 68.7 | C | 181.4 | 0.27 | s2 | n | y | d2
TN_2017_664 |  |  |  | CABLES RCT ARA-Z1 RZ1-K (AS) 0.6/1KV 3G1.5 | 9.83 | 15 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | OD | 70.6 | 25.2 | No | 2017-09-05 | C_s1_d1 | 1.84 | 18.3 | 29.7 | 663 | 85.4 | C | 42.9 | 0.07 | s1 | y | n | d1
TN_2017_665 |  | 64254 | 372944Z | RVMV-K 1KV 3G2.5 | 16.5 | 9 | Vilanova | SXLPE+6010+ARMOUR+LANTORTAPELONGITUDINAL+1420FEES+6010SEES | OD | 68.2 | 26.8 | No | 2017-09-05 | D_s1_d2 | 1.68 | 30.3 | 47.5 | 1053 | 65.5 | D | 13 | 0.03 | s1 | n | y | d2
TN_2017_666 |  |  |  | ADIF DRAKA 64FO MN TKEST | 15.99 | 9 | Vilanova |  | OD | 63.9 | 28.2 | No | 2017-09-05 | E ou F_s2_d2 | 3.3 | 121 | 236.6 | 1134 | 296.5 | E ou F | 50.6 | 0.08 | s2 | n | y | d2
TN_2017_667 |  |  | 10-F28339 | FS17 1X240 MM2 | 25.57 | 6 | Vilanova | 2800GPIT | CD | 82.6 | 23.7 | No | 2017-09-06 | B2_s2_d0 | 0.82 | 11.1 | 17.2 | 624 | 80.9 | B2 | 269.9 | 0.56 | s2 | n | n | d0
TN_2017_668 |  |  | C25519 | 1602SEES | 4.07 | 90 | Vilanova | 2600IPIT+2800GPITASSKIN | CD | 78.7 | 20.6 | No | 2017-09-13 | D_s2_d0 | 1.24 | 12.1 | 34.1 | 441 | 494.3 | D | 189 | 0.95 | s2 | n | n | d0
TN_2017_669 |  |  | T7-C25568 | FS17 1X2.5 MM2 | 3.54 | 105 | Vilanova | 2600IPIT+2800GPITASSKIN | CD | 65.7 | 23 | No | 2017-09-13 | C_s2_d0 | 1.13 | 5.7 | 23.6 | 435 | 202.3 | C | 190.9 | 0.97 | s2 | n | n | d0
TN_2017_670 |  |  | T7-C83167 | FS17 1X6 MM2 | 4.61 | 60 | Vilanova | 2600IPIT+2800GPITASSKIN | CD | 59.6 | 24.4 | No | 2017-09-13 | C_s2_d0 | 1.15 | 5 | 21 | 426 | 198.4 | C | 175.9 | 0.88 | s2 | n | n | d0
TN_2017_671 |  |  | 345739D | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.23 | 14 | Vilanova | SXLPE+15ABSEES | OD | 50.7 | 26.1 | No | 2017-09-13 | _ _
17090003 |  | 16923 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 | 3.1 | 150 | Paron | SW3800FR | -- | 52.2 | 22.4 | No | 2017-09-14 | B2_s2_d0 | 1.35 | 13 | 25.7 | -- | 44 | B2 | 68 | 0.14 | s2 | n | n | d0
17090004 |  | 16929 | -- | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.4 | 8 | Paron | COPPERTAPE50%+MICATAPE50%+LANTORTAPE25%+1420+1602SEES | -- | 48.2 | 21.9 | No | 2017-09-14 | C_s1_d2 | 1.1 | 16.8 | 48.6 | 1500 | 41 | C | 36 | 0.12 | s1 | y | y | d2
TN_2017_672 |  | 64288 | 389503Y | PRYSMIAN AFUMEX SCH3 1KV 14X0.5 | 19.98 | 8 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 81.4 | 23.3 | No | 2017-09-14 | B2_s1_d0 | 0.75 | 13.7 | 27 | 1326 | 32.1 | B2 | 35.4 | 0.08 | s1 | n | n | d0
TN_2017_673 |  | 64225 | 389468K | PRYSMIAN AFUMEX SCH4 1KV 2X4 2017 | 17.29 | 9 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 80 | 24 | No | 2017-09-14 | B2_s1_d0 | 0.43 | 8.3 | 13 | 1299 | 23 | B2 | 20.4 | 0.03 | s1 | n | n | d0
TN_2017_674 |  | 64230 | 381482E | PRYSMIAN AFUMEX SCH3 1KV 27X0.5 | 23.56 | 7 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 79.5 | 25.1 | No | 2017-09-14 | B2_s1_d2 | 0.76 | 5.6 | 19.8 | 1500 | 16.5 | B2 | 1.2 | 0.03 | s1 | n | y | d2
TN_2017_675 |  | 64226 | 389514K | PRYSMIAN AFUMEX SCH4 1KV 8X0.5 | 17.49 | 9 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 78.7 | 25.4 | No | 2017-09-14 | C_s1_d1 | 0.72 | 17.1 | 29.5 | 1188 | 41.2 | C | 4.1 | 0.02 | s1 | y | n | d1
TN_2017_676 |  |  | 358669H | AL-HEPRZ1(AS) 1X500MM2 26/45KV | 53.71 | 4 | Vilanova | HEPR+6000SEES | OD | 76.4 | 26.1 | No | 2017-09-14 | D_s1_d2 | 2.45 | 62.1 | 104.5 | 1458 | 101 | D | 22.4 | 0.05 | s1 | n | y | d2
TN_2017_677 |  | 64232 | 386509U | PRYSMIAN AFUMEX SCH3 1KV 1X300 | 35.29 | 5 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 72.9 | 19.2 | No | 2017-09-15 | B2_s1_d1 | 0.43 | 8 | 12.4 | 1497 | 21.5 | B2 | 0.2 | 0 | s1 | y | n | d1
TN_2017_678 |  |  | T1-H12617 | PRYSMIAN FG16M16 1 KV 1X70 | 17.76 | 8 | Vilanova | TNT+0400FEIT+5300SEIT | CD | 69.3 | 19 | No | 2017-09-15 | B2_s1_d1 | 0.47 | 7.8 | 12.8 | 1476 | 33.2 | B2 | 0 | 0 | s1 | y | n | d1
TN_2017_679 |  |  | T1-H16025 | PRYSMIAN FG16M16 1 KV 1X120 | 22 | 7 | Vilanova | TNT+0400FEIT+5300SEIT | CD | 67.7 | 19.6 | No | 2017-09-15 | B2_s1_d1 | 0.47 | 5.3 | 7.9 | 1500 | 23.9 | B2 | 6.7 | 0.01 | s1 | y | n | d1
TN_2017_680 |  |  | T1-H12660 | FG16R16 1X25MM² - 0.6/1 KV | 12.98 | 12 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 70.7 | 19.3 | No | 2017-09-15 | B2_s2_d0 | 0.76 | 8.8 | 15.6 | 876 | 74.1 | B2 | 107.7 | 0.24 | s2 | n | n | d0
TN_2017_681 |  |  | 7-F83206 | FG16R16 1X1.5MM² - 0.6/1 KV | 8.13 | 19 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 54.5 | 16.2 | No | 2017-09-17 | D_s2_d0 | 0.7 | 13.3 | 23.5 | 345 | 542.6 | D | 115.4 | 0.52 | s2 | n | n | d0
TN_2017_682 |  |  | F68166 | FG16R16 1X2.5MM² - 0.6/1 KV | 8.51 | 17 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 53.1 | 17 | No | 2017-09-17 | B2_s2_d0 | 0.82 | 4.6 | 12.8 | 543 | 62.2 | B2 | 120.9 | 0.5 | s2 | n | n | d0
TN_2017_683 |  | 64230 | 381482E | PRYSMIAN AFUMEX SCH3 1KV 27X0.5 | 23.56 | 7 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 78.9 | 18.1 | No | 2017-09-19 | C_s1_d0 | 0.9 | 12.5 | 38 | 1497 | 31.8 | C | 13.1 | 0.07 | s1 | n | n | d0
TN_2017_684 |  |  | T1-H15977 | PRYSMIAN FG16M16 1 KV 1X95 | 19.56 | 8 | Vilanova | TNT+0400FEIT+5300SEIT | CD | 74.4 | 17.8 | No | 2017-09-19 | B2_s1_d0 | 0.4 | 2.7 | 4.9 | 1497 | 12 | B2 | 0 | 0 | s1 | n | n | d0
TN_2017_685 |  |  | T1-H16017 | FG16R16 1X50MM² - 0.6/1 KV | 16.52 | 9 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 64.7 | 20.1 | No | 2017-09-19 | B2_s2_d1 | 0.81 | 13.7 | 21.1 | 1023 | 54.6 | B2 | 144.6 | 0.28 | s2 | y | n | d1
TN_2017_686 |  |  | F68164 | FG16R16 1X4MM² - 0.6/1 KV | 9.08 | 17 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 58.2 | 21.5 | No | 2017-09-19 | B2_s2_d0 | 0.8 | 7.9 | 14.1 | 609 | 100.1 | B2 | 112 | 0.45 | s2 | n | n | d0
TN_2017_687 |  |  | 07-F85829 | FG16R16 1X6 MM² - 0.6/1 KV | 7.37 | 21 | Vilanova | SXLPE+2000DPITNOFILLER | CD | 47.7 | 23.2 | No | 2017-09-19 | D_s3_d2 | 3.1 | 27 | 37.4 | 678 | 152.1 | D | 647.2 | 0.84 | s3 | n | y | d2
TN_2017_688 |  |  | 360615Y | PRYSMIAN SAP 2017 81363317 AFUMEX VARINET K RZ1KZ1-K 1KV 3X16/16MM2 | 21.22 | 7 | Vilanova | PENDING | OD | 66.7 | 18.2 | No | 2017-09-20 | C_s1_d2 | 1.29 | 25.1 | 37.7 | 1281 | 62 | C | 17.1 | 0.05 | s1 | n | y | d2
TN_2017_689 |  |  | 388139R | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.25 | 14 | Vilanova | SXLPE+1602SEES | OD | 66.9 | 18.3 | No | 2017-09-20 | E ou F_s2_d2 | 3.3 | 73.4 | 174.8 | 1371 | 163.2 | E ou F | 76.3 | 0.33 | s2 | n | y | d2
TN_2017_690 |  |  | 219583C | PRYSMIAN SAP 2015 81367096 AFUMEX VARINET K RZ1KZ1-K 1KV 3X50/25MM2 | 31.15 | 6 | Vilanova | PENDING | OD | 58.5 | 21.2 | No | 2017-09-20 | C_s1_d2 | 0.85 | 16.1 | 17.7 | 609 | 66.4 | C | 16.6 | 0.02 | s1 | n | y | d2
TN_2017_691 |  |  | 10-H12629 | PRYSMIAN FG16M16 1 KV 1X50 | 15.95 | 9 | Vilanova | TNT+0400FEIT+5300SEIT | OD | 57.5 | 23.1 | No | 2017-09-20 | B2_s1_d2 | 0.36 | 7.2 | 10.6 | 1236 | 38.1 | B2 | 1 | 0.01 | s1 | n | y | d2
TN_2017_692 |  | 63936 | 383024F | PRYSMIAN VOLTALENE RHVMA-TR (FCA) 2RH 1X300+H16 12/20KV 2017 | 49.97 | 4 | Vilanova | PENDING | -- | 54.7 | 24 | No | 2017-09-20 | B2_s3_d1 | 1.14 | 13.4 | 21 | 1497 | 67.7 | B2 | 841.6 | 0.99 | s3 | y | n | d1
1709005 |  | 16942 | drum | 1800-S-1*16-SH-NF F 55-625-255 | 15.2 | 10 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 59.9 | 22.9 | No | 2017-09-28 | B2_s1_d2 | 0.7 | 9.3 | 14.5 | 1209 | 30 | B2 | 22 | 0.04 | s1 | y | y | d2
17090006 |  | 16942 | drum | K25 750V 1X1.5 -SH-NF F 55-625-255 ( IRRADIÉ) | 2.86 | 165 | Paron | SW3800FR | -- | 63.5 | 22.4 | No | 2017-09-28 | B2_s1_d0 | 0.9 | 9.2 | 22.9 | 735 | 55 | B2 | 48 | 0.07 | s1 | n | n | d0
17090007 |  | 16942 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 | 3.1 | 150 | Paron | SW3800FR | -- | 58.6 | 25.1 | No | 2017-09-28 | B2_s2_d0 | 1.25 | 11.1 | 29.6 | 765 | 64 | B2 | 54 | 0.13 | s2 | n | n | d0
TN_2017_693 |  |  | 10-H15948 | FG16R16 1X35MM² - 0.6/1 KV | 14.25 | 11 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 68.7 | 19.8 | No | 2017-09-21 | D_s2_d2 | 0.76 | 18.6 | 25.9 | 894 | 498.2 | D | 121.1 | 0.27 | s2 | n | y | d2
TN_2017_694 |  |  | 10-H15728 | FG16R16 1X70MM² - 0.6/1 KV | 18.17 | 8 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 66.5 | 20.4 | No | 2017-09-21 | B2_s2_d0 | 0.75 | 12.4 | 16.1 | 1254 | 67.1 | B2 | 85.5 | 0.21 | s2 | n | n | d0
TN_2017_695 |  |  | 07-F83179 | FG16OR16 3G1.5 MM² - 0.6/1 KV | 9.87 | 15 | Vilanova | TALCO+2000SPIT | CD | 62.8 | 22.2 | No | 2017-09-21 | D_s3_d2 | 2.34 | 21.5 | 42.1 | 597 | 144.3 | D | 586.5 | 1.36 | s3 | n | y | d2
TN_2017_696 |  |  | 09-D47324 | PRYSMIAN FG16M16 1 KV 1X10 | 10.42 | 15 | Vilanova | CARTA+0400FEIT+5300SEIT | CD | 65.4 | 23.9 | No | 2017-09-21 | B2_s1_d1 | 0.76 | 12 | 20.3 | 888 | 61.4 | B2 | 14.8 | 0.03 | s1 | y | n | d1
TN_2017_697 |  |  | 388139R | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.25 | 14 | Vilanova | SXLPE+1602SEES | CD | 66.4 | 24.6 | No | 2017-09-21 | E ou F_s2_d2 | 3.3 | 89.4 | 193.7 | 1281 | 197.4 | E ou F | 111.6 | 0.24 | s2 | n | y | d2
TN_2017_698 |  |  | PEDANA | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X16 | 7.52 | 19 | Vilanova | 1602SEES | CD | 74 | 21.6 | No | 2017-09-27 | B2_s1_d0 | 0.37 | 3.6 | 9.3 | 510 | 44.5 | B2 | 3.5 | 0.01 | s1 | n | n | d0
TN_2017_699 |  |  | 336592L | AL-HEPRZ1(AS) 1X300MM2 36/66KV | 50.58 | 4 | Vilanova | HEPR+6000SEES | OD | 70 | 22.6 | No | 2017-09-27 | D_s1_d2 | 1.82 | 41.5 | 63.4 | 1416 | 74.9 | D | 10.4 | 0.02 | s1 | n | y | d2
TN_2017_700 |  |  | 10G84100 | RG7OM1NM1 2X25 | 30.43 | 6 | Vilanova | ID7600+0400FEIT+5300SEIT+STEELTAPE+5300SEIT | CD | 72 | 19.4 | No | 2017-09-28 | C_s1_d2 | 0.78 | 15.4 | 26.6 | 1359 | 31.7 | C | 2.5 | 0.01 | s1 | n | y | d2
TN_2017_701 |  |  | 10G84102 | RG7OM1NM1 3X10 | 26.77 | 6 | Vilanova | ID7600+0400FEIT+5300SEIT+STEELTAPE+5300SEIT | CD | 72 | 19.8 | No | 2017-09-28 | D_s1_d2 | 1.05 | 23.4 | 66.7 | 1500 | 55.6 | D | 30.7 | 0.11 | s1 | n | y | d2
TN_2017_702 |  |  | ROLLO | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X25 | 8.8 | 17 | Vilanova | 1602SEES | OD | 68 | 22.2 | No | 2017-09-28 | B2_s1_d0 | 0.72 | 7.2 | 13.6 | 633 | 55 | B2 | 0.1 | 0 | s1 | n | n | d0
TN_2017_703 |  |  | 10F62195 | FG10OM1 3X1.5 | 12.8 | 12 | Vilanova | ID2900+0400FEIT+5300SEIT | CD | 78.6 | 19.5 | No | 2017-09-29 | B2_s1_d2 | 0.94 | 11 | 20.6 | 855 | 37.1 | B2 | 25.4 | 0.06 | s1 | n | y | d2
TN_2017_704 |  |  |  | CABLES RCT ARA-Z1 RZ1-K (AS) 0.6/1KV 3G2.5 | 10.73 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | CD | 67.5 | 23.6 | No | 2017-09-29 | C_s1_d1 | 1.24 | 16.2 | 32.5 | 768 | 69.5 | C | 23.1 | 0.05 | s1 | y | n | d1
TN_2017_705 |  |  |  | PRYSMIAN 05 1FO G-657A2 INT ORANGE ESPANA | 1.89 | 405 | Vilanova | PENDING | OD | 64.2 | 24.8 | No | 2017-09-29 | E ou F_s1_d0 | 3.3 | 80.7 | 185.2 | 891 | 313.6 | E ou F | 46.7 | 0.12 | s1 | n | n | d0
TN_2017_706 |  | OF1107266 |  | ASCABLE-RECAEL RZ1-K (AS) 1KV 3G2.5 | 11.64 | 13 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | OD | 87.5 | 19.9 | No | 2017-10-02 | E ou F_s1_d2 | 3.3 | 80.7 | 185.2 | 891 | 313.6 | E ou F | 46.7 | 0.12 | s1 | n | y | d2
TN_2017_707 |  |  |  | REVI ECOCLASS RZ1-K (AS) 1KV 3G2.5 | 10.6 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | OD | 83.4 | 21.3 | No | 2017-10-02 | D_s2_d2 | 3.3 | 45 | 103 | 1500 | 85.8 | D | 81.2 | 0.21 | s2 | n | y | d2
TN_2017_708 |  |  |  | EXZHELLENT RZ1-K (AS) 1KV 3G2.5 | 11.31 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | OD | 79.1 | 22.2 | No | 2017-10-02 | B2_s1_d0 | 0.86 | 12.8 | 18.7 | 903 | 34.4 | B2 | 5.7 | 0.04 | s1 | n | n | d0
TN_2017_710 |  |  |  | REVI ECOCLASS RZ1-K (AS) 0.6/1KV 3G1.5 | 9.76 | 15 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | CD | 67.6 | 25.1 | No | 2017-10-02 | B2_s1_d0 | 0.77 | 9.8 | 12.9 | 609 | 45.2 | B2 | 31.7 | 0.14 | s1 | n | n | d0
TN_2017_711 |  |  |  | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.45 | 15 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | OD | 84.4 | 21 | No | 2017-10-04 | C_s1_d0 | 1.65 | 20.3 | 27.3 | 876 | 51.3 | C | 29.2 | 0.05 | s1 | n | n | d0
TN_2017_712 |  |  |  | EXZHELLENT RZ1-K (AS) 1KV 5G35 | 27.64 | 6 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | OD | 85.3 | 21.2 | No | 2017-10-05 | B2_s1_d2 | 0.7 | 8.4 | 23.3 | 1494 | 24.2 | B2 | 8.2 | 0.03 | s1 | n | y | d2
TN_2017_713 |  |  |  | CABLES RCT ARA-Z1 RZ1-K (AS) 0.6/1KV 3G2.5 | 10.73 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | OD | 83.3 | 21.9 | No | 2017-10-05 | C_s1_d0 | 1.64 | 20.3 | 25.4 | 996 | 57.6 | C | 25 | 0.05 | s1 | n | n | d0
TN_2017_714 |  | OF1107266 |  | ASCABLE-RECAEL RZ1-K (AS) 1KV 3G2.5 | 11.64 | 13 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | OD | 77.3 | 24 | No | 2017-10-05 | D_s2_d0 | 3.3 | 45.7 | 97.1 | 1497 | 81.1 | D | 59.2 | 0.17 | s2 | n | n | d0
TN_2017_715 |  |  |  | REVI ECOCLASS RZ1-K (AS) 1KV 3G2.5 | 10.6 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | OD | 67.1 | 26.2 | No | 2017-10-05 | B2_s1_d2 | 1.42 | 11.8 | 18 | 651 | 51.5 | B2 | 27.6 | 0.04 | s1 | n | y | d2
17100002 |  | 16967 | -- | K22 2X1.6-SH-SH-NF F 55-622-PRYSMIAN 255 | 13.6 | 11 | Paron | SW3800FR+RUBANSCAPA+5300SEIT | -- | 50.9 | 24.8 | No | 2017-10-10 | B2_s1_d2 | 0.3 | 5 | 6.3 | 933 | 28 | B2 | 7 | 0.01 | s1 | y | y | d2
TN_2017_716 |  |  | 395277Z | AFUMEX CLASS RZ1-K (AS) 1KV 5G16 | 22.48 | 7 | Vilanova | SXLPE+1420FEES+1602SEES | OD | 80.2 | 19 | No | 2017-10-10 | B2_s1_d0 | 0.56 | 7.9 | 11 | 1464 | 34.9 | B2 | 11.5 | 0.02 | s1 | n | n | d0
TN_2017_717 |  | OP65450 | 398682A | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.15 | 14 | Vilanova | TALCUM+1602SEES | OD | 78.1 | 20.2 | No | 2017-10-10 | E ou F_s2_d2 | 3.3 | 96.9 | 204.8 | 1278 | 210.4 | E ou F | 88.2 | 0.24 | s2 | n | y | d2
TN_2017_718 |  | OP65450 | 395840L | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.31 | 14 | Vilanova | TALCUM+1602SEES | OD | 70 | 23.8 | No | 2017-10-10 | E ou F_s2_d2 | 3.3 | 104.7 | 222.5 | 1110 | 274.8 | E ou F | 120.6 | 0.39 | s2 | n | y | d2
TN_2017_719 |  | OP64373 | 395152N | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 10X2.5 | 20.99 | 7 | Vilanova | PENDING | OD | 63.3 | 25 | No | 2017-10-10 | B2_s1_d1 | 0.52 | 5.1 | 9.3 | 1464 | 16.9 | B2 | 2.9 | 0.01 | s1 | y | n | d1
17100003 |  | 16964 | -- | PRYSMIAN 2017 60 FO +MÉTRIQUE LSZH (CÂBLE Nº7 MLT 72F (6X12)) | 8 | 19 | Paron | 1.35PBT+UNIGEL400N+0400FEIT+MEGOLONS-540 | -- | 51.2 | 23.9 | No | 2017-10-11 | B2_s2_d1 | 1.25 | 9.8 | 28 | 621 | 99 | B2 | 57 | 0.15 | s2 | y | n | d1
17100004 |  | 16964 | -- | PRYSMIAN 2017 60 FO + METRIQUE NS (CABLE Nº3 FLEX TUBE 6OFO (5X12)) | 7.6 | 19 | Paron | 1.2SANTOPRENE+H-55+CONGUARDS6650 | -- | 52.4 | 23.6 | No | 2017-10-11 | C_s1_d0 | 1.9 | 11.7 | 26.9 | 672 | 96 | C | 35 | 0.07 | s1 | n | n | d0
17100005 |  | 16964 | -- | PRYSMIAN 2017 60 FO + METRIQUE HY (CABLE Nº2 FLEX TUBE 60F (5X12)) | 8 | 19 | Paron | 1.3HYTREL+UNIGEL400N+CONGUARDS6650 | -- | 50 | 23.1 | No | 2017-10-13 | D_s2_d0 | 3.3 | 41.5 | 72.6 | 1098 | 141 | D | 105 | 0.21 | s2 | n | n | d0
17100006 |  | 16964 | -- | PRYSMIAN 2017 60 FO + METRIQUE 4K FLEX (CABLE Nº1 FLEX TUBE 60F (5X12)) | 8 | 19 | Paron | 1.3SANTOPRENEW/CACO3+NOJELLY+CONGUARDS6650 | -- | 50.9 | 24.2 | No | 2017-10-13 | B2_s1_d0 | 1.3 | 7.2 | 22.1 | 645 | 112 | B2 | 25 | 0.07 | s1 | n | n | d0
1710007 |  | 16980 | -- | DRAKA 128FO FXT VT ( MODEL Nº1) | 13.4 | 12 | Paron | CYGSALHC-1800/R | -- | 48.3 | 23.4 | No | 2017-10-17 | D_s2_d2 | 3.3 | 59.6 | 113 | 1179 | 159 | D | 145 | 0.35 | s2 | y | y | d2
1710008 |  | 16980 | -- | DRAKA 128FO FXT VT ( MODEL Nº2) | 12.4 | 13 | Paron | MEGOLONS-540 | -- | 53.8 | 22.8 | No | 2017-10-17 | D_s2_d2 | 3.3 | 68.4 | 177.1 | 1026 | 252 | D | 199 | 0.58 | s2 | y | y | d2
TN_2017_721 |  |  | D38039 | SAP CODE 20213070 FS17 1X10 | 6.45 | 21 | Vilanova | 2600IPIT+2800GPITASSKIN | CD | 71.5 | 20.9 | No | 2017-10-17 | B2_s2_d0 | 0.42 | 3.6 | 8 | 393 | 55.7 | B2 | 46.1 | 0.39 | s2 | n | n | d0
TN_2017_722 |  |  |  | REVI ECOCLASS RZ1-K (AS) 0.6/1KV 3G1.5 | 9.83 | 15 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | OD | 68 | 25.7 | No | 2017-10-17 | B2_s1_d0 | 0.83 | 13.3 | 25.4 | 771 | 64.4 | B2 | 36.6 | 0.1 | s1 | n | n | d0
TN_2017_723 |  |  | T8F74903 | PRYSMIAN FG16M16 1 KV 1X10 | 10.47 | 15 | Vilanova | PENDINGTOCONFIRM | CD | 65 | 24.3 | No | 2017-10-17 | B2_s1_d0 | 0.34 | 5.9 | 8 | 933 | 36.5 | B2 | 1.7 | 0 | s1 | n | n | d0
TN_2017_724 |  |  | T8F74891 | FG16OM16 3G1.5 MM² - 0.6/1 KV | 11.13 | 14 | Vilanova | CARTA+04AMFEIT+5300SEIT | CD | 72.5 | 21 | No | 2017-10-18 | B2_s1_d2 | 0.43 | 7.8 | 12.6 | 867 | 39.7 | B2 | 0 | 0 | s1 | n | y | d2
TN_2017_725 |  |  |  | MIGUELEZ AFIREFENIX SZ1-K 1KV PH90 (AS+) 3G2.5 | 10.15 | 15 | Vilanova | SILICONERUBBER+LSOH | OD | 72 | 21.3 | No | 2017-10-18 | B2_s1_d0 | 0.39 | 5.3 | 13 | 591 | 47.8 | B2 | 8 | 0.03 | s1 | n | n | d0
TN_2017_726 |  |  |  | MIGUELEZ AFIREFENIX SZ1-K 1KV PH90 (AS+) 3G1.5 | 9.36 | 17 | Vilanova | SILICONERUBBER+LSOH | OD | 71.1 | 22.2 | No | 2017-10-18 | B2_s1_d1 | 0.51 | 8.3 | 14.2 | 675 | 45.7 | B2 | 2.8 | 0.01 | s1 | y | n | d1
TN_2017_727 |  | OP65177 SAP 20228084 | 398690J | BLINDEX Z1C4Z1-K 1KV (AS) 4G10MM2 | 17.37 | 9 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 67.7 | 24.5 | No | 2017-10-18 | B2_s1_d2 | 0.41 | 6.9 | 8.5 | 1194 | 26.3 | B2 | 0 | 0 | s1 | n | y | d2
TN_2017_728 |  | OP65178 SAP 20228085 | 395839K | BLINDEX Z1C4Z1-K 1KV (AS) 12G1.5MM2 | 16.13 | 9 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 66.7 | 24.5 | No | 2017-10-18 | B2_s1_d0 | 0.76 | 11.3 | 13.4 | 990 | 33.3 | B2 | 8.4 | 0.01 | s1 | n | n | d0
1710009 |  | 16980 | -- | DRAKA 128FO FXT VT ( MODEL Nº3) | 13.4 | 12 | Paron | RAVAGO6 | -- | 52.1 | 23 | No | 2017-10-19 | D_s2_d2 | 3.3 | 61.4 | 112.9 | 1164 | 181 | D | 204 | 0.5 | s2 | y | y | d2
1710010 |  | 16980 | -- | DRAKA 128FO FXT VT ( MODEL Nº4) | 13.4 | 12 | Paron | RAVAGO30 | -- | 53.1 | 22.9 | No | 2017-10-19 | D_s2_d2 | 3.3 | 69.9 | 173.4 | 1035 | 250 | D | 191 | 0.59 | s2 | y | y | d2
TN_2017_729 |  | OP65175 SAP 20228082 | 397924B | BLINDEX Z1C4Z1-K 500V (AS) 12G1MM2 | 13.18 | 12 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 80.9 | 18.6 | No | 2017-10-19 | C_s1_d2 | 0.62 | 17.7 | 24.1 | 891 | 59.7 | C | 0.9 | 0.01 | s1 | n | y | d2
TN_2017_730 |  | OP65176 SAP 20228083 | 397927E | BLINDEX Z1C4Z1-K 500V (AS) 16G1MM2 | 14.79 | 10 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 80.2 | 19 | No | 2017-10-19 | B2_s1_d0 | 0.52 | 7 | 10 | 921 | 30.7 | B2 | 3.6 | 0.01 | s1 | n | n | d0
TN_2017_731 |  | OP65174 SAP 20228081 | 398674S | BLINDEX Z1C4Z1-K 500V (AS) 2X1MM2 | 7.36 | 21 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 78.7 | 20 | No | 2017-10-19 | C_s1_d0 | 1.26 | 12.5 | 33.9 | 657 | 108 | C | 26.8 | 0.09 | s1 | n | n | d0
TN_2017_732 |  | OP64821 SAP 20226001 | 399064R | RZ1FA3Z1-K 3KV 1X300 | 36.96 | 5 | Vilanova | XLPE+1602SEES+TAPEAL/PE+TAPELANTOR+SHEATH1602SEES | OD | 59 | 16.6 | No | 2017-10-23 | B2_s1_d0 | 0.4 | 8 | 13.7 | 1500 | 27.2 | B2 | 5.1 | 0.01 | s1 | n | n | d0
TN_2017_733 |  | OP65204 SAP 22226647 | 398672P | AFUMEX CLASS 1KV Z1Z1-K (AS) 16X2.5MM2 | 20.37 | 8 | Vilanova | INS:=1602SEES+TALCUM+SHEATH1602SEES | OD | 60.8 | 16.7 | No | 2017-10-23 | B2_s1_d2 | 0.44 | 8.7 | 13.7 | 663 | 37.6 | B2 | 1 | 0 | s1 | n | y | d2
TN_2017_734 |  | OP65205 SAP 20229629 | 395169G | AFUMEX CLASS 1KV Z1Z1-K (AS) 19X1.5MM2 | 18.91 | 8 | Vilanova | INS:=1602SEES+TALCUM+SHEATH1602SEES | OD | 57.2 | 18.2 | No | 2017-10-23 | B2_s1_d1 | 0.74 | 9.2 | 12.8 | 1461 | 25 | B2 | 4.2 | 0.01 | s1 | y | n | d1
TN_2017_735 |  | OP65207 SAP 20226649 | 395149K | AFUMEX CLASS 1KV Z1Z1-K (AS) 24X1.5MM2 | 21.41 | 7 | Vilanova | INS:=1602SEES+TALCUM+SHEATH1602SEES | OD | 54.3 | 21.8 | No | 2017-10-23 | C_s1_d2 | 0.76 | 16 | 23.7 | 753 | 52.3 | C | 14.6 | 0.02 | s1 | n | y | d2
TN_2017_736 |  | OP65202 SAP 20226650 | 398691K | AFUMEX CLASS 1KV Z1Z1-K (AS) 14X1.5MM2 | 16.66 | 9 | Vilanova | INS:=1602SEES+TALCUM+SHEATH1602SEES | OD | 48.1 | 22.6 | No | 2017-10-23 | B2_s1_d2 | 0.69 | 14.8 | 19.6 | 1257 | 41.6 | B2 | 8.3 | 0.02 | s1 | n | y | d2
TN_2017_737 |  | OP65206 SAP 20226648 | 398667J | AFUMEX CLASS 1KV Z1Z1-K (AS) 19X2.5MM2 | 20.94 | 7 | Vilanova | INS:=1602SEES+TALCUM+SHEATH1602SEES | OD | 51.7 | 18.02 | No | 2017-10-24 | B2_s1_d2 | 0.6 | 7.5 | 13 | 1500 | 25.3 | B2 | 0 | 0 | s1 | n | y | d2
TN_2017_738 |  | OP65203 SAP 20229628 | 395177R | AFUMEX CLASS 1KV Z1Z1-K (AS) 16X1.5MM2 | 18.08 | 8 | Vilanova | INS:=1602SEES+TALCUM+SHEATH1602SEES | OD | 46.3 | 21.5 | No | 2017-10-24 | B2_s1_d0 | 0.77 | 1 | 13.1 | 1344 | 27.9 | B2 | 5.2 | 0.01 | s1 | n | n | d0
TN_2017_739 |  | OP65208 SAP 20229627 | 375173L | AFUMEX CLASS 1KV Z1Z1-K (AS) 24X2.5MM2 | 25.6 | 6 | Vilanova | INS:=1602SEES+TALCUM+SHEATH1602SEES | OD | 45.3 | 22.1 | No | 2017-10-24 | B2_s1_d2 | 0.75 | 14 | 21 | 780 | 43.8 | B2 | 15.7 | 0.02 | s1 | n | y | d2
17100011 |  | 16996 | -- | K22 2X1.6-SH-NF F 55-622-PRYSMIAN 255 | 14 | 11 | Paron | 5300SEIT | -- | 54.5 | 23.9 | No | 2017-10-25 | B2_s1_d2 | 0.7 | 9.5 | 14.9 | 1119 | 34 | B2 | 20 | 0.04 | s1 | y | y | d2
17100012 |  | 16996 | -- | K22 2X1.6-SH-NF F 55-622-PRYSMIAN 255 | 14 | 11 | Paron | 5300SEIT | -- | 57.7 | 23.5 | No | 2017-10-25 | B2_s1_d2 | 0.7 | 6.1 | 14.9 | 1146 | 43 | B2 | 20 | 0.04 | s1 | y | y | d2
17100013 |  | 16948 | -- | PRYSMIAN 255/2017-1*2500 AL-320 000V ELECTRIC CABLE -9954 | 124 | 2 | Paron | 60ACSEES+SKINSCI | -- | 54.1 | 23.2 | No | 2017-10-27 | B2_s1_d0 | 0.8 | 5.1 | 7.6 | 765 | 18 | B2 | 6 | 0.01 | s1 | n | n | d0
17100014 |  | 16996 | -- | K25 5G1.50-SH-NF F 55-625-255 | 12.4 | 13 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 36.5 | 20.9 | No | 2017-10-30 | B2_s1_d2 | 0.9 | 9.7 | 27.1 | 918 | 44 | B2 | 44 | 0.09 | s1 | y | y | d2
17100015 |  | 16996 | -- | 1000-3G10MM²-SH-NF F 55-625-255 | 17.6 | 8 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 41.9 | 20.9 | No | 2017-10-30 | B2_s1_d2 | 0.6 | 6.4 | 10.1 | 1302 | 15 | B2 | 14 | 0.03 | s1 | y | y | d2
TN_2017_740 |  | OP65151 SAP 20229393 | 382440W | RHOZ1-K (AS) 500V 4X2X1MM2 | 16.21 | 9 | Vilanova | SXLPE+LANTORTAPE+1602SEES | OD | 79.7 | 18.4 | No | 2017-10-26 | B2_s1_d2 | 0.9 | 13.4 | 20.6 | 1131 | 28.3 | B2 | 34.7 | 0.07 | s1 | n | y | d2
TN_2017_741 |  | OP64616 SAP 20226336 | 395402K | AL AFUMEX RZ1F3Z1 3KV 3X25 | 32.05 | 6 | Vilanova | SXLPE+1602SEES | OD | 80 | 19.1 | No | 2017-10-26 | D_s1_d2 | 1.68 | 33.1 | 40.8 | 1500 | 83.5 | D | 21.7 | 0.05 | s1 | n | y | d2
TN_2017_742 |  | OP65150 SAP 20229392 | 397886K | RHOZ1-K (AS) 500V 4X2X1MM2 | 16.25 | 9 | Vilanova | SXLPE+LANTORTAPE+1602SEES | OD | 78.9 | 20.7 | No | 2017-10-26 | C_s1_d2 | 0.74 | 19.8 | 33.2 | 888 | 57.4 | C | 35.7 | 0.09 | s1 | n | y | d2
TN_2017_743 |  |  | 402215R | AFUMEX EASY RZ1-K 0.6/1.0KV 5G1.5 | 11.17 | 14 | Vilanova | SXLPE+1602SEES | OD | 75 | 22.2 | No | 2017-10-26 | E ou F_s2_d2 | 3.3 | 95.1 | 224.8 | 1203 | 248.9 | E ou F | 145.8 | 0.46 | s2 | n | y | d2
TN_2017_744 |  |  | 397881E | AFUMEX CLASS 1KV Z1Z1-K (AS) 12X1.5MM2 | 16.51 | 9 | Vilanova | SXLPE+1602SEES | OD | 62.9 | 20.4 | No | 2017-10-27 | C_s1_d2 | 0.8 | 15.2 | 21.4 | 930 | 54.6 | C | 11.4 | 0.03 | s1 | n | y | d2
TN_2017_746 |  |  | 392750C | AFUMEX CLASS RZ1-K (AS) 1KV 4G1.5 | 9.51 | 15 | Vilanova | PENDING | OD | 60.5 | 23 | No | 2017-10-27 | D_s2_d2 | 3.3 | 59.4 | 182 | 1071 | 236 | D | 101.6 | 0.22 | s2 | n | y | d2
TN_2017_747 |  |  | 390780L | AFUMEX CLASS RZ1-K (AS) 1KV 3G6 | 13.58 | 11 | Vilanova | SXLPE+1602SEES | OD | 61.2 | 16.3 | No | 2017-10-30 | C_s1_d0 | 0.89 | 17.8 | 30.7 | 1089 | 39.4 | C | 21.2 | 0.03 | s1 | n | n | d0
TN_2017_748 |  | OP 64618 SAP 20226337 | 392189T | AL AFUMEX RZ1F3Z1 3KV 2X150 | 48.16 | 4 | Vilanova | SXLPE+1602SEES | OD | 63.7 | 16.4 | No | 2017-10-30 | C_s1_d2 | 1.51 | 27.6 | 37.2 | 993 | 88.3 | C | 25.7 | 0.1 | s1 | n | y | d2
TN_2017_749 |  |  | 393260G | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 5G1.5 | 16.4 | 9 | Vilanova | SXLPE+1602SEES | OD | 58.7 | 19.6 | No | 2017-10-30 | B2_s1_d2 | 0.77 | 13.4 | 21.8 | 1062 | 28.9 | B2 | 11.8 | 0.03 | s1 | n | y | d2
TN_2017_750 |  |  | MATASSA | FG16OM16 3G1.5 MM² - 0.6/1 KV | 11.21 | 14 | Vilanova | TNT+04AMFEIT+5300SEIT | CD | 38.5 | 25.5 | No | 2017-10-30 | B2_s1_d0 | 0.52 | 7.2 | 16.1 | 801 | 34.2 | B2 | 4.1 | 0.02 | s1 | n | n | d0
TN_2017_751 |  |  | MATASSA | FG16OR16 3G1.5 MM² - 0.6/1 KV | 9.21 | 17 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 41.1 | 24.2 | No | 2017-10-30 | C_s2_d0 | 1.8 | 15 | 33.3 | 801 | 112.1 | C | 322.4 | 0.78 | s2 | n | n | d0
17110001 |  | 17019 | -- | FR-N1 X1G1-U- 3G1.5 MM² | 10.4 | 15 | Paron | SXLPE+0400FEIT+S663 | -- | 32 | 19.8 | No | 2017-11-08 | C_s2_d0 | 1.3 | 19 | 34.5 | 891 | 63 | C | 52 | 0.1 | s2 | n | n | d0
17110002 |  | 16980 | -- | DRAKA 14 2016 IGN 96 FO ORANGE ESPANA | 13.1 | 12 | Paron | CYGSALHC-1800/R | -- | 34 | 20.1 | No | 2017-11-08 | E ou F_s2_d2 | 3.3 | 86 | 207.4 | 1029 | 287 | E ou F | 293 | 0.84 | s2 | y | y | d2
17110003 |  | 16980 | -- | DRAKA 128FO FXT VT ( MODEL Nº1) | 13.1 | 12 | Paron | CYGSALHC-1800/R | -- | 32.4 | 21.5 | No | 2017-11-08 | D_s2_d2 | 3.3 | 62.2 | 127.9 | 1125 | 178 | D | 168 | 0.39 | s2 | y | y | d2
TN_2017_752 |  |  | 395457V | AFUMEX CLASS RZ1-K (AS) 1KV 4G240 | 62.5 | 3 | Vilanova | SXLPE+1420FEES+1602SEES | OD | 68 | 20.2 | No | 2017-11-03 | B2_s1_d0 | 0.6 | 4.4 | 6.5 | 648 | 21.1 | B2 | 15 | 0.03 | s1 | n | n | d0
TN_2017_753 |  |  | MATASSA | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.88 | 11 | Vilanova | PAPER+04AMFEIT+5300SEIT | CD | 66.4 | 21.9 | No | 2017-11-03 | B2_s1_d0 | 0.86 | 9.8 | 15.5 | 1500 | 31 | B2 | 29.5 | 0.04 | s1 | n | n | d0
TN_2017_754 |  | OP65200 SAP 20226646 | 397902C | AFUMEX CLASS 1KV Z1Z1-K (AS) 7X2.5MM2 | 14.19 | 11 | Vilanova | WITHOUTPAPER+TALCUM+1602 | OD | 63.3 | 23.2 | No | 2017-11-03 | B2_s1_d2 | 0.82 | 11.8 | 19.1 | 1035 | 40.1 | B2 | 10 | 0.03 | s1 | n | y | d2
TN_2017_755 |  |  |  | BALDASSARI FG16OM16 1KV 3G1.5 | 10.22 | 15 | Vilanova | COMPETITORSAMPLE | CD | 49.5 | 13.3 | No | 2017-11-06 | C_s2_d2 | 1.78 | 28.8 | 38.4 | 1287 | 106.2 | C | 152.4 | 0.3 | s2 | n | y | d2
TN_2017_756 |  |  |  | FG16OR16 3G1.5 MM² - 0.6/1 KV ( BALDASSARI) | 10.17 | 15 | Vilanova | COMPETITORSAMPLE | CD | 46.8 | 14 | No | 2017-11-06 | C_s3_d2 | 1.65 | 17.9 | 33.2 | 717 | 115.5 | C | 544.9 | 1.12 | s3 | n | y | d2
TN_2017_757 |  |  |  | FG16OR16 5G1.5 MM² - 0.6/1 KV ( ICEL CAVI) | 12.84 | 12 | Vilanova | COMPETITORSAMPLE | CD | 40.3 | 16.5 | No | 2017-11-06 | B2_s1_d1 | 0.41 | 5.9 | 15.3 | 732 | 40.5 | B2 | 13.3 | 0.06 | s1 | y | n | d1
TN_2017_758 |  | OP65619 | 401816G | VOLTALENE RH5Z1 (AS) 20KV 1X95K AL | 34.77 | 5 | Vilanova | XLPE+1420FEES+6000SEES | OD | 30 | 19.4 | No | 2017-11-06 | C_s1_d2 | 1.36 | 29.1 | 39.8 | 1383 | 49.9 | C | 17.8 | 0.07 | s1 | n | y | d2
TN_2017_759 |  | OP64583 20184157 | 402495V | LXHIOZ1 1X120 30KV | 44.23 | 5 | Vilanova | XLPE+1420FEES+6000SEES | OD | 25.7 | 20.6 | No | 2017-11-06 | D_s1_d2 | 1.74 | 36.7 | 56.2 | 1437 | 63.7 | D | 46.6 | 0.08 | s1 | n | y | d2
TN_2017_760 |  |  | Roll | FG16OR16 3G1.5 MM² - 0.6/1 KV ( ICEL CAVI) | 11.09 | 14 | Vilanova | COMPETITORSAMPLE | CD | 34.8 | 11.3 | No | 2017-11-07 | B2_s2_d0 | 0.59 | 6.1 | 13.2 | 648 | 45 | B2 | 104 | 0.29 | s2 | n | n | d0
TN_2017_761 |  |  |  | FG16OR16 3G1.5 MM² - 0.6/1 KV ( LA TRIVENETA) | 9.54 | 15 | Vilanova | COMPETITORSAMPLE | CD | 75.6 | 11.3 | No | 2017-11-07 | B2_s2_d0 | 1.14 | 8.9 | 22.5 | 573 | 86.7 | B2 | 204.8 | 0.57 | s2 | n | n | d0
TN_2017_762 |  |  |  | LA TRAVENETA CAVI FG16OM16 1KV 3G1.5 | 10.4 | 15 | Vilanova | COMPETITORSAMPLE | CD | 24.9 | 16.3 | No | 2017-11-07 | B2_s1_d0 | 0.35 | 7.4 | 14.4 | 711 | 40.4 | B2 | 26.7 | 0.03 | s1 | n | n | d0
TN_2017_763 |  |  |  | LA TRAVINETA CAVI FG16OM16 1KV 5G1.5 | 12.44 | 13 | Vilanova | COMPETITORSAMPLE | CD | 20.8 | 19.7 | No | 2017-11-07 | C_s1_d0 | 1.16 | 17.2 | 21.5 | 1059 | 42.9 | C | 16.5 | 0.03 | s1 | n | n | d0
TN_2017_764 |  |  |  | FG16OR16 5G1.5 MM² - 0.6/1 KV ( GENERAL CAVI) | 13.17 | 12 | Vilanova | COMPETITORSAMPLE | CD | 39.1 | 11 | No | 2017-11-08 | B2_s2_d2 | 0.95 | 12.5 | 17 | 960 | 60.2 | B2 | 165.7 | 0.35 | s2 | n | y | d2
TN_2017_765 |  |  | Roll | FG16OR16 3G1.5 MM² - 0.6/1 KV ( GENERAL CAVI) | 11.16 | 14 | Vilanova | COMPETITORSAMPLE | CD | 38.6 | 11.8 | No | 2017-11-08 | B2_s2_d0 | 1.11 | 11.6 | 23.5 | 636 | 83.5 | B2 | 228 | 0.66 | s2 | n | n | d0
TN_2017_766 |  |  | MATASSA | FG16OR16 5G1.5MM² - 0.6/1 KV | 14.1 | 11 | Vilanova | TALCUM+0500FPIT+2000SPIT | CD | 37.4 | 13.6 | No | 2017-11-08 | C_s2_d1 | 0.83 | 15.1 | 25.6 | 840 | 91.2 | C | 185.7 | 0.35 | s2 | y | n | d1
TN_2017_767 |  |  | 10H19240 | FG16R16 1X50MM² - 0.6/1 KV | 15.68 | 9 | Vilanova | TALCUM+0500FPIT+2000SPIT | CD | 36.7 | 16 | No | 2017-11-08 | C_s2_d0 | 0.72 | 15.4 | 24.5 | 1071 | 109.9 | C | 129.5 | 0.22 | s2 | n | n | d0
TN_2017_768 |  |  | T7F87936 | FG16OR16 2X1.5 MM² - 0.6/1 KV | 9.74 | 15 | Vilanova | TALCO+05ABFPIT+2000SPIT | CD | 35.1 | 18 | No | 2017-11-08 | C_s2_d0 | 0.72 | 10.6 | 19.5 | 600 | 197.8 | C | 107.8 | 0.45 | s2 | n | n | d0
17110004 |  | 17025 | -- | FR-N1 X1G1-U- 5G10MM² | 19.6 | 8 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 39.9 | 18.6 | No | 2017-11-13 | B2_s1_d0 | 0.45 | 3.2 | 4.7 | 1500 | 12 | B2 | 4 | 0.01 | s1 | n | n | d0
17110005 |  | 16996 | -- | 750-19X1.5-SH-NF F 55-625-255 | 21.7 | 7 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 39.6 | 19 | No | 2017-11-13 | B2_s1_d0 | 0.25 | 2.1 | 3.8 | 645 | 12 | B2 | 4 | 0.01 | s1 | n | n | d0
TN_2017_769 |  |  | 07F83472 | PRYSMIAN FG16M16 1 KV 1X16 | 10.71 | 14 | Vilanova | SXLPE+TNT+04AMFEIT+5300SEIT | CD | 49.7 | 11.2 | No | 2017-11-09 | B2_s1_d0 | 0.36 | 7.8 | 10.3 | 780 | 46.2 | B2 | 9.2 | 0.01 | s1 | n | n | d0
TN_2017_770 |  |  | T7F87930 | FG16OM16 4G1.5 MM² - 0.6/1 KV | 12.43 | 13 | Vilanova | CARTA+04AMFEIT+5300SEIT | CD | 48.2 | 12 | No | 2017-11-09 | B2_s1_d2 | 0.57 | 11.5 | 14 | 1326 | 40.3 | B2 | 13.4 | 0.02 | s1 | n | y | d2
TN_2017_771 |  |  | 08F74582 | PRYSMIAN FG16M16 1 KV 1X50 | 16.11 | 9 | Vilanova | TNT+04AMFEIT+5300SEIT | CD | 45 | 14.1 | No | 2017-11-09 | B2_s1_d0 | 0.35 | 5.1 | 8.6 | 1500 | 19.8 | B2 | 5.2 | 0.01 | s1 | n | n | d0
TN_2017_772 |  |  | 10H19239 | FG16R16 1X16MM² - 0.6/1 KV | 11.02 | 14 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 42.7 | 15.9 | No | 2017-11-09 | B2_s2_d0 | 0.45 | 10.7 | 15.2 | 729 | 103.2 | B2 | 68.1 | 0.31 | s2 | n | n | d0
TN_2017_773 |  |  | 07F87931 | FG16OM16 4X10 MM² - 0.6/1 KV | 19.1 | 8 | Vilanova | CARTA+04AMFEIT+5300SEIT | CD | 37.5 | 17.9 | No | 2017-11-09 | B2_s1_d0 | 0.5 | 6.6 | 12.7 | 1500 | 15.9 | B2 | 3.9 | 0.01 | s1 | n | n | d0
TN_2017_774 |  |  | F83757 | FG16OR16 4G10 MM² - 0.6/1 KV | 18.72 | 8 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 54.7 | 10.9 | No | 2017-11-10 | C_s2_d0 | 0.73 | 15.9 | 17.8 | 1227 | 138 | C | 128.4 | 0.31 | s2 | n | n | d0
TN_2017_775 |  |  | 398740N | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 19X1.5 | 23.59 | 7 | Vilanova | IRN267+GRI141+GRI141 | OD | 53.5 | 11.3 | No | 2017-11-10 | B2_s1_d1 | 0.25 | 7.5 | 11.5 | 1500 | 17.2 | B2 | 12.5 | 0.03 | s1 | y | n | d1
TN_2017_776 |  |  | 403753M | BLINDEX Z1C4Z1-K 1KV (AS) 2X1.5 | 9.25 | 17 | Vilanova | 1602SEES | OD | 49 | 13.4 | No | 2017-11-10 | B2_s1_d0 | 0.67 | 11 | 17.8 | 669 | 66.6 | B2 | 5.8 | 0.01 | s1 | n | n | d0
TN_2017_777 |  | OP65175 SAP 20228082 | 397924B | BLINDEX Z1C4Z1-K 500V (AS) 12G1MM2 | 13.18 | 12 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 43.9 | 16.2 | No | 2017-11-10 | B2_s1_d0 | 0.47 | 9.8 | 13.5 | 981 | 32 | B2 | 6.1 | 0.01 | s1 | n | n | d0
TN_2017_778 |  | OP64583 20184157 | 402495V | LXHIOZ1 1X120 30KV | 45.04 | 4 | Vilanova | XLPE+1420FEES+6000SEES | OD | 37 | 23.6 | No | 2017-11-10 | D_s1_d2 | 1.71 | 38.9 | 59.7 | 1500 | 65.8 | D | 13 | 0.04 | s1 | n | y | d2
TN_2017_779 |  |  | 403740Y | BLINDEX Z1C4Z1-K 1KV (AS) 3G1.5 | 9.33 | 17 | Vilanova | 1602SEES | OD | 37.7 | 21.6 | No | 2017-11-10 | B2_s1_d0 | 0.43 | 6.1 | 10.9 | 624 | 46 | B2 | 4.1 | 0.01 | s1 | n | n | d0
TN_2017_780 |  |  | 405445B | BLINDEX Z1C4Z1-K 1KV (AS) 4G1.5 | 10.61 | 14 | Vilanova | 1602SEES | OD | 62.2 | 13.8 | No | 2017-11-12 | B2_s1_d0 | 0.29 | 4.7 | 9.3 | 699 | 36 | B2 | 9.6 | 0.01 | s1 | n | n | d0
TN_2017_781 |  | OP65177 SAP 20228084 | 398690J | BLINDEX Z1C4Z1-K 1KV (AS) 4G10MM2 | 17.37 | 9 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 62.3 | 13.8 | No | 2017-11-12 | B2_s1_d0 | 0.42 | 7.4 | 8.7 | 1044 | 29.2 | B2 | 1 | 0 | s1 | n | n | d0
TN_2017_782 |  |  | 393260G | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 5G1.5 | 16.4 | 9 | Vilanova | SXLPE+1602SEES | OD | 54.7 | 17.6 | No | 2017-11-12 | B2_s1_d2 | 0.75 | 14.2 | 23.1 | 1032 | 32.1 | B2 | 4.2 | 0.02 | s1 | n | y | d2
TN_2017_783 |  |  | MATASSA | FG16OR16 5G1.5MM² - 0.6/1 KV | 14.11 | 11 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 45.2 | 14.1 | No | 2017-11-13 | C_s2_d0 | 0.73 | 18.1 | 23.9 | 840 | 243 | C | 141.5 | 0.29 | s2 | n | n | d0
TN_2017_784 |  |  | MATASSA | FG16OR16 2X6 MM² - 0.6/1 KV | 13.21 | 12 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 33.3 | 11.3 | No | 2017-11-14 | C_s2_d0 | 0.73 | 18.7 | 24.9 | 816 | 214.3 | C | 114.9 | 0.26 | s2 | n | n | d0
TN_2017_785 |  |  | 080P02623 | NEXANS AL SECURE RZ1-K (AS) 1KV 1X240 | 27.62 | 6 | Vilanova | COMPETITORSAMPLE | OD | 33.3 | 11.7 | No | 2017-11-14 | C_s1_d2 | 1.24 | 23.9 | 57.5 | 1398 | 52.4 | C | 15.6 | 0.08 | s1 | n | y | d2
TN_2017_786 |  |  | 10F62195 | FG10OM1 3X1.5 | 12.8 | 12 | Vilanova | ID2900+0400FEIT+5300SEIT | CD | 31.2 | 13.6 | No | 2017-11-14 | B2_s1_d2 | 0.75 | 13.4 | 23.8 | 786 | 71.8 | B2 | 18 | 0.03 | s1 | n | y | d2
TN_2017_787 |  |  |  | NEXANS ALSECURE RZ1-K (AS) 1KV 3G2.5 | 11.96 | 13 | Vilanova | COMPETITORSAMPLE | OD | 27.5 | 16.7 | No | 2017-11-14 | C_s1_d2 | 1.75 | 27.7 | 36.1 | 891 | 77.8 | C | 16 | 0.02 | s1 | n | y | d2
TN_2017_788 |  | OP64581 20184155 | 391249W | LXHIOZ1 1X500 15KV | 50.35 | 4 | Vilanova | XLPE+1420FEES+6000SEES | OD | 24.4 | 18.7 | No | 2017-11-14 | C_s1_d2 | 1.1 | 23.6 | 34.7 | 1335 | 45.6 | C | 0.6 | 0.01 | s1 | n | y | d2
TN_2017_789 |  | OP63395 | 391251Y | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44.88 | 4 | Vilanova | XLPE+1420FEES+6000SEES | OD | 46.7 | 10.7 | No | 2017-11-16 | C_s1_d2 | 1.1 | 24.9 | 39.4 | 1428 | 44.8 | C | 9.8 | 0.05 | s1 | n | y | d2
TN_2017_790 |  | OP65394 | 391252Z | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 45.48 | 4 | Vilanova | XLPE+1420FEES+6000SEES | OD | 46.7 | 10.9 | No | 2017-11-16 | D_s1_d2 | 1.23 | 30.9 | 46.2 | 1431 | 51.4 | D | 5.8 | 0.02 | s1 | n | y | d2
TN_2017_791 |  | OP64582 20184156 | 391258F | XHIOZ1 1X500 15KV | 50.34 | 4 | Vilanova | XLPE+1420FEES+6000SEES | OD | 43 | 13.2 | No | 2017-11-16 | C_s1_d2 | 1.05 | 20.2 | 30.7 | 1434 | 37.5 | C | 9.3 | 0.02 | s1 | n | y | d2
TN_2017_792 |  | OP64582 20184156 | 391255C | XHIOZ1 1X500 15KV | 50.54 | 4 | Vilanova | XLPE+1420FEES+6000SEES | OD | 39.2 | 17.8 | No | 2017-11-16 | C_s1_d2 | 1.25 | 27.6 | 45.4 | 1500 | 53.5 | C | 14.1 | 0.03 | s1 | n | y | d2
17110007 |  | 16996 | -- | 1000-3G10MM²-SH-NF F 55-625-255 | 17.6 | 8 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 34.7 | 20.4 | No | 2017-11-16 | B2_s1_d2 | 0.6 | 4.2 | 9.1 | 1500 | 12 | B2 | 5 | 0.01 | s1 | y | y | d2
17110008 |  | 16996 | -- | 1000-3G16MM²-SH-NF F55-625-255 | 20.8 | 7 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 35.9 | 20.2 | No | 2017-11-16 | B2_s1_d2 | 0.65 | 4.8 | 11.8 | 1500 | 13 | B2 | 5 | 0.01 | s1 | y | y | d2
17110009 |  | 17010 | -- | RCOCD-1B-025090-D001F-KPD | 2.05 | 330 | Paron | 1700SEIT | -- | 34.2 | 21.3 | No | 2017-11-16 | B2_s1_d0 | 1.33 | 11.4 | 26.8 | 714 | 85 | B2 | 13 | 0.04 | s1 | n | n | d0
17110010 |  | 17035 | -- | 32F DRY VT (SANS MICA) | 14.4 | 11 | Paron | 1700SEES | -- | 37 | 18.9 | No | 2017-11-20 | D_s2_d1 | 2.2 | 36 | 51.5 | 978 | 90 | D | 70 | 0.1 | s2 | y | n | d1
17110011 |  | 17035 | -- | 32F DRY VT (AVEC MICA) | 14 | 11 | Paron | 1700SEES | -- | 37.8 | 19.7 | No | 2017-11-20 | D_s2_d1 | 2.8 | 39.7 | 54.4 | 939 | 96 | D | 97 | 0.12 | s2 | y | n | d1
17110012 |  | 17035 | -- | 32F DRY KT (SANS MICA) | 13.7 | 11 | Paron | 1700SEES | -- | 43.2 | 19.7 | No | 2017-11-20 | D_s2_d2 | 2.7 | 37 | 52.5 | 978 | 92 | D | 87 | 0.13 | s2 | y | y | d2
17110013 |  | 17039 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.3 | 6 | Paron | TNT+04AMFEIT+5300SEIT | -- | 34.6 | 23 | No | 2017-11-22 | B2_s1_d2 | 0.7 | 8.6 | 22.6 | 1494 | 19 | B2 | 6 | 0.01 | s1 | y | y | d2
17110017 |  | 17039 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.6 | 6 | Paron | CARTA+04AMFEIT+5300SEIT | -- | 35.2 | 23 | No | 2017-11-22 | B2_s1_d1 | 0.45 | 3.4 | 4.7 | 576 | 17 | B2 | 4 | 0.01 | s1 | y | n | d1
17110014 |  | 17039 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.4 | 6 | Paron | NASTROCARTARIEMPITIVOSPAGNOLO1420FEES | -- | 36.4 | 22.5 | No | 2017-11-22 | B2_s1_d0 | 0.6 | 5.5 | 7.5 | 1500 | 15 | B2 | 6 | 0.01 | s1 | n | n | d0
17110015 |  | 17039 | -- | FG16OM16 5G35 MM² - 0.6/1 KV | 31 | 6 | Paron | CARTA+04AMFEIT+5300SEIT | -- | 37.2 | 22.9 | No | 2017-11-22 | B2_s1_d0 | 0.3 | 3.9 | 4.6 | 792 | 17 | B2 | 3 | 0 | s1 | n | n | d0
17110016 |  | 17039 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.6 | 6 | Paron | NASTROTNTRIEMPITIVOSPAGNOLO1420FEES | -- | 35.3 | 23.3 | No | 2017-11-22 | B2_s1_d1 | 0.6 | 4.5 | 7.1 | 1500 | 15 | B2 | 4 | 0.01 | s1 | y | n | d1
17110018 |  | 17039 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.4 | 6 | Paron | NASTROCARTARIEMPITIVOSPAGNOLO1420FEES | -- | 40.3 | 19.9 | No | 2017-11-27 | B2_s1_d1 | 0.6 | 4.2 | 7.4 | 1500 | 10 | B2 | 5 | 0.01 | s1 | y | n | d1
17110019 |  | 17039 | -- | FG16OM16 5G35 MM² - 0.6/1 KV | 31 | 6 | Paron | CARTA+04AMFEIT+5300SEIT | -- | 39.6 | 19.6 | No | 2017-11-27 | B2_s1_d0 | 0.4 | 1.8 | 3.2 | 681 | 8 | B2 | 4 | 0.01 | s1 | n | n | d0
17110020 |  | 17039 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.6 | 6 | Paron | NASTROTNTRIEMPITIVOSPAGNOLO1420FEES | -- | 40.7 | 19.9 | No | 2017-11-27 | B2_s1_d1 | 0.6 | 4.7 | 8.6 | 1500 | 12 | B2 | 5 | 0.01 | s1 | y | n | d1
17110021 |  | 17039 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.6 | 6 | Paron | CARTA+04AMFEIT+5300SEIT | -- | 40.6 | 20.3 | No | 2017-11-27 | B2_s1_d0 | 0.4 | 2.8 | 4.4 | 687 | 11 | B2 | 4 | 0.01 | s1 | n | n | d0
17110022 |  | 17039 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.3 | 6 | Paron | TNT+04AMFEIT+5300SEIT | -- | 38.8 | 20.4 | No | 2017-11-27 | B2_s1_d2 | 0.7 | 4.5 | 8.4 | 1500 | 11 | B2 | 6 | 0.01 | s1 | y | y | d2
TN_2017_793 |  | OP82291888 SAP 20165688 | 405959K | BALIZAS ORANGE | 18.36 | 8 | Vilanova | 1602SEES | OD | 67.9 | 14.9 | No | 2017-11-23 | E ou F_s2_d2 | 3.3 | 71.8 | 177 | 1491 | 151 | E ou F | 92.6 | 0.24 | s2 | n | y | d2
TN_2017_794 |  |  | CERVI A48151 | TOP CABLE TOXFREE ZH Z1Z1-K(AS) 7G1.5 1KV | 11.05 | 14 | Vilanova | COMPETITORSAMPLE | OD | 45 | 15.5 | No | 2017-11-23 | B2_s1_d0 | 0.43 | 12.7 | 21.3 | 885 | 50.1 | B2 | 3.5 | 0.02 | s1 | n | n | d0
TN_2017_795 |  | OP 65008 | Box | AFUMEX CLASS 750V HO7Z1-R (AS) TYPE2 1X10 | 6 | 25 | Vilanova | 1602SEES | OD | 51.2 | 23 | No | 2017-11-23 | B2_s1_d0 | 0.29 | 2 | 4.1 | 489 | 16.9 | B2 | 0 | 0 | s1 | n | n | d0
TN_2017_796 |  |  | 481814E | AFUMEX CLASS RZ1-K (AS) 1KV 1X630 | 48.63 | 4 | Vilanova | SXLPE+1420FEES+1602SEES | OD | 45.4 | 13.8 | No | 2017-11-27 | B2_s1_d0 | 0.38 | 5.2 | 6.8 | 681 | 19.5 | B2 | 4.4 | 0.01 | s1 | n | n | d0
TN_2017_797 |  |  | 286370X | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 4X185 | 70 | 3 | Vilanova | 1602SEES | OD | 35.6 | 19.8 | No | 2017-11-27 | B2_s1_d0 | 0.38 | 5.3 | 7.3 | 648 | 21 | B2 | 0.7 | 0 | s1 | n | n | d0
TN_2017_798 |  | OP 65009 | Box | AFUMEX CLASS 750V HO7Z1-R (AS) TYPE2 1X16 | 6.77 | 21 | Vilanova | 1602SEES | OD | 37.5 | 17.9 | No | 2017-11-27 | B2_s1_d0 | 0.28 | 3.4 | 5.4 | 795 | 20 | B2 | 1 | 0 | s1 | n | n | d0
TN_2017_799 |  | OP 65007 | Box | AFUMEX CLASS 750V HO7Z1-R (AS) TYPE2 1X2.5 | 3.66 | 105 | Vilanova | 1602SEES | OD | 56.4 | 10.6 | No | 2017-11-28 | B2_s1_d0 | 0.9 | 8.9 | 17.3 | 615 | 55.2 | B2 | 10.5 | 0.04 | s1 | n | n | d0
TN_2017_800 |  |  | 407644S | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 19X1.5 | 22.27 | 7 | Vilanova | 1602SEES | OD | 52.5 | 12.3 | No | 2017-11-28 | B2_s1_d0 | 0.85 | 9.2 | 24.2 | 1485 | 20.5 | B2 | 2.4 | 0.02 | s1 | n | n | d0
TN_2017_801 |  |  | 10G84102 | RG7OM1NM1 3X10 | 26.77 | 6 | Vilanova | ID7600+0400FEIT+5300SEIT+STEELTAPE+5300SEIT | CD | 47.5 | 14.3 | No | 2017-11-28 | C_s1_d2 | 1.2 | 23.1 | 56.4 | 1461 | 48.6 | C | 20.8 | 0.08 | s1 | n | y | d2
TN_2017_802 |  |  | 10G84100 | RG7OM1NM1 2X25 | 30.43 | 6 | Vilanova | ID7600+0400FEIT+5300SEIT+STEELTAPE+5300SEIT | CD | 36.3 | 19.1 | No | 2017-11-28 | B2_s1_d2 | 0.68 | 14.1 | 23.1 | 1449 | 26.1 | B2 | 10.1 | 0.03 | s1 | n | y | d2
TN_2017_803 |  |  |  | AENOR USE HAR 338 NX HO7Z1-K TYPE 3 (AS) 2017 1X1.5 | 2.9 | 165 | Vilanova | COMPETITORSAMPLE | OD | 33.6 | 17.3 | No | 2017-11-28 | C_s1_d0 | 1.13 | 17.1 | 25.1 | 735 | 99.4 | C | 39.6 | 0.1 | s1 | n | n | d0
TN_2017_804 |  |  | 7-F83206 | FG16R16 1X1.5MM² - 0.6/1 KV | 8.13 | 19 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 50.2 | 9.9 | No | 2017-11-29 | D_s2_d0 | 0.5 | 16 | 23.2 | 360 | 396.4 | D | 99.5 | 0.6 | s2 | n | n | d0
TN_2017_805 |  |  |  | AENOR USE HAR 338 NX HO7Z1-K TYPE 3 (AS) 2017 1X2.5 | 3.65 | 105 | Vilanova | COMPETITORSAMPLE | OD | 48.9 | 10.3 | No | 2017-11-29 | C_s1_d0 | 1.45 | 13.9 | 30.5 | 639 | 94.7 | C | 30.4 | 0.08 | s1 | n | n | d0
17110023 |  | 17035 | -- | 32F DRY KT (AVEC MICA) | 13.7 | 11 | Paron | 1700SEES | -- | 34.8 | 19 | No | 2017-11-29 | D_s2_d1 | 2.5 | 33.1 | 48.4 | 996 | 82 | D | 91 | 0.11 | s2 | y | n | d1
17110024 |  | 17035 | -- | 32F FILLED VT (SANS MICA) | 13.6 | 11 | Paron | 1700SEES | -- | 33.4 | 20.5 | No | 2017-11-29 | E ou F_s2_d2 | 3.3 | 118.3 | 286.6 | 1254 | 283 | E ou F | 238 | 0.72 | s2 | y | y | d2
TN_2017_806 |  |  | 07-F85594 | AFUMEX GOLD 1KV 5G1.5 IEMMEQU | 16.02 | 9 | Vilanova | SCAPA+0600FEIT+5300SEIT | CD | 43.8 | 10.6 | No | 2017-11-30 | C_s1_d2 | 0.74 | 16.7 | 24.5 | 1317 | 34.2 | C | 10.7 | 0.02 | s1 | y | y | d2
TN_2017_807 |  |  | 07-F85584 | AFUMEX GOLD 1KV 5G1.5 IEMMEQU | 16.09 | 9 | Vilanova | CARTA+0600FEIT+5300SEIT | CD | 44 | 10 | No | 2017-11-30 | B2_s1_d1 | 0.41 | 8.6 | 13.3 | 1215 | 25.3 | B2 | 2.1 | 0.01 | s1 | y | n | d1
TN_2017_808 |  |  | 10-H12629 | PRYSMIAN FG16M16 1 KV 1X50 | 15.95 | 9 | Vilanova | TNT+0400FEIT+5300SEIT | CD | 45.1 | 11.1 | No | 2017-11-30 | B2_s1_d1 | 0.3 | 7.1 | 9 | 1500 | 24.6 | B2 | 4.9 | 0.01 | s1 | y | n | d1
TN_2017_809 |  |  | 10-H15948 | FG16R16 1X35MM² - 0.6/1 KV | 14.25 | 11 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 34.6 | 13.8 | No | 2017-11-30 | C_s2_d0 | 0.5 | 14.2 | 15.9 | 1071 | 186.7 | C | 67.2 | 0.19 | s2 | n | n | d0
TN_2017_810 |  |  | 07-F85634 | AFUMEX GOLD 1KV 5G1.5 IEMMEQU | 15.58 | 9 | Vilanova | SKINLSOH+CARTA+0600FEIT+5300SEIT | CD | 29.2 | 16 | No | 2017-11-30 | B2_s1_d1 | 0.45 | 9.8 | 14.3 | 1215 | 29.9 | B2 | 5 | 0.01 | s1 | y | n | d1
TN_2017_811 |  | OP65352 20230351 | 401833A | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 5X120 | 61.98 | 3 | Vilanova | INSULATIONIRN267+GRI141+ARMOURED+SHEATHGRI141 | OD | 42.4 | 13.7 | No | 2017-12-01 | B2_s1_d2 | 0.3 | 9.1 | 18.2 | 1461 | 19.1 | B2 | 6.5 | 0.03 | s1 | y | y | d2
TN_2017_812 |  | OP65195 20229612 | 409551P | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 3X70 | 40.58 | 5 | Vilanova | INSULATIONIRN267+GRI141+ARMOURED+SHEATHGRI141 | OD | 36.6 | 8.2 | No | 2017-12-04 | B2_s1_d2 | 0.34 | 11.3 | 16.6 | 1251 | 22.2 | B2 | 7.8 | 0.01 | s1 | n | y | d2
TN_2017_813 |  | OP65194 20229611 | 409526M | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 1X500 | 49.13 | 4 | Vilanova | INSULATIONIRN267+GRI141+ARMOURED+SHEATHGRI141 | OD | 37.7 | 8.5 | No | 2017-12-04 | B2_s1_d2 | 0.39 | 6 | 10.3 | 1071 | 13.3 | B2 | 11.9 | 0.02 | s1 | y | y | d2
1712002 |  | 17035 | -- | 32F FILLED VT (AVEC MICA) | 14.3 | 11 | Paron | 1700SEES | -- | 42.4 | 19.8 | No | 2017-12-04 | E ou F_s2_d1 | 3.3 | 110.8 | 226 | 1287 | 234 | E ou F | 268 | 0.85 | s2 | y | n | d1
TN_2017_814 |  |  | 396530L | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 77.5 | 3 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | OD | 51 | 12.2 | No | 2017-12-05 | C_s1_d2 | 1.16 | 22.4 | 36.8 | 1104 | 57.4 | C | 10.4 | 0.05 | s1 | y | y | d2
TN_2017_815 |  |  | 396530L | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 77.5 | 3 | Vilanova | XLPE+ALFOIL+6000SEESGRIS+SKINSC | OD | 39.6 | 16.9 | No | 2017-12-05 | C_s1_d2 | 1.6 | 27.8 | 43.2 | 1452 | 56.2 | C | 7.8 | 0.01 | s1 | y | y | d2
17120003 |  | 17067 | -- | K22 60X1.6-SH-NF F 55-622-PRYSMIAN 255 | 39 | 5 | Paron | IX4800IT+5300SEIT | -- | 36.7 | 19.7 | No | 2017-12-06 | B2_s1_d2 | 0.3 | 2.8 | 4.7 | 540 | 18 | B2 | 13 | 0.02 | s1 | y | y | d2
17102004 |  | 17042 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 ( IRRADIÉ) | 2.89 | 165 | Paron | 1602SEES | -- | 33 | 19 | No | 2017-12-06 | B2_s1_d1 | 1.09 | 9.2 | 18.7 | 735 | 54 | B2 | 31 | 0.09 | s1 | y | n | d1
17102005 |  | 17042 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 ( IRRADIÉ) | 2.91 | 165 | Paron | 1602SEES | -- | 31.9 | 22.7 | No | 2017-12-06 | C_s1_d1 | 1.1 | 12.8 | 32.6 | 759 | 74 | C | 26 | 0.06 | s1 | y | n | d1
17102006 |  | 17035 | -- | ORANGE DRAKA SR 07/11/2017 L1120 M4 72 FO G657A2 OHC FRC | 8.4 | 19 | Paron | 1700SEES | -- | 31.8 | 21.9 | No | 2017-12-06 | D_s2_d1 | 3.3 | 46.4 | 203.8 | 705 | 510 | D | 89 | 0.42 | s2 | y | n | d1
TN_2017_816 |  |  | TN-F35412 | RG16H1M16 12/20KV 1X25 | 27.01 | 7 | Vilanova | SCAPA+0400FEIT+5300SEIT | CD | 63.2 | 10.7 | No | 2017-12-07 | D_s1_d2 | 1.12 | 18.3 | 67.1 | 1497 | 56.1 | D | 15.4 | 0.12 | s1 | y | y | d2
TN_2017_817 |  |  | TN-F35412 | RG16H1M16 18/30KV 1X630 | 60.1 | 4 | Vilanova | SCAPA+0400FEIT+5300SEIT | CD | 63.6 | 11.8 | No | 2017-12-07 | B2_s1_d0 | 0.56 | 5.4 | 7.4 | 1500 | 18.5 | B2 | 0 | 0 | s1 | n | n | d0
17120007 |  | 17066 | -- | DRAKA 2017 1 F.O. 10D-7A2 INT MOVISTAR (DRY INDOOR DROP Ø 4.2MM ) | 4.2 | 75 | Paron | 1700SEES | -- | 35.1 | 22 | No | 2017-12-08 | D_s1_d0 | 3.3 | 44.7 | 55.5 | 1137 | 137 | D | 41 | 0.06 | s1 | n | n | d0
17120008 |  | 17066 | -- | DRAKA 2017 1 F.O. 10D-7A2 INT MOVISTAR (DRY INDOOR DROP Ø 4.2MM ) | 4.2 | 75 | Paron | CYGSALHC-1800/R | -- | 33 | 19 | No | 2017-12-08 | D_s2_d0 | 3.3 | 62.6 | 142.1 | 1002 | 203 | D | 59 | 0.11 | s2 | n | n | d0
17120009 |  | 17010 | -- | FO DISTR MM 68 D1 | 6.8 | 31 | Paron | 1700SEES | -- | 30.9 | 19.6 | No | 2017-12-09 | C_s1_d2 | 1.8 | 16.4 | 39.6 | 630 | 131 | C | 18 | 0.04 | s1 | y | y | d2
17120010 |  | 17077 | -- | 16X1 UG10OG10M2NM1 | 20 | 8 | Paron | ID2900+SD3500IT+SV3400IT | -- | 41.7 | 21.9 | No | 2017-12-11 | B2_s1_d2 | 0.8 | 12.4 | 17.9 | 1314 | 22 | B2 | 29 | 0.05 | s1 | y | y | d2
17120011 |  | 17077 | -- | PRYSMIAN(P) 20213358-804/295 2X25MM² -EFSAT-2017 | 31 | 6 | Paron | ID7600+5300SEIT+5300SEIT | -- | 38.3 | 22 | No | 2017-12-11 | B2_s1_d2 | 0.6 | 10.7 | 22.9 | 1500 | 22 | B2 | 11 | 0.03 | s1 | y | y | d2
17120012 |  | 17077 | -- | PRYSMIAN(P) 20213357-804/295 3X10MM² -EFSAT CPR-2017 | 26.5 | 6 | Paron | ID7600+5300SEIT+5300SEIT | -- | 35.3 | 22 | No | 2017-12-11 | D_s1_d2 | 0.7 | 23.6 | 74.1 | 1500 | 62 | D | 30 | 0.15 | s1 | y | y | d2
TN_2017_818 |  | OP 65550 20080354 | 030874J | AL-HEPRZ1(AS) 1X300MM2 36/66KV | 55.92 | 4 | Vilanova | HEPR+1420FEES+6000SEES | OD | 60.4 | 15.6 | No | 2017-12-11 | B2_s1_d2 | 0.7 | 14.3 | 16.9 | 942 | 40.8 | B2 | 5.1 | 0.02 | s1 | y | y | d2
TN_2017_819 |  | OP 65548 20231837 | 336593M | AL-HEPRZ1(AS) 1X500MM2 26/45KV | 57.45 | 4 | Vilanova | HEPR+1420FEES+6000SEES | OD | 57.9 | 9.3 | No | 2017-12-12 | C_s1_d2 | 0.79 | 25 | 43.9 | 1395 | 44.2 | C | 11.8 | 0.02 | s1 | y | y | d2
TN_2017_820 |  |  | 372413X | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 75.62 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS+SKINSC | OD | 56.4 | 10.4 | No | 2017-12-12 | C_s1_d2 | 0.84 | 22.1 | 32.6 | 1338 | 43.1 | C | 4.9 | 0.01 | s1 | y | y | d2
TN_2017_821 |  |  | 372413X | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 75.62 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS+SKINSC | OD | 49.7 | 13.5 | No | 2017-12-12 | C_s1_d2 | 0.81 | 15.2 | 17.3 | 1296 | 43.5 | C | 8.7 | 0.02 | s1 | y | y | d2
17120013 |  | 17063 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 28 | 6 | Paron | SXLPE+1400FEIT+5300SEIT | -- | 31.9 | 22 | No | 2017-12-13 | B2_s1_d2 | 0.5 | 5.1 | 7.9 | 1299 | 19 | B2 | 6 | 0.01 | s1 | y | y | d2
17120014 |  | 17063 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.9 | 6 | Paron | SXLPE+1400FEIT+5300SEIT | -- | 32.5 | 21.6 | No | 2017-12-13 | C_s1_d2 | 0.6 | 12.1 | 37.7 | 1494 | 32 | C | 8 | 0.03 | s1 | y | y | d2
17120015 |  | 17063 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 14.3 | 11 | Paron | SXLPE+1400FEIT+5300SEIT | -- | 36 | 21.3 | No | 2017-12-13 | C_s1_d2 | 1.1 | 22.2 | 34.9 | 1230 | 46 | C | 45 | 0.08 | s1 | y | y | d2
17120016 |  | 17063 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 14.3 | 11 | Paron | SXLPE+1400FEIT+5300SEIT | -- | 31.4 | 23 | No | 2017-12-14 | C_s1_d2 | 1.1 | 22.4 | 42.8 | 1200 | 48 | C | 42 | 0.1 | s1 | y | y | d2
TN_2017_822 |  |  | 481814E | AFUMEX CLASS RZ1-K (AS) 1KV 1X630 | 48.63 | 4 | Vilanova | SXLPE+1420FEES+1602SEES | OD | 54.8 | 15 | No | 2017-12-14 | B2_s1_d0 | 0.41 | 3.8 | 6 | 993 | 14.4 | B2 | 4.7 | 0.01 | s1 | n | n | d0
TN_2017_823 |  |  | 395457V | AFUMEX CLASS RZ1-K (AS) 1KV 4G240 | 62.5 | 3 | Vilanova | SXLPE+1420FEES+1602SEES | OD | 53.8 | 15.8 | No | 2017-12-14 | B2_s1_d0 | 0.63 | 5.3 | 7.7 | 918 | 19.2 | B2 | 3.1 | 0 | s1 | n | n | d0
TN_2017_824 |  | OP64373 | 395152N | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 10X2.5 | 20.99 | 7 | Vilanova | PENDING | OD | 48 | 17.8 | No | 2017-12-14 | B2_s1_d0 | 0.55 | 8.4 | 15.3 | 1410 | 17.3 | B2 | 8.9 | 0.02 | s1 | n | n | d0
TN_2017_825 |  |  | 407644S | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 19X1.5 | 22.27 | 7 | Vilanova | 1602SEES | OD | 50.3 | 17 | No | 2017-12-14 | B2_s1_d1 | 0.81 | 9.2 | 23.3 | 1500 | 26.5 | B2 | 6.1 | 0.03 | s1 | y | n | d1
TN_2017_826 |  |  | 343557G | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS+SKINSC | OD | 51.7 | 17.4 | No | 2017-12-14 | B2_s1_d2 | 0.78 | 12.3 | 17.5 | 1458 | 30.5 | B2 | 7.9 | 0.02 | s1 | y | y | d2
TN_2017_827 |  |  | 393260G | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 5G1.5 | 16.4 | 9 | Vilanova | SXLPE+1602SEES | OD | 53.1 | 15.2 | No | 2017-12-15 | B2_s1_d1 | 0.78 | 13.8 | 20.4 | 1080 | 35.8 | B2 | 21.8 | 0.03 | s1 | y | n | d1
TN_2017_828 |  |  | 286370X | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 4X185 | 70 | 3 | Vilanova | 1602SEES | OD | 43.9 | 16.2 | No | 2017-12-15 | B2_s1_d0 | 0.38 | 3.6 | 5.4 | 648 | 16.3 | B2 | 1.4 | 0 | s1 | n | n | d0
TN_2017_829 |  | OP 65550 20080354 | 030874J | AL-HEPRZ1(AS) 1X300MM2 36/66KV | 55.92 | 4 | Vilanova | HEPR+1420FEES+6000SEES | OD | 26.7 | 24 | No | 2017-12-15 | C_s1_d2 | 0.95 | 18.6 | 30.7 | 1500 | 44.3 | C | 5.8 | 0.01 | s1 | y | y | d2
TN_2017_830 |  | OP 65548 20231837 | 336593M | AL-HEPRZ1(AS) 1X500MM2 26/45KV | 57.45 | 4 | Vilanova | HEPR+1420FEES+6000SEES | OD | 24.5 | 23.5 | No | 2017-12-15 | C_s1_d2 | 0.84 | 15.4 | 25 | 1374 | 30.4 | C | 7.4 | 0.02 | s1 | y | y | d2
TN_2017_831 |  | OP65175 SAP 20228082 | 397924B | BLINDEX Z1C4Z1-K 500V (AS) 12G1MM2 | 13.18 | 12 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 50 | 11.7 | No | 2017-12-18 | B2_s1_d0 | 0.72 | 9.3 | 15.7 | 996 | 35.9 | B2 | 9.6 | 0.02 | s1 | n | n | d0
TN_2017_832 |  | OP65176 SAP 20228083 | 397927E | BLINDEX Z1C4Z1-K 500V (AS) 16G1MM2 | 14.79 | 10 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 50.3 | 12.1 | No | 2017-12-18 | B2_s1_d0 | 0.42 | 6.8 | 9.9 | 873 | 35.2 | B2 | 8.6 | 0.01 | s1 | n | n | d0
TN_2017_833 |  | OP65174 SAP 20228081 | 398674S | BLINDEX Z1C4Z1-K 500V (AS) 2X1MM2 | 7.36 | 21 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 49.3 | 12.6 | No | 2017-12-18 | C_s1_d0 | 1.37 | 15.1 | 40 | 669 | 123.2 | C | 22 | 0.07 | s1 | n | n | d0
TN_2017_834 |  | OP65177 SAP 20228084 | 398690J | BLINDEX Z1C4Z1-K 1KV (AS) 4G10MM2 | 17.37 | 9 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 59.7 | 8 | No | 2017-12-19 | B2_s1_d1 | 0.41 | 7.1 | 8.9 | 996 | 23.5 | B2 | 5.8 | 0.01 | s1 | y | n | d1
TN_2017_835 |  | OP65178 SAP 20228085 | 395839K | BLINDEX Z1C4Z1-K 1KV (AS) 12G1.5MM2 | 16.13 | 9 | Vilanova | INS:=1602SEES+PETTAPE+CUPU+TALCUM+SHEATH1602SEES | OD | 61.2 | 8 | No | 2017-12-19 | B2_s1_d0 | 0.38 | 5.7 | 8.2 | 783 | 26.7 | B2 | 0.9 | 0 | s1 | n | n | d0
TN_2017_836 |  | OP66210 20226667 | 414680P | AFUMEX CLASS 1KV Z1Z1-K (AS) 12X1.5MM2 | 15.05 | 10 | Vilanova | INSULATION1602SEES+SHEATH1602SEESWITHADITIVELE210025AL1.5% | OD | 55.6 | 10.8 | No | 2017-12-19 | B2_s1_d0 | 0.61 | 10.3 | 14.3 | 798 | 35.3 | B2 | 1 | 0 | s1 | n | n | d0
TN_2017_837 |  | OP66209 20226646 | 414671E | AFUMEX CLASS 1KV Z1Z1-K (AS) 7X2.5MM2 | 13.35 | 11 | Vilanova | INSULATION1602SEES+SHEATH1602SEESWITHADITIVELE210025AL1.5% | OD | 24 | 25.8 | No | 2017-12-19 | B2_s1_d0 | 0.73 | 11.9 | 16.1 | 1146 | 38.6 | B2 | 16.4 | 0.03 | s1 | n | n | d0
TN_2017_838 |  |  | 398740N | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 19X1.5 | 23.59 | 7 | Vilanova | IRN267+GRI141+GRI141 | OD | 21.9 | 28 | No | 2017-12-19 | B2_s1_d1 | 0.4 | 6.6 | 11.6 | 1425 | 15.7 | B2 | 21.3 | 0.05 | s1 | y | n | d1
17120017 |  | 17063 | -- | FG16OM16 5G10 MM² - 0.6/1 KV | 20.3 | 8 | Paron | SXLPE+1400FEIT+5300SEIT | -- | 32.1 | 21.6 | No | 2017-12-19 | B2_s1_d0 | 0.4 | 5.4 | 8.8 | 1500 | 23 | B2 | 3 | 0.01 | s1 | n | n | d0
17120018 |  | 17063 | -- | FG16OM16 5G10 MM² - 0.6/1 KV | 20.2 | 8 | Paron | SXLPE+1400FEIT+5300SEIT | -- | 32.8 | 21.6 | No | 2017-12-19 | B2_s1_d0 | 0.5 | 5.1 | 7.8 | 1482 | 25 | B2 | 4 | 0.01 | s1 | n | n | d0
17120020 |  | 17042 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 | 2.89 | 165 | Paron | 1602SEES | -- | 43.7 | 21.5 | No | 2017-12-21 | B2_s1_d0 | 1.1 | 8.6 | 17.5 | 783 | 54 | B2 | 21 | 0.05 | s1 | n | n | d0
17120020 |  | 17089 | -- | FR-N1X1G1 5G1.5MM² | 12.6 | 12 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 42.1 | 22.6 | No | 2017-12-21 | B2_s2_d2 | 1 | 12.8 | 24.2 | 1149 | 40 | B2 | 70 | 0.23 | s2 | y | y | d2
18010001 |  | 17096 | -- | FG16OM16 3G10 MM² - 0.6/1 KV | 16 | 9 | Paron | SXLPE+1420FEES+5300SEIT | -- | 42.3 | 20 | No | 2018-01-09 | B2_s1_d0 | 0.7 | 8.4 | 13.9 | 1497 | 31 | B2 | 11 | 0.02 | s1 | n | n | d0
18010002 |  | 17096 | -- | FG16OM16 1X10 MM² - 0.6/1 KV | 11 | 14 | Paron | SXLPE+1420FEES+5300SEIT | -- | 41.8 | 20.4 | No | 2018-01-09 | B2_s1_d2 | 0.7 | 11.7 | 17.3 | 843 | 45 | B2 | 17 | 0.03 | s1 | y | y | d2
18010003 |  | 17092 | -- | PRYSMIAN 255/2017-1X2500 AL-320 000V ELECTRIC CABLE -9351 | 123.6 | 2 | Paron | XLPE+TUBEAL+60ACESNOIR+SKINSC | -- | 42.1 | 22.1 | No | 2018-01-09 | B2_s1_d0 | 0.7 | 7.1 | 11.6 | 810 | 28 | B2 | 10 | 0.02 | s1 | n | n | d0
18010004 |  | 17096 | -- | FG16OM16 5G10 MM² - 0.6/1 KV | 20.8 | 7 | Paron | SXLPE+1420FEES+5300SEIT | -- | 39 | 23 | No | 2018-01-11 | B2_s1_d2 | 0.6 | 6 | 8.3 | 1494 | 24 | B2 | 5 | 0.01 | s1 | y | y | d2
18010005 |  | 17096 | -- | FG16OM16 3G1.5 MM² - 0.6/1 KV | 11 | 14 | Paron | SXLPE+1420FEES+5300SEIT | -- | 38.8 | 22.7 | No | 2018-01-11 | C_s1_d2 | 1 | 16.3 | 22.7 | 984 | 51 | C | 34 | 0.09 | s1 | y | y | d2
18010006 |  | 17096 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 14 | 11 | Paron | SXLPE+1420FEES+5300SEIT | -- | 42.4 | 23.2 | No | 2018-01-11 | C_s1_d2 | 1 | 15.9 | 21.8 | 1041 | 39 | C | 25 | 0.05 | s1 | y | y | d2
18010007 |  | 17066 | -- | DRAKA 2017 1 F.O. 10D-7A2 INT MOVISTAR (DRY INDOOR DROP Ø 4.2MM ) | 4.2 | 75 | Paron | 1700SEES | -- | 35.1 | 22 | No | 2018-01-12 | D_s1_d2 | 3.3 | 55.4 | 96.4 | 972 | 180 | D | 38 | 0.05 | s1 | y | y | d2
18010008 |  | 17109 | -- | DRAKA 128 FO G657 A2 / (VTEST) | 19 | 8 | Paron | 1700SEES | -- | 41.2 | 22.9 | No | 2018-01-16 | B2_s1_d0 | 0.54 | 7.9 | 14.6 | 1005 | 27 | B2 | 15 | 0.04 | s1 | n | n | d0
18010009 |  | 17109 | -- | DRY LT 8X4 VTEST | 19.9 | 8 | Paron | 1700SEES | -- | 42.3 | 23.1 | No | 2018-01-16 | B2_s1_d2 | 0.8 | 12.1 | 16.8 | 1050 | 33 | B2 | 28 | 0.05 | s1 | y | y | d2
18010011 |  | 17109 | -- | DRY LT 8X4 KTEST | 19.7 | 8 | Paron | 1700SEES | -- | 38.8 | 23.2 | No | 2018-01-16 | B2_s1_d2 | 0.75 | 11.4 | 17.6 | 1053 | 30 | B2 | 23 | 0.05 | s1 | y | y | d2
18010012 |  | 17110 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 28 | 6 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 42.3 | 23.2 | No | 2018-01-18 | B2_s1_d0 | 0.5 | 5.4 | 6.7 | 993 | 25 | B2 | 4 | 0.01 | s1 | n | n | d0
18010013 |  | 17110 | -- | FG16OM16 1X10 MM² - 0.6/1 KV | 10.6 | 14 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 43 | 23 | No | 2018-01-18 | B2_s1_d0 | 0.7 | 8.5 | 11.3 | 561 | 48 | B2 | 20 | 0.03 | s1 | n | n | d0
18010014 |  | 17110 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 14 | 11 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 47.5 | 22.6 | No | 2018-01-18 | B2_s1_d1 | 0.9 | 14.9 | 22 | 1353 | 42 | B2 | 25 | 0.04 | s1 | y | n | d1
18010015 |  | 17110 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.6 | 11 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 47.8 | 22.9 | No | 2018-01-18 | B2_s1_d1 | 0.7 | 10.5 | 15.9 | 1173 | 42 | B2 | 14 | 0.03 | s1 | y | n | d1
TN_2018_840 |  | OP66209 20226646 | 414686W | AFUMEX CLASS 1KV Z1Z1-K (AS) 7X2.5MM2 | 13.52 | 11 | Vilanova | INSULATION1602SEES+SHEATH1602SEES | OD | 49.1 | 12 | No | 2018-01-10 | B2_s1_d0 | 0.62 | 11.9 | 14.4 | 960 | 41.8 | B2 | 13.6 | 0.02 | s1 | n | n | d0
TN_2018_841 |  | OP66210 20226668 | 414672F | AFUMEX CLASS 1KV Z1Z1-K (AS) 12X1.5MM2 | 15.06 | 10 | Vilanova | INSULATION1602SEES+SHEATH1602SEES | OD | 49.7 | 9.7 | No | 2018-01-10 | B2_s1_d0 | 0.58 | 11.6 | 14.2 | 1239 | 32.1 | B2 | 15.5 | 0.02 | s1 | n | n | d0
TN_2018_842 |  |  | 397570S | AL-HEPRZ1(AS) 1X240MM2 18/30KV | 46.6 | 4 | Vilanova | HEPR+1420FEES+6000SEES | OD | 49.4 | 12.5 | No | 2018-01-10 | C_s1_d2 | 1.52 | 24.7 | 36.7 | 1488 | 41.6 | C | 1.5 | 0 | s1 | n | y | d2
TN_2018_843 |  | OP65643 20232332 | 402676S | AL AFUMEX RZ1F3Z1 3KV 3X25 | 31.92 | 6 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 32 | 18.6 | No | 2018-01-10 | B2_s1_d2 | 0.7 | 7.9 | 10.4 | 1278 | 31 | B2 | 2.1 | 0.01 | s1 | n | y | d2
TN_2018_844 |  | OP65644 20232331 | 401833A | AL AFUMEX RZ1F3Z1 3KV 2X150 | 46.71 | 4 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 42.5 | 12.7 | No | 2018-01-11 | B2_s1_d0 | 0.33 | 6 | 8.6 | 681 | 27.6 | B2 | 0.5 | 0 | s1 | n | n | d0
TN_2018_845 |  | OP65524 20231715 | 402673N | AL AFUMEX RZ1FA3Z1-K 1KV ADIF 1X240 | 32.51 | 6 | Vilanova | LLDPE+6000SEES | OD | 41.7 | 12.1 | No | 2018-01-11 | C_s1_d2 | 0.93 | 15.1 | 34.2 | 1497 | 28.6 | C | 6.4 | 0.01 | s1 | n | y | d2
TN_2018_846 |  | OP65525 20231716 | 402679V | AL AFUMEX RZ1FA3Z1-K 1KV ADIF 2X16 | 20.4 | 7 | Vilanova | LLDPE+6000SEES | OD | 41.6 | 12.9 | No | 2018-01-11 | D_s1_d2 | 1.67 | 34.8 | 105.2 | 1500 | 87.7 | D | 43.3 | 0.17 | s1 | n | y | d2
TN_2018_847 |  | OP65526 20231713 | 406882N | AL AFUMEX RZ1FA3Z1-K 1KV ADIF 1X240 | 31.85 | 6 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 35.2 | 16.2 | No | 2018-01-11 | B2_s1_d0 | 0.59 | 7.5 | 9.9 | 927 | 26 | B2 | 1.5 | 0.01 | s1 | n | n | d0
TN_2018_848 |  | OP65527 20231714 | 402656V | AL AFUMEX RZ1FA3Z1-K 1KV ADIF 2X16 | 20.82 | 7 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 27.5 | 16 | No | 2018-01-11 | B2_s1_d2 | 0.9 | 11.5 | 18.8 | 1275 | 25.5 | B2 | 20.8 | 0.06 | s1 | n | y | d2
TN_2018_849 |  |  | 471055 | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 75.86 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS+SKINSC | OD | 55.5 | 9.5 | No | 2018-01-12 | D_s1_d2 | 1.9 | 37.2 | 66.7 | 1500 | 59.7 | D | 6.7 | 0.01 | s1 | n | y | d2
TN_2018_850 |  | OP65706 20232524 | 417024M | AFUMEX RZ1FA3Z1-K 1KV ADIF 3X1.5 | 13.78 | 11 | Vilanova | LLDPE+6000SEES | OD | 45 | 16.8 | No | 2018-01-12 | D_s1_d2 | 3 | 53.8 | 96 | 1326 | 93.6 | D | 36.5 | 0.06 | s1 | n | y | d2
TN_2018_851 |  |  | 471056 | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 75.76 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS+SKINSC | OD | 34.2 | 18.7 | No | 2018-01-12 | D_s1_d2 | 2.1 | 45 | 91.9 | 1500 | 78.9 | D | 11.7 | 0.04 | s1 | n | y | d2
TN_2018_852 |  | OP 65009 | Box | AFUMEX CLASS 750V HO7Z1-R (AS) TYPE2 1X16 | 6.77 | 21 | Vilanova | 1602SEES | OD | 57 | 12.3 | No | 2018-01-15 | B2_s1_d1 | 0.25 | 2.3 | 4.9 | 549 | 18 | B2 | 0.1 | 0.01 | s1 | y | n | d1
TN_2018_853 |  | OP 65008 | Box | AFUMEX CLASS 750V HO7Z1-R (AS) TYPE2 1X10 | 6 | 25 | Vilanova | 1602SEES | OD | 26.4 | 14.5 | No | 2018-01-15 | B2_s1_d0 | 0.37 | 2.9 | 7.8 | 510 | 42.3 | B2 | 0.3 | 0 | s1 | n | n | d0
TN_2018_854 |  | OP 65007 | Box | AFUMEX CLASS 750V HO7Z1-R (AS) TYPE2 1X2.5 | 3.66 | 105 | Vilanova | 1602SEES | OD | 47 | 15.3 | No | 2018-01-15 | B2_s1_d0 | 0.71 | 7.1 | 15.2 | 467 | 70.5 | B2 | 9.5 | 0.02 | s1 | n | n | d0
TN_2018_855 |  | OP64582 20184156 | 391258F | XHIOZ1 1X500 15KV | 50.34 | 4 | Vilanova | XLPE+1420FEES+6000SEES | OD | 48.1 | 14.1 | No | 2018-01-16 | B2_s1_d2 | 0.8 | 13.7 | 16.1 | 1071 | 42.7 | B2 | 12.3 | 0.04 | s1 | n | y | d2
TN_2018_856 |  | OP65205 20229629 | 395169G | AFUMEX CLASS 1KV Z1Z1-K (AS) 19X1.5MM2 | 18.91 | 8 | Vilanova | INS:=1602SEES+TALCUM+SHEATH1602SEES | OD | 44.8 | 16.6 | No | 2018-01-16 | B2_s1_d0 | 0.7 | 9.2 | 12.9 | 1491 | 25.4 | B2 | 14.9 | 0.03 | s1 | n | n | d0
TN_2018_857 |  | OP65206 20226648 | 398667J | AFUMEX CLASS 1KV Z1Z1-K (AS) 19X2.5MM2 | 20.94 | 7 | Vilanova | INS:=1602SEES+TALCUM+SHEATH1602SEES | OD | 37.5 | 20.5 | No | 2018-01-16 | B2_s1_d1 | 0.73 | 10.4 | 12.7 | 780 | 35.6 | B2 | 10.2 | 0.02 | s1 | y | n | d1
TN_2018_858 |  | OP65203 20229628 | 395177R | AFUMEX CLASS 1KV Z1Z1-K (AS) 16X1.5MM2 | 18.08 | 8 | Vilanova | INS:=1602SEES+TALCUM+SHEATH1602SEES | OD | 42.3 | 18.8 | No | 2018-01-16 | B2_s1_d0 | 0.76 | 12.9 | 17.4 | 1404 | 31.9 | B2 | 15.9 | 0.05 | s1 | n | n | d0
TN_2018_859 |  | OP65409 20150403 | 419058Y | EATST 19X1X1.4 | 21.4 | 7 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 51.6 | 13 | No | 2018-01-18 | B2_s1_d0 | 0.72 | 8.3 | 18.8 | 1500 | 30.8 | B2 | 6.3 | 0.03 | s1 | n | n | d0
TN_2018_860 |  | OP65409 20150403 | 420230X | EATST 19X1X1.4 | 20.73 | 7 | Vilanova | 1602SEES+1602SEES | OD | 36.1 | 20.4 | No | 2018-01-18 | B2_s1_d2 | 0.87 | 14.1 | 26.2 | 1500 | 39.2 | B2 | 13.2 | 0.05 | s1 | n | y | d2
TN_2018_861 |  | OP65705 20232527 | 416073D | AFUMEX RZ1FA3Z1-K 1KV ADIF 1X300 | 33.6 | 5 | Vilanova | PENDINGTOCONFIRM | OD | 41.3 | 16.7 | No | 2018-01-18 | B2_s1_d1 | 0.48 | 6.2 | 9 | 1494 | 28 | B2 | 3.3 | 0.02 | s1 | y | n | d1
TN_2018_862 |  | OP65711 20232525 | 415035A | AFUMEX RZ1FA3Z1-K 1KV ADIF 1X300 | 34.57 | 5 | Vilanova | PENDINGTOCONFIRM | OD | 55.8 | 12.4 | No | 2018-01-19 | B2_s1_d0 | 0.49 | 6.5 | 8.7 | 990 | 22.4 | B2 | 1.8 | 0 | s1 | n | n | d0
TN_2018_863 |  | OP65709 20232526 | 402674P | AFUMEX RZ1FA3Z1-K 1KV ADIF 3X1.5 | 13.57 | 11 | Vilanova | PENDINGTOCONFIRM | OD | 54.3 | 13.8 | No | 2018-01-19 | B2_s1_d0 | 0.65 | 11.8 | 18.1 | 984 | 37.7 | B2 | 15.4 | 0.04 | s1 | n | n | d0
TN_2018_864 |  |  | 416736Z | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 77.28 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS+SKINSC | OD | 43.8 | 18.8 | No | 2018-01-19 | D_s1_d2 | 0.84 | 38.9 | 62 | 1401 | 62.9 | D | 18.7 | 0.03 | s1 | n | y | d2
TN_2018_865 |  |  | TH G93953 | FG18OM16 AFUMEX GOLD 1KV 5X1.5 | 16.24 | 9 | Vilanova | ID2900IT+SCAPA+0400FEIT+5300SEIT | CD | 53.2 | 16.9 | No | 2018-01-22 | B2_s1_d1 | 0.85 | 13 | 28.5 | 1074 | 36.8 | B2 | 18.7 | 0.05 | s1 | y | n | d1
TN_2018_866 |  |  | TH H74881 | FG18OM16 AFUMEX GOLD 1KV 5X1.5 | 15.86 | 9 | Vilanova | SD3500IT+0400FEIT+5300SEIT | CD | 48.8 | 18.5 | No | 2018-01-22 | B2_s1_d1 | 0.7 | 13.2 | 19.4 | 1470 | 28.7 | B2 | 6.9 | 0.02 | s1 | y | n | d1
TN_2018_867 |  | OP65352 20230351 | 417304S | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 5X120 | 62.32 | 3 | Vilanova | IRN267+INNERSHEATHGRI141MUDRESISTANT+OUTERSHEATHGFR380 | OD | 32.5 | 23.3 | No | 2018-01-22 | B2_s1_d0 | 0.64 | 4.7 | 6.4 | 633 | 23.4 | B2 | 6.2 | 0.01 | s1 | n | n | d0
TN_2018_868 |  | OP65194 20229611 | 418407R | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 1X500 | 48.38 | 4 | Vilanova | IRN267+INNERSHEATHGRI141MUDRESISTANT+OUTERSHEATHGFR380 | OD | 65.7 | 12.9 | No | 2018-01-23 | B2_s1_d1 | 0.62 | 5.9 | 8.5 | 708 | 28.5 | B2 | 16.7 | 0.02 | s1 | y | n | d1
TN_2018_869 |  |  | H11629 | AFUMEX CLASS RZ1-K (AS) 1KV 5G2.5 | 13.8 | 11 | Vilanova | 16AA+FEIT | OD | 66.7 | 12.6 | No | 2018-01-23 | D_s1_d1 | 2.02 | 28.4 | 53.2 | 1407 | 49.2 | D | 22.3 | 0.05 | s1 | y | n | d1
TN_2018_870 |  |  | 416736Z | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.82 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS+SKINSC | OD | 63.2 | 14.5 | No | 2018-01-23 | D_s1_d2 | 0.83 | 30.7 | 44.1 | 1362 | 54.5 | D | 2.3 | 0.01 | s1 | n | y | d2
TN_2018_871 |  | OP65197 20229614 | 420273U | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 19X1.5 | 22.93 | 7 | Vilanova | IRN267+INNERSHEATHGRI141MUDRESISTANT+OUTERSHEATHGFR380 | CD | 53.2 | 18.6 | No | 2018-01-23 | B2_s1_d1 | 0.42 | 7.3 | 17.1 | 687 | 44.3 | B2 | 22.2 | 0.06 | s1 | y | n | d1
TN_2018_872 |  |  | Roll | IRISTECH U-1000 RZV-V 3G1.5-NP USE 26S | 8.71 | 17 | Vilanova | SXLPE+1100FPFR+1900SPFR+1000GPFR | CD | 71.5 | 14.1 | No | 2018-01-25 | E ou F_s2_d2 | 3.3 | 64.7 | 328 | 429 | 1810.3 | E ou F | 305 | 1.39 | s2 | n | y | d2
TN_2018_873 |  |  | 389637U | AFUMEX CLASS RZ1-K (AS) 1KV 4G35 | 27.11 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 70.8 | 14.9 | No | 2018-01-25 | B2_s1_d2 | 0.8 | 9.1 | 16.6 | 1497 | 19.3 | B2 | 13.4 | 0.03 | s1 | n | y | d2
TN_2018_874 |  |  | 358976S | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.32 | 15 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 78.5 | 11.1 | No | 2018-01-26 | C_s1_d2 | 1.26 | 22.3 | 29.7 | 933 | 59.9 | C | 41.9 | 0.1 | s1 | n | y | d2
TN_2018_875 |  |  | TH H75334 | FG18OM16 AFUMEX GOLD 1KV 5X1.5 | 15.42 | 10 | Vilanova | ID2900IT+0400FEIT+5300SEIT | CD | 73.2 | 11.4 | No | 2018-01-26 | B2_s1_d2 | 0.76 | 9.9 | 15.9 | 1164 | 29.4 | B2 | 9.1 | 0.01 | s1 | n | y | d2
TN_2018_876 |  |  | 416745J | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.3 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS+SKINSC | CD | 72.3 | 11.1 | No | 2018-01-26 | C_s1_d2 | 0.87 | 22.4 | 34.6 | 1236 | 38.6 | C | 14.2 | 0.02 | s1 | n | y | d2
18010016 |  | 17110 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.6 | 11 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 45.4 | 22.5 | No | 2018-01-29 | B2_s1_d2 | 0.8 | 12.5 | 20.6 | 1254 | 36 | B2 | 21 | 0.04 | s1 | y | y | d2
18010017 |  | 17110 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 14 | 11 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 45.7 | 22.3 | No | 2018-01-29 | C_s1_d2 | 0.9 | 15.3 | 20.6 | 1407 | 44 | C | 28 | 0.06 | s1 | y | y | d2
TN_2018_877 |  |  | TH H75330 | FG18OM16 AFUMEX GOLD 1KV 5X1.5 | 15.53 | 10 | Vilanova | SD3500IT+SCAPA+0400FEIT+5300SEIT | CD | 60.9 | 12.5 | No | 2018-01-29 | B2_s1_d1 | 0.46 | 8.3 | 11.2 | 1386 | 35.1 | B2 | 1.1 | 0 | s1 | y | n | d1
TN_2018_878 |  |  | TA D34813 | PRYSMIAN(P) 20214075-804/273 (6+1)X0.93MM² -EFSAT CPR-2017 | 9.56 | 16 | Vilanova | ID2900IT+5100SVIT | CD | 55 | 15.1 | No | 2018-01-29 | D_s2_d2 | 3.3 | 68.2 | 229.1 | 1098 | 287.9 | D | 127.1 | 0.45 | s2 | y | y | d2
TN_2018_879 |  |  | H11629 | AFUMEX CLASS RZ1-K (AS) 1KV 5G2.5 | 13.8 | 11 | Vilanova | 16AA+FEIT | CD | 49.5 | 17.2 | No | 2018-01-29 | C_s1_d2 | 1.69 | 26.2 | 39.1 | 1296 | 60.1 | C | 30.5 | 0.08 | s1 | y | y | d2
TN_2018_880 |  |  | Roll | IRISTECH U-1000 RZV-V 3G1.5-NP USE 26S | 8.89 | 17 | Vilanova | SXLPE+1100FPFR+1900SPFR+1000GPFR | CD | 63.3 | 10.9 | No | 2018-01-30 | E ou F_s3_d2 | 3.3 | 68.7 | 308.8 | 483 | 1726.8 | E ou F | 315.1 | 1.51 | s3 | y | y | d2
TN_2018_881 |  |  | Roll | FG16OR16 3G1.5 MM² - 0.6/1 KV ( GENERAL CAVI) | 11.4 | 13 | Vilanova | COMPETITORSAMPLE | CD | 61.9 | 12.9 | No | 2018-01-30 | B2_s2_d1 | 0.74 | 11.3 | 17.9 | 774 | 55.4 | B2 | 96.4 | 0.09 | s2 | y | n | d1
TN_2018_882 |  | 17105 | CV2202 | IRISTECH U-1000 RZV-V 3G1.5-NP USE 26S | 9.06 | 16 | Vilanova | SXLPE+0500FPIT+2000SPIT | CD | 40 | 22.5 | No | 2018-01-30 | B2_s2_d1 | 0.72 | 10.8 | 20.8 | 561 | 94.4 | B2 | 92.4 | 0.32 | s2 | y | n | d1
18020001 |  | 17127 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.9 | 6 | Paron | SXLPE+1400FEIT+5300SEIT | -- | 31.7 | 22 | No | 2018-02-01 | C_s1_d2 | 0.9 | 11.8 | 45.5 | 1500 | 38 | C | 6 | 0.02 | s1 | y | y | d2
18020002 |  | 17127 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 14.3 | 11 | Paron | SXLPE+1400FEIT+5300SEIT | -- | 32.7 | 22.2 | No | 2018-02-01 | C_s1_d2 | 1.1 | 19.4 | 37 | 1170 | 49 | C | 42 | 0.09 | s1 | y | y | d2
18020003 |  | 17127 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 14.3 | 11 | Paron | SXLPE+1400FEIT+5300SEIT | -- | 32.8 | 22 | No | 2018-02-01 | D_s2_d2 | 1.4 | 31.6 | 77.1 | 1070 | 99 | D | 56 | 0.11 | s2 | y | y | d2
TN_2018_883 |  | 17105 | CV2179 | IRISTECH U-1000 RZV-V 3G1.5-NP USE 26S | 8.91 | 17 | Vilanova | SXLPE+1100FPFR+2000SPIT | CD | 67.3 | 11.5 | No | 2018-02-01 | C_s2_d2 | 1.43 | 15.9 | 35.7 | 528 | 162.1 | C | 253.2 | 0.64 | s2 | n | y | d2
TN_2018_884 |  | 17105 | CV2144 | IRISTECH U-1000 RZV-V 3G1.5-NP USE 26S | 9.02 | 17 | Vilanova | SXLPE+0500FPIT+2000SPIT | CD | 66.3 | 12.1 | No | 2018-02-01 | B2_s2_d1 | 0.57 | 7.7 | 16.1 | 579 | 74.5 | B2 | 73 | 0.3 | s2 | y | n | d1
TN_2018_885 |  | 17105 | CV2050 | IRISTECH U-1000 RZV-V 3G1.5-NP USE 26S | 8.85 | 17 | Vilanova | SXLPE+1100FPFR+2000SPIT | CD | 62.9 | 13.4 | No | 2018-02-01 | C_s2_d2 | 0.95 | 16.7 | 31.6 | 498 | 160 | C | 167.3 | 0.58 | s2 | n | y | d2
18020004 |  | 17127 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 14 | 11 | Paron | SXLPE+1420FEES+5300SEIT | -- | 35.9 | 21.8 | No | 2018-02-01 | C_s1_d2 | 1 | 16.3 | 21.7 | 1275 | 35 | C | 21 | 0.03 | s1 | y | y | d2
18020005 |  | 17127 | -- | FG16OM16 3G1.5 MM² - 0.6/1 KV | 11.48 | 14 | Paron | SXLPE+1420FEES+5300SEIT | -- | 35.4 | 22 | No | 2018-02-01 | B2_s1_d2 | 0.7 | 11.3 | 13.9 | 1230 | 44 | B2 | 23 | 0.04 | s1 | y | y | d2
18020006 |  | 17134 | -- | ORANGE DRAKA SR 25/01/2018 L1120 M12 24 FO G6557A2 OHC FRC | 6.3 | 25 | Paron | 1700SEES | -- | 29.4 | 18 | No | 2018-02-05 | D_s1_d1 | 3.3 | 23 | 68 | 543 | 292 | D | 28 | 0.06 | s1 | y | n | d1
18020007 |  | 17134 | -- | ORANGE DRAKA SR 25/01/2018 L1120 M4 72 FO G6557A2 OHC FRC | 9.2 | 17 | Paron | 1700SEES | -- | 29 | 19 | No | 2018-02-05 | D_s2_d2 | 3.3 | 58.3 | 122.3 | 858 | 244 | D | 56 | 0.014 | s2 | y | y | d2
18020008 |  | 17127 | -- | FG16OM16 5G10 MM² - 0.6/1 KV | 20.8 | 7 | Paron | SXLPE+1420FEES+5300SEIT | -- | 33.9 | 20.5 | No | 2018-02-06 | B2_s1_d0 | 0.6 | 4 | 6.3 | 1500 | 17 | B2 | 17 | 0.01 | s1 | n | n | d0
18020009 |  | 17127 | -- | FG16OM16 5G10 MM² - 0.6/1 KV | 20.2 | 8 | Paron | SXLPE+1400FEIT+5300SEIT | -- | 33.6 | 20.4 | No | 2018-02-06 | B2_s1_d0 | 0.35 | 3.3 | 4.5 | 567 | 17 | B2 | 4 | 0.01 | s1 | n | n | d0
TN_2018_886 |  | OP65643 20232332 | 402676S | AL AFUMEX RZ1F3Z1 3KV 3X25 | 31.92 | 6 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 84.1 | 10 | No | 2018-02-05 | B2_s1_d2 | 0.88 | 9.6 | 13.1 | 1500 | 34.3 | B2 | 2 | 0.01 | s1 | n | y | d2
TN_2018_887 |  | OP65527 20231714 | 402656V | AL AFUMEX RZ1FA3Z1-K 1KV ADIF 2X16 | 20.82 | 7 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 78 | 10.2 | No | 2018-02-06 | B2_s1_d2 | 0.73 | 8.4 | 14 | 1473 | 21 | B2 | 2 | 0.02 | s1 | n | y | d2
TN_2018_889 |  | OP65197 20229614 | 420273U | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 19X1.5 | 22.93 | 7 | Vilanova | IRN267+INNERSHEATHGRI141MUDRESISTANT+OUTERSHEATHGFR380 | OD | 58.8 | 7.3 | No | 2018-02-07 | B2_s1_d1 | 0.37 | 5.9 | 9.2 | 1329 | 27.3 | B2 | 5.1 | 0.02 | s1 | y | n | d1
TN_2018_890 |  | OP65194 20229611 | 418407R | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 1X500 | 48.38 | 4 | Vilanova | IRN267+INNERSHEATHGRI141MUDRESISTANT+OUTERSHEATHGFR380 | OD | 52.9 | 10.4 | No | 2018-02-07 | B2_s1_d1 | 0.5 | 6.4 | 8.9 | 624 | 30.4 | B2 | 0.3 | 0 | s1 | y | n | d1
TN_2018_891 |  | OP65352 20230351 | 417304S | AFUMEX CLASS ATEX RZ1MZ1-K(AS) 1KV 5X120 | 62.32 | 3 | Vilanova | IRN267+INNERSHEATHGRI141MUDRESISTANT+OUTERSHEATHGFR380 | OD | 34.3 | 16.1 | No | 2018-02-07 | B2_s1_d0 | 0.65 | 4.4 | 7.8 | 705 | 20.5 | B2 | 14.1 | 0.01 | s1 | n | n | d0
TN_2018_893 |  |  | H11629 | AFUMEX CLASS RZ1-K (AS) 1KV 5G2.5 | 13.8 | 11 | Vilanova | SXLPE+FEIT+16AA | CD | 56.7 | 4.8 | No | 2018-02-08 | B2_s1_d1 | 0.58 | 12.3 | 18.9 | 1059 | 30.1 | B2 | 0.8 | 0 | s1 | y | n | d1
TN_2018_894 |  |  | H11629 | AFUMEX CLASS RZ1-K (AS) 1KV 5G2.5 | 13.8 | 11 | Vilanova | SXLPE+FEIT+16AA | CD | 43.7 | 9.8 | No | 2018-02-08 | C_s1_d2 | 1.64 | 24.7 | 37.9 | 1383 | 46.3 | C | 16.8 | 0.04 | s1 | n | y | d2
TN_2018_895 |  | OP66296 20235312 | 408683W | MRZ1F3Z1-K (AS+) 1KV 2X35 | 27.86 | 6 | Vilanova | CUC5+MICA+SXLPE+1602SEES+STEELSNCORRUGATED+LANTORTAPE+1602SEES | OD | 52 | 13 | No | 2018-02-08 | B2_s1_d2 | 0.4 | 7.6 | 9.6 | 1128 | 32.4 | B2 | 2.2 | 0.01 | s1 | n | y | d2
TN_2018_896 |  | OP66297 20235313 | 406885S | MRZ1F3Z1-K (AS+) 1KV 3X1.5 | 14.92 | 10 | Vilanova | CUC5+MICA+SXLPE+1602SEES+STEELSNCORRUGATED+LANTORTAPE+1602SEES | OD | 55.6 | 7.9 | No | 2018-02-09 | B2_s1_d2 | 0.72 | 12.8 | 17.6 | 975 | 45.1 | B2 | 4.1 | 0.02 | s1 | n | y | d2
18020010 |  | 17148 | -- | K25 5G1.50-SH-NF F 55-625-255 | 12.5 | 12 | Paron | ID3100/SV3300FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 28.2 | 22 | No | 2018-02-10 | B2_s1_d2 | 0.9 | 11.3 | 24.7 | 936 | 41 | B2 | 28 | 0.08 | s1 | y | y | d2
18020011 |  | 17148 | -- | FR-N1X1G1 3G10MM² | 17.5 | 8 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 26.7 | 21 | No | 2018-02-10 | B2_s1_d2 | 0.5 | 6.6 | 11.9 | 933 | 21 | B2 | 6 | 0.01 | s1 | y | y | d2
18020012 |  | 17151 | -- | DRAKA 2018 256 FO 10DO KT MOVISTAR | 17 | 9 | Paron | 1700SEES | -- | 31.2 | 21.7 | No | 2018-02-14 | D_s2_d1 | 2.6 | 44.7 | 64.8 | 1500 | 75 | D | 80 | 0.17 | s2 | y | n | d1
18020013 |  | 17151 | -- | DRAKA 2018 256 FO 10DO KT MOVISTAR | 17 | 9 | Paron | 16BBSEES | -- | 33.4 | 21 | No | 2018-02-14 | E ou F_s2_d2 | 3.3 | 104.1 | 180.4 | 1224 | 198 | E ou F | 305 | 0.66 | s2 | y | y | d2
18020014 |  | 17154 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 14.3 | 11 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 36.3 | 22.7 | No | 2018-02-17 | B2_s1_d1 | 0.7 | 10.1 | 16.7 | 1158 | 29 | B2 | 16 | 0.03 | s1 | y | n | d1
18020017 |  | 17154 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.5 | 6 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 36.1 | 22.2 | No | 2018-02-17 | B2_s1_d2 | 0.55 | 5.1 | 9.6 | 1494 | 16 | B2 | 4 | 0.01 | s1 | y | y | d2
18020016 |  | 17154 | -- | FG16OM16 5G10 MM² - 0.6/1 KV | 20.6 | 7 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 37.1 | 21.9 | No | 2018-02-17 | B2_s1_d0 | 0.4 | 1.6 | 3.3 | 798 | 9 | B2 | 3 | 0 | s1 | n | n | d0
18020018 |  | 17154 | -- | FG16OM16 3G10 MM² - 0.6/1 KV | 16 | 9 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 27.4 | 20.5 | No | 2018-02-19 | B2_s1_d2 | 0.7 | 5.6 | 14.6 | 1434 | 18 | B2 | 17 | 0.03 | s1 | y | y | d2
18020019 |  | 17154 | -- | FG16OM16 3G1.5 MM² - 0.6/1 KV | 10.9 | 14 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 30 | 20 | No | 2018-02-19 | B2_s1_d1 | 0.86 | 13.3 | 20.2 | 807 | 45 | B2 | 41 | 0.09 | s1 | y | n | d1
18020020 |  | 17154 | -- | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.9 | 11 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 30.9 | 22.1 | No | 2018-02-19 | B2_s1_d0 | 0.7 | 11.2 | 18.1 | 1068 | 32 | B2 | 16 | 0.03 | s1 | n | n | d0
TN_2018_897 |  |  | D-34991 | FG16OM16 5G1.5 MM² - 0.6/1 KV | 14 | 11 | Vilanova | CARTA+04AMFEIT+5300SEIT | CD | 42 | 10.4 | No | 2018-02-09 | B2_s1_d2 | 0.48 | 13.3 | 19.7 | 1035 | 43.9 | B2 | 0.2 | 0 | s1 | n | y | d2
TN_2018_898 |  | 20223260 |  | FG16OR16 4G6 MM² - 0.6/1 KV | 15.43 | 10 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 60.8 | 7.7 | No | 2018-02-13 | B2_s2_d1 | 0.72 | 11.6 | 22.4 | 942 | 51.8 | B2 | 127.3 | 0.29 | s2 | y | n | d1
TN_2018_899 |  | 20223258 |  | FG16OR16 3G6 MM² - 0.6/1 KV | 13.83 | 11 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 54.5 | 9.5 | No | 2018-02-13 | B2_s2_d0 | 0.74 | 11.3 | 21 | 783 | 69.7 | B2 | 170.2 | 0.37 | s2 | n | n | d0
TN_2018_900 |  | 20214405 | T1 H16276 | FG16OR16 5G6 MM² - 0.6/1 KV | 18.13 | 8 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 50.2 | 12 | No | 2018-02-13 | B2_s2_d2 | 0.89 | 12.7 | 18.5 | 1290 | 59 | B2 | 172.3 | 0.23 | s2 | n | y | d2
TN_2018_901 |  | 20214408 |  | FG16OR16 3G2.5 MM² - 0.6/1 KV | 11.42 | 13 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 47.7 | 12.5 | No | 2018-02-13 | B2_s2_d1 | 0.72 | 9.3 | 21.1 | 687 | 80.5 | B2 | 160.8 | 0.46 | s2 | y | n | d1
TN_2018_902 |  |  | T9 D46890 | FG16OM16 2G1.5 MM² - 0.6/1 KV | 11.9 | 13 | Vilanova | CARTA+04AMFEIT+5300SEIT | CD | 57.2 | 9.4 | No | 2018-02-14 | B2_s1_d1 | 0.46 | 9.4 | 12.1 | 579 | 52.8 | B2 | 8.8 | 0.02 | s1 | y | n | d1
TN_2018_903 |  |  | T8 G70689 | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X16 | 7.11 | 21 | Vilanova | 1602SEES | CD | 57.7 | 9.3 | No | 2018-02-14 | B2_s1_d0 | 0.23 | 6.5 | 8.2 | 564 | 44.4 | B2 | 0.5 | 0 | s1 | n | n | d0
TN_2018_904 |  | 82346537 20193689 |  | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 11.08 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 58 | 9.5 | No | 2018-02-14 | B2_s1_d0 | 0.5 | 7.9 | 14.1 | 774 | 33.5 | B2 | 7.3 | 0.01 | s1 | n | n | d0
TN_2018_905 |  | 82368425 20193690 |  | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 12.04 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 56 | 10.8 | No | 2018-02-14 | B2_s1_d2 | 0.72 | 14.6 | 20.1 | 978 | 54 | B2 | 22.5 | 0.05 | s1 | n | y | d2
TN_2018_906 |  | 82321581 20193694 |  | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11.93 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 55.2 | 11.1 | No | 2018-02-14 | B2_s1_d2 | 0.7 | 9.8 | 18 | 828 | 35.7 | B2 | 12.4 | 0.02 | s1 | n | y | d2
TN_2018_909 |  | 82067399 20163635 | 375976V | AFUMEX CLASS RZ1-K (AS) 1KV 1X10 | 9.78 | 15 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 68 | 13.2 | No | 2018-02-16 | B2_s1_d0 | 0.5 | 10.2 | 16 | 744 | 47.5 | B2 | 14.9 | 0.02 | s1 | n | n | d0
TN_2018_911 |  | 82309063 20193683 | 418962U | AFUMEX CLASS RZ1-K (AS) 1KV 5G25 | 27.12 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 65.3 | 10.2 | No | 2018-02-19 | B2_s1_d0 | 0.37 | 7.2 | 8.3 | 1425 | 34.9 | B2 | 5.4 | 0.01 | s1 | n | n | d0
TN_2018_912 |  | 82338081 20193658 | 412430U | AFUMEX CLASS RZ1-K (AS) 1KV 3G10 | 15.81 | 9 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 65.1 | 10.7 | No | 2018-02-19 | B2_s1_d0 | 0.48 | 11.6 | 18.4 | 1236 | 31.7 | B2 | 13.2 | 0.02 | s1 | n | n | d0
TN_2018_913 |  | 82191941 20193639 | 390820E | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 15.81 | 9 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 61 | 13.1 | No | 2018-02-19 | C_s1_d2 | 1.35 | 22.6 | 50 | 1314 | 49.4 | C | 2.9 | 0.02 | s1 | n | y | d2
TN_2018_914 |  | 82368440 20193681 | 422165A | AFUMEX CLASS RZ1-K (AS) 1KV 5G10 | 19.38 | 8 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 56.3 | 15.4 | No | 2018-02-19 | B2_s1_d1 | 0.6 | 11.6 | 25.8 | 1470 | 25.6 | B2 | 1.4 | 0.01 | s1 | y | n | d1
TN_2018_915 |  | 82321602 20193645 | 422568N | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 27.46 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 52.2 | 16.4 | No | 2018-02-19 | B2_s2_d0 | 0.37 | 4.6 | 6.4 | 1497 | 18.3 | B2 | 60.1 | 0.07 | s2 | n | n | d0
18020021 |  | 17151 | -- | DRAKA 2018 1FO 10D-7A2 INT MOVISTAR | 4.2 | 75 | Paron | RAVAGO6F | -- | 32.9 | 21.5 | No | 2018-02-20 | D_s1_d0 | 3.3 | 64.8 | 120.5 | 1131 | 146 | D | 45 | 0.08 | s1 | n | n | d0
18020022 |  | 17151 | -- | DRAKA 2018 1FO 10D-7A2 INT MOVISTAR | 4.2 | 75 | Paron | RAVAGO30 | -- | 32.7 | 22.4 | No | 2018-02-20 | D_s2_d0 | 3.3 | 60.4 | 117.4 | 1032 | 162 | D | 53 | 0.09 | s2 | n | n | d0
18020023 |  | 17154 | -- | FG16OM16 5G25 MM² - 0.6/1 KV | 27.5 | 6 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 27.7 | 21 | No | 2018-02-21 | C_s1_d2 | 0.8 | 10.4 | 43.7 | 1500 | 26 | C | 6 | 0.03 | s1 | y | y | d2
18020024 |  | 17154 | -- | FG16OM16 3G10 MM² - 0.6/1 KV | 16 | 9 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 26.7 | 20.6 | No | 2018-02-21 | B2_s1_d2 | 0.7 | 8.2 | 16.2 | 1479 | 26 | B2 | 8 | 0.02 | s1 | y | y | d2
18020025 |  | 17154 | -- | FG16OM16 3G1.5 MM² - 0.6/1 KV | 10.9 | 14 | Paron | SXLPE+03AAFDIT+5300SEIT | -- | 26.6 | 21.3 | No | 2018-02-21 | C_s1_d1 | 1 | 18 | 34.6 | 1020 | 49 | C | 47 | 0.12 | s1 | y | n | d1
TN_2018_916 |  | 20215085 |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 3.02 | 165 | Vilanova | 16AASEES | CD | 52.5 | 13.5 | No | 2018-02-21 | C_s2_d0 | 1.62 | 15.5 | 33.7 | 732 | 93.4 | C | 77.5 | 0.15 | s2 | n | n | d0
TN_2018_917 |  |  | T9-F89895 | FG16R16 1X50MM² - 0.6/1 KV | 15.76 | 9 | Vilanova | TALCO+05ABFPIT+2000SPIT | CD | 48.3 | 7.3 | No | 2018-02-22 | B2_s2_d1 | 0.67 | 14 | 24.3 | 882 | 48.6 | B2 | 153.6 | 0.31 | s2 | y | n | d1
TN_2018_918 |  |  | TW-H10478 | FG16OR16 24G1.5 MM² - 0.6/1 KV | 22.94 | 7 | Vilanova | TALCO+05ABFPIT+2000SPIT | CD | 47.1 | 7.4 | No | 2018-01-22 | C_s2_d1 | 1.56 | 25.1 | 44.9 | 1494 | 50.8 | C | 396.3 | 0.66 | s2 | y | n | d1
TN_2018_919 |  | 20230037 |  | FG16OM16 3G2.5 MM² - 0.6/1 KV | 12.41 | 12 | Vilanova | SXLPE+0400FEIT+5300SEIT | CD | 42.2 | 10.7 | No | 2018-02-22 | B2_s1_d0 | 0.6 | 8.9 | 13.6 | 1047 | 32.7 | B2 | 8.7 | 0.02 | s1 | n | n | d0
TN_2018_920 |  | 20224238 |  | FG16OM16 2G1.5 MM² - 0.6/1 KV | 10.75 | 14 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 42.1 | 12.2 | No | 2018-02-22 | B2_s1_d0 | 0.47 | 6.4 | 10.3 | 630 | 33.3 | B2 | 0.6 | 0 | s1 | n | n | d0
TN_2018_921 |  |  | T8-D58941 | FG16OR16 5G1.5MM² - 0.6/1 KV | 13.9 | 11 | Vilanova | TALCO+05ABFPIT+2000SPIT | CD | 41 | 13.4 | No | 2018-02-22 | C_s2_d1 | 1.15 | 14.6 | 30.5 | 834 | 68.3 | C | 256.7 | 0.49 | s2 | y | n | d1
TN_2018_925 |  | 82404240 20236484 | 414259G | AL-HEPRZ1(AS) 1X630MM2 18/30KV | 59.62 | 4 | Vilanova | HEPR+1420FEES+6000ACES | CD | 49.5 | 7.1 | No | 2018-02-27 | C_s1_d2 | 1.28 | 22.4 | 32.6 | 1173 | 38 | C | 11 | 0.02 | s1 | n | y | d2
TN_2018_926 |  | OP66070 20234256 | 430096W | AFUMEX CLASS O 1Z1C7Z1-K 1KV 37X1 | 28.7 | 6 | Vilanova | 1602+1602+COPPERTAPE+LANTORTAPE+1602 | CD | 59.8 | 7.6 | No | 2018-02-27 | B2_s1_d2 | 0.51 | 6.8 | 12.5 | 1497 | 11.7 | B2 | 16.4 | 0.04 | s1 | n | y | d2
18030001 |  | 17174 | EBT 144137 | 16X1 UG10OG10M2NM1 | 25.6 | 6 | Paron | SW3800FR | - | 33.9 | 21.9 | No | 2018-03-08 | C_s2_d2 | 1.15 | 18.7 | 41 | 1407 | 37 | C | 63 | 0.18 | s2 | y | y | d2
18030002 |  | 17172 | -- | FO DROP 1MM 38 D 01 | 3.8 | 90 | Paron | 1700SEES | -- | 36.9 | 20.8 | No | 2018-03-08 | B2_s1_d1 | 0.75 | 10.7 | 22.5 | 567 | 94 | B2 | 20 | 0.03 | s1 | y | n | d1
TN_2018_927 |  | OP66067 20234259 | 425679V | AFUMEX CLASS O 1Z1C7Z1-K 1KV 37X2.5 | 34.03 | 5 | Vilanova | 1602+1602+LANTORTAPE+1602 | CD | 45.7 | 11.4 | No | 2018-03-02 | B2_s1_d2 | 0.44 | 7.3 | 11.8 | 1296 | 24 | B2 | 1.8 | 0 | s1 | n | y | d2
TN_2018_928 |  | OP66066 20234258 | 426345U | AFUMEX CLASS O 1Z1C7Z1-K 1KV 14X1 | 19.18 | 8 | Vilanova | 1602+1602+COPPERTAPE+LANTORTAPE+1602 | CD | 41.1 | 14.5 | No | 2018-03-02 | B2_s1_d2 | 0.4 | 10 | 15.2 | 1101 | 23 | B2 | 9.2 | 0.02 | s1 | n | y | d2
TN_2018_929 |  | OP66065 20234257 | 426339M | AFUMEX CLASS O 1Z1C7Z1-K 1KV 2X16 | 19.35 | 8 | Vilanova | 1602+1602+COPPERTAPE+LANTORTAPE+1602 | CD | 37.4 | 15.5 | No | 2018-03-02 | B2_s1_d2 | 0.73 | 10.5 | 16.8 | 1293 | 19.3 | B2 | 7 | 0.03 | s1 | n | y | d2
TN_2018_930 |  | OP65697 20221259 | 429382V | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 11.4 | 14 | Vilanova | INNERSHEATH:0.48MM1602+EG001765%+1.61MMOUTERSHEATH:1602 | CD | 78.4 | 13.7 | No | 2018-03-05 | D_s1_d2 | 2.19 | 31.4 | 52.9 | 1359 | 51.6 | D | 40.9 | 0.09 | s1 | n | y | d2
TN_2018_931 |  | OP65698 20222160 | 429389C | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 10.55 | 14 | Vilanova | INNERSHEATH:0.58MM1602+EG001765%+0.98MMOUTERSHEATH:1602 | CD | 49.4 | 15.5 | No | 2018-03-06 | D_s2_d2 | 3.3 | 67.7 | 138.2 | 1431 | 123.2 | D | 59.2 | 0.24 | s2 | n | y | d2
TN_2018_932 |  | OP65699 20221258 | 429377P | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 11.62 | 14 | Vilanova | INNERSHEATH:0.46MM1602+EG001765%+1.61MMOUTERSHEATH:1602 | CD | 41 | 17.3 | No | 2018-03-06 | E ou F_s2_d2 | 3.3 | 92.6 | 213 | 1287 | 216.2 | E ou F | 81.7 | 0.26 | s2 | n | y | d2
TN_2018_933 |  | OP65700 20221257 | 429384X | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 10.34 | 14 | Vilanova | INNERSHEATH:0.60MM1602+EG001765%+0.84MMOUTERSHEATH:1602 | CD | 33 | 19.4 | No | 2018-03-06 | E ou F_s2_d2 | 3.3 | 84.8 | 243 | 1107 | 301.1 | E ou F | 77.4 | 0.24 | s2 | n | y | d2
TN_2018_934 |  |  | 343560K | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.16 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS+SKINSC | CD | 35.2 | 14.6 | No | 2018-03-07 | C_s1_d2 | 0.99 | 17.9 | 26.6 | 1497 | 39.4 | C | 7.1 | 0.02 | s1 | n | y | d2
TN_2018_935 |  | OP66297 20235313 | 433668D | MRZ1F3Z1-K (AS+) 1KV 2X35 | 27.99 | 6 | Vilanova | CUC5+MICA+XLPE+1602SEES+STEELTAPESNCORRUGATED+TAPELANTOR+SHEATH1602SEES | CD | 34.9 | 16 | No | 2018-03-07 | B2_s1_d2 | 0.38 | 6 | 7.8 | 1005 | 27.9 | B2 | 2.2 | 0.01 | s1 | n | y | d2
TN_2018_936 |  | OP65643 20232332 | 434236W | AL AFUMEX RZ1F3Z1 3KV 3X25 | 31.97 | 6 | Vilanova | ALC2K+XLPE+1602SEES+STEELTAPESNCORRUGATED+TAPELANTOR+SHEATH1602SEES | CD | 34.8 | 17.2 | No | 2018-03-07 | B2_s1_d2 | 0.67 | 8.2 | 13.6 | 1500 | 18 | B2 | 5.7 | 0.01 | s1 | n | y | d2
TN_2018_937 |  |  | 343560K | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.16 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS+SKINSC | CD | 51.7 | 11.2 | No | 2018-03-08 | B2_s1_d2 | 0.59 | 13.9 | 17.1 | 1494 | 38.8 | B2 | 10 | 0.04 | s1 | n | y | d2
TN_2018_938 |  | OP67165 20064278 | 434021M | RZ1MZ-K 1KV 2RH 3G2.5 | 15.18 | 10 | Vilanova | XLPE+6010SEES+GFR380 | CD | 59.6 | 12.5 | No | 2018-03-08 | B2_s1_d2 | 0.89 | 13.9 | 22.9 | 1053 | 34.9 | B2 | 28.3 | 0.04 | s1 | n | y | d2
EFR-18-BB000918 |  | -- | -- | PRYSMIAN 255/2017-1X2500 AL-320 000V ELECTRIC CABLE -9351 | 123.6 | 2 | Efectis | XLPE+TUBEAL+60ACESNOIR+SKINSC | -- | 50.2 | 15.62 | No | 2018-03-12 | B2_s1_d0 | 0.82 | 5.3 | 8.1 | 801 | 20.4 | B2 | 1.2 | 0.01 | s1 | n | n | d0
TN_2018_939 |  | OP67165 20064278 | 434019K | RZ1MZ1-K 1KV 2RH 3G2.5 | 15.11 | 10 | Vilanova | XLPE+6010SEES+GFR380 | CD | 73.8 | 10.4 | No | 2018-03-09 | C_s1_d2 | 0.8 | 15.8 | 26.1 | 1062 | 36.9 | C | 31.5 | 0.06 | s1 | n | y | d2
TN_2018_940 |  |  | T8-F72321 | FG16R16 1X6 MM² - 0.6/1 KV | 8.14 | 19 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 65.3 | 14.4 | No | 2018-03-09 | B2_s2_d0 | 0.73 | 5.8 | 22.5 | 576 | 84.3 | B2 | 116.6 | 0.41 | s2 | n | n | d0
TN_2018_941 |  |  | T8-D58941 | FG16OR16 5G1.5MM² - 0.6/1 KV | 13.9 | 11 | Vilanova | TALCO+05ABFPIT+2000SPIT | CD | 62.4 | 16.3 | No | 2018-03-09 | B2_s2_d1 | 0.99 | 13.4 | 26.3 | 789 | 60.2 | B2 | 214.1 | 0.49 | s2 | y | n | d1
TN_2018_942 |  |  | T9-F89895 | FG16R16 1X50MM² - 0.6/1 KV | 15.76 | 9 | Vilanova | TALCO+05ABFPIT+2000SPIT | CD | 58.5 | 18.3 | No | 2018-03-09 | B2_s2_d1 | 0.67 | 11 | 17.6 | 984 | 54.1 | B2 | 127 | 0.23 | s2 | y | n | d1
TN_2018_943 |  |  | TW-H10478 | FG16OR16 24G1.5 MM² - 0.6/1 KV | 22.94 | 7 | Vilanova | TALCO+05ABFPIT+2000SPIT | CD | 51.1 | 14.1 | No | 2018-03-12 | C_s2_d2 | 1.5 | 27.5 | 56.8 | 1236 | 61.4 | C | 393.4 | 0.7 | s2 | n | y | d2
TN_2018_944 |  |  | T9 D46890 | FG16OM16 2G1.5 MM² - 0.6/1 KV | 11.9 | 13 | Vilanova | CARTA+04AMFEIT+5300SEIT | CD | 45 | 16.7 | No | 2018-03-12 | B2_s1_d0 | 0.73 | 7.7 | 12.9 | 969 | 50 | B2 | 13 | 0.02 | s1 | n | n | d0
TN_2018_945 |  | 20214405 | T1 H16276 | FG16OR16 5G6 MM² - 0.6/1 KV | 18.13 | 8 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 39.6 | 18.4 | No | 2018-03-12 | B2_s2_d1 | 0.7 | 9.1 | 14 | 1263 | 41.7 | B2 | 115.8 | 0.19 | s2 | y | n | d1
TN_2018_946 |  |  | T8 G70689 | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X16 | 7.11 | 21 | Vilanova | 1602SEES | CD | 50.7 | 15 | No | 2018-02-13 | B2_s1_d0 | 0.44 | 1.6 | 6.3 | 582 | 22.3 | B2 | 5.1 | 0.01 | s1 | n | n | d0
TN_2018_947 |  |  |  | TOP CABLE TOXFREE ZH C RZ1-K (AS) 1KV 3G1.5 | 10.43 | 15 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | CD | 48.4 | 16.4 | No | 2018-03-13 | B2_s1_d0 | 0.7 | 7.9 | 16.7 | 828 | 32 | B2 | 2 | 0.01 | s1 | n | n | d0
TN_2018_948 |  |  |  | MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G1.5 | 10.71 | 14 | Vilanova | COMPETITORSAMPLE | CD | 62.7 | 11.7 | No | 2018-03-14 | B2_s1_d0 | 0.57 | 8 | 14.8 | 708 | 38.4 | B2 | 12.7 | 0.03 | s1 | n | n | d0
TN_2018_949 |  |  |  | TOP CABLE TOXFREE ZH C RZ1-K (AS) 1KV 3G2.5 | 11.28 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | CD | 58.6 | 16.8 | No | 2018-03-14 | B2_s1_d0 | 0.76 | 9.3 | 19.5 | 840 | 37.6 | B2 | 13.7 | 0.03 | s1 | n | n | d0
18030003 |  | 17200 | -- | 1000-3G10MM²-SH-NF F 55-625-255 | 18 | 8 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 28.2 | 20.8 | No | 2018-03-21 | B2_s1_d2 | 0.6 | 5.8 | 13.8 | 1497 | 24 | B2 | 5 | 0.01 | s1 | y | y | d2
18030004 |  | 17200 | -- | 1000-3G10MM²-SH-NF F 55-625-255 | 17.6 | 8 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 25.5 | 21.2 | No | 2018-03-21 | B2_s1_d2 | 0.5 | 5.7 | 11.3 | 1500 | 24 | B2 | 4 | 0.01 | s1 | y | y | d2
TN_2018_950 |  |  | 089117H | AENOR MIGUELEZ AFIRENAS RZ1-K (AS) 1KV 1X150 | 23.27 | 7 | Vilanova | COMPETITORSAMPLE | CD | 58 | 12.3 | No | 2018-03-16 | B2_s1_d2 | 0.35 | 5.4 | 7.9 | 1491 | 23.5 | B2 | 0.9 | 0 | s1 | n | y | d2
TN_2018_951 |  |  | A-12-08-0001 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 1X150 | 22.05 | 7 | Vilanova | COMPETITORSAMPLE | CD | 48 | 16.4 | No | 2018-03-16 | B2_s1_d0 | 0.1 | 2.6 | 5.6 | 1500 | 11.9 | B2 | 0.1 | 0 | s1 | n | n | d0
TN_2018_952 |  |  |  | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G2.5MM2 | 11.31 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | CD | 44.8 | 18.3 | No | 2018-03-16 | B2_s1_d0 | 0.4 | 10.3 | 15.8 | 891 | 30.5 | B2 | 6.2 | 0.02 | s1 | n | n | d0
TN_2018_953 |  |  | 106947B | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 1X240MM² | 21.17 | 6 | Vilanova | SXLPE+SHEATHLSOH | CD | 41.6 | 19.3 | No | 2018-03-16 | B2_s1_d1 | 0.56 | 7.6 | 16.3 | 1500 | 30.1 | B2 | 1.6 | 0.01 | s1 | y | n | d1
TN_2018_954 |  |  | 30-9-219 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 1X240 | 26.75 | 6 | Vilanova | SXLPE+SHEATHLSOH | CD | 67.2 | 7.9 | No | 2018-03-20 | B2_s1_d1 | 0.63 | 7.5 | 16.2 | 1488 | 25.9 | B2 | 35.3 | 0.04 | s1 | y | n | d1
TN_2018_955 |  | OP65526 20231713 | 406882N | AL AFUMEX RZ1FA3Z1-K 1KV ADIF 1X240 | 31.85 | 6 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 26.2 | 13.4 | No | 2018-03-21 | B2_s1_d0 | 0.49 | 7.8 | 10.6 | 1041 | 22.4 | B2 | 0.8 | 0 | s1 | n | n | d0
TN_2018_956 |  | OP65527 20231714 | 402656V | AL AFUMEX RZ1FA3Z1-K 1KV ADIF 2X16 | 20.82 | 7 | Vilanova | 1602SEES+LANTOR+1602SEES | OD | 18.7 | 17.2 | No | 2018-03-21 | B2_s1_d1 | 0.92 | 11.2 | 21.5 | 1419 | 21.4 | B2 | 25.1 | 0.07 | s1 | y | n | d1
TN_2018_957 |  | OP65711 20232525 | 415035A | AFUMEX RZ1FA3Z1-K 1KV ADIF 1X300 | 34.57 | 5 | Vilanova | PENDINGTOCONFIRM | OD | 21.1 | 14.4 | No | 2018-03-21 | B2_s1_d0 | 0.51 | 4.6 | 7.5 | 1068 | 17.9 | B2 | 2.9 | 0 | s1 | n | n | d0
TN_2018_958 |  | OP65709 20232526 | 402674P | AFUMEX RZ1FA3Z1-K 1KV ADIF 3X1.5 | 13.57 | 11 | Vilanova | PENDINGTOCONFIRM | OD | 19.4 | 15.6 | No | 2018-03-21 | B2_s1_d1 | 0.92 | 14.2 | 21.2 | 1047 | 34.8 | B2 | 17.7 | 0.03 | s1 | y | n | d1
TN_2018_959 |  | 82404240 20236484 | 414259G | AL-HEPRZ1(AS) 1X630MM2 18/30KV | 59.62 | 4 | Vilanova | HEPR+1420FEES+6000ACES | OD | 26.6 | 12.7 | No | 2018-03-22 | C_s1_d2 | 1.26 | 24.7 | 35.2 | 1410 | 44.4 | C | 8.7 | 0.02 | s1 | n | y | d2
TN_2018_960 |  |  |  | TOP CABLE HO7Z1-K 1X1.5MM2 | 2.93 | 165 | Vilanova | COMPETITORSAMPLE | CD | 28.5 | 14.3 | No | 2018-03-22 | D_s1_d1 | 2.32 | 22 | 34.5 | 693 | 99.2 | D | 37.7 | 0.06 | s1 | y | n | d1
18030006 |  | 17188 | -- | 4-1.2-NF F 55-623-PRYSMIAN 255-CE 6521 | 18 | 8 | Paron | IX1400FR+3000GVFR+5300SEIT | -- | 32.8 | 23.7 | No | 2018-03-27 | B2_s1_d0 | 0.7 | 7.8 | 13.4 | 1356 | 27 | B2 | 5 | 0.01 | s1 | n | n | d0
18030005 |  | 17201 | -- | 1X95MM2 ELECLINK | 24 | 7 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 27.2 | 22.5 | No | 2018-03-23 | B2_s1_d2 | 0.4 | 6 | 8.4 | 1497 | 20 | B2 | 4 | 0.01 | s1 | y | y | d2
18030006 |  | 17201 | -- | 1X95MM2 ELECLINK | 24 | 7 | Paron | IX1100FR+0400FEIT+5300SEIT | -- | 27.1 | 22 | No | 2018-03-23 | C_s1_d2 | 0.7 | 10.4 | 32.3 | 1500 | 27 | C | 7 | 0.04 | s1 | y | y | d2
18030010 |  | 17182 | -- | 1000-1X6MM²-SH-NF F55-625-255 | 8.3 | 19 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 36.1 | 21.1 | No | 2018-03-29 | B2_s1_d1 | 0.5 | 5.9 | 11.3 | 654 | 46 | B2 | 11 | 0.02 | s1 | y | n | d1
18030008 |  | 17201 | -- | 1X95MM2 ELECLINK | 24 | 7 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 35 | 23.3 | No | 2018-03-27 | B2_s1_d2 | 0.4 | 4.7 | 10.3 | 1500 | 19 | B2 | 5 | 0.02 | s1 | y | y | d2
18030009 |  | 17201 | -- | 1X95MM2 ELECLINK | 24 | 7 | Paron | IX1100FR+0400FEIT+5300SEIT | -- | 36.3 | 23.5 | No | 2018-03-27 | B2_s1_d2 | 0.7 | 6.6 | 23.8 | 1500 | 20 | B2 | 7 | 0.02 | s1 | y | y | d2
18030011 |  | 17210 | -- | 256 F.O KT 8X32 FILLED | 18 | 8 | Paron | 1700SEES | -- | 33.8 | 23 | No | 2018-03-29 | D_s2_d2 | 3 | 67.3 | 105.8 | 1056 | 140 | D | 238.2 | 0.59 | s2 | y | y | d2
18030012 |  | 17210 | -- | 256 F.O KT 8X32 FILLED | 17.7 | 8 | Paron | RAVAGO6F | -- | 32.3 | 22.5 | No | 2018-03-29 | D_s2_d2 | 1.8 | 36.1 | 54.9 | 1386 | 72 | D | 88.2 | 0.22 | s2 | y | y | d2
18030014 |  | 17210 | -- | 256 F.O KT 16X16 DRY | 20.6 | 7 | Paron | 1700SEES | -- | 30.1 | 22.7 | No | 2018-03-30 | D_s2_d2 | 1.75 | 36.7 | 62.5 | 1293 | 63 | D | 80.9 | 0.15 | s2 | y | y | d2
18030013 |  | 17210 | -- | 256 F.O KT 16X16(AF) FILLED | 20.6 | 7 | Paron | 1700SEES | -- | 29.2 | 22.7 | No | 2018-03-30 | B2_s1_d2 | 0.7 | 14.4 | 18.8 | 1176 | 32 | B2 | 9.4 | 0.02 | s1 | y | y | d2
18040001 |  | 17210 | -- | CÂBLE 96FO (12X8) TKEST FILLED | 22.6 | 7 | Paron | 1700SEES+1602SEES | -- | 35 | 23.3 | No | 2018-04-03 | D_s2_d2 | 1.45 | 31.5 | 47.3 | 1317 | 50.6 | D | 55.6 | 0.08 | s2 | y | y | d2
18040002 |  | 17210 | -- | 256 F.O KT 16X16(AF) DRY | 20 | 8 | Paron | 1700SEES | -- | 34.3 | 23.5 | No | 2018-04-03 | B2_s1_d0 | 0.7 | 11.4 | 14.2 | 1110 | 28.2 | B2 | 7.2 | 0.01 | s1 | n | n | d0
18040003 |  | 17210 | -- | CÂBLE 96FO (12X8) TKEST FILLED | 25.7 | 6 | Paron | 1700SEES+1602SEES | -- | 42 | 23.1 | No | 2018-04-03 | C_s1_d2 | 0.8 | 18.9 | 29.8 | 1473 | 31.6 | C | 28.7 | 0.04 | s1 | y | y | d2
18040004 |  | 17210 | -- | CÂBLE 96FO (12X8) TKEST DRY | 25 | 7 | Paron | 1700SEES+1602SEES | -- | 43.2 | 23.5 | No | 2018-04-03 | B2_s1_d2 | 0.7 | 14.8 | 19.4 | 1326 | 29 | B2 | 27 | 0.05 | s1 | y | y | d2
TN_2018_961 |  | OP67202 20226649 | 433998M | AFUMEX CLASS 1KV Z1Z1-K (AS) 24X1.5MM2 | 21.43 | 7 | Vilanova | INSULATION1602SEES+SHEATH1602SEES | CD | 37 | 10.5 | No | 2018-03-23 | B2_s1_d2 | 0.75 | 14.8 | 20.6 | 885 | 42.8 | B2 | 9.3 | 0.01 | s1 | n | y | d2
TN_2018_962 |  | OP67201 20226647 | 419075S | AFUMEX CLASS 1KV Z1Z1-K (AS) 16X2.5MM2 | 19.7 | 8 | Vilanova | INSULATION1602SEES+SHEATH1602SEES | CD | 34.2 | 12.1 | No | 2018-03-23 | B2_s1_d2 | 0.71 | 9.4 | 12.8 | 639 | 37.9 | B2 | 6.4 | 0.01 | s1 | n | y | d2
TN_2018_963 |  |  | DYD140E-18-1321 | 7X1.4MM CCTSST FRO.3 DRAKA 2018 1020242453 | 32.55 | 6 | Vilanova | BERLINSAMPLE | CD | 66.3 | 10 | No | 2018-03-26 | B2_s1_d0 | 0.65 | 9.4 | 11.4 | 690 | 31.4 | B2 | 17.8 | 0.02 | s1 | n | n | d0
TN_2018_964 |  | OP67203 20229627 | 419078V | AFUMEX CLASS 1KV Z1Z1-K (AS) 24X2.5MM2 | 23.91 | 7 | Vilanova | INSULATION1602SEES+SHEATH1602SEES | CD | 55.5 | 10.3 | No | 2018-03-26 | C_s1_d2 | 0.73 | 15.2 | 19.8 | 795 | 48.6 | C | 27.9 | 0.03 | s1 | n | y | d2
TN_2018_965 |  |  | 424602Z | AFUMEX CLASS RZ1-K (AS) 1KV 4G2.5 | 13.02 | 12 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 60.3 | 13.2 | No | 2018-03-26 | C_s1_d2 | 1.52 | 21.8 | 29.2 | 912 | 50.4 | C | 10.1 | 0.03 | s1 | n | y | d2
TN_2018_966 |  | OP67002 20226650 | 434007X | AFUMEX CLASS 1KV Z1Z1-K (AS) 14X1.5MM2 | 16.38 | 9 | Vilanova | INSULATION1602SEES+SHEATH1602SEES | CD | 57.5 | 15.5 | No | 2018-03-26 | B2_s1_d2 | 0.52 | 9.3 | 11.3 | 999 | 43.3 | B2 | 0 | 0 | s1 | n | y | d2
TN_2018_967 |  | OP66640 | 420273U | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 13.43 | 12 | Vilanova | SXLPE+1602SEES | CD | 51.4 | 17.5 | No | 2018-03-26 | D_s1_d2 | 3 | 35.6 | 54.8 | 1134 | 77.5 | D | 41.3 | 0.09 | s1 | n | y | d2
TN_2018_968 |  | OP66640 | 419069K | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 13.72 | 11 | Vilanova | SXLPE+1602SEES | CD | 47.8 | 14.6 | No | 2018-03-27 | D_s1_d2 | 3 | 32.3 | 55.8 | 1083 | 71.4 | D | 43.7 | 0.1 | s1 | n | y | d2
TN_2018_969 |  |  |  | ASCABLE-RECAEL RZ1-K (AS) 1KV 3G2.5 | 11.82 | 13 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | CD | 56.1 | 17 | No | 2018-03-28 | D_s2_d2 | 3.3 | 67.3 | 123.7 | 1374 | 123.8 | D | 85.6 | 0.21 | s2 | n | y | d2
TN_2018_970 |  |  |  | MIGUELEX AFIRENAS L H07Z1-K (AS) TYPE2 1X1.5 0.75 KV 70ºC | 2.91 | 165 | Vilanova | COMPETITORSAMPLE | CD | 69.7 | 13.7 | No | 2018-04-03 | C_s1_d0 | 1.78 | 18.5 | 30.9 | 828 | 64.9 | C | 32.4 | 0.06 | s1 | n | n | d0
TN_2018_971 |  |  | T8-F72321 | FG16R16 1X6 MM² - 0.6/1 KV | 8.14 | 19 | Vilanova | TALCO+0500FPIT+2000SPIT | CD | 65.6 | 16.1 | No | 2018-04-03 | B2_s2_d0 | 0.77 | 8.2 | 21.7 | 573 | 81.3 | B2 | 116.6 | 0.39 | s2 | n | n | d0
TN_2018_972 |  | OP66640 | 419144S | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 13.36 | 12 | Vilanova | SXLPE+1602SEES | CD | 63.5 | 17.1 | No | 2018-04-03 | D_s2_d2 | 3.3 | 41.7 | 74.6 | 1464 | 76.7 | D | 50.1 | 0.13 | s2 | n | y | d2
18040005 |  | 17210 | -- | CÂBLE 96FO (12X8) TKEST DRY | 24.6 | 7 | Paron | 1700SEES+1602SEES | -- | 38.1 | 24.1 | No | 2018-04-05 | B2_s1_d2 | 0.7 | 14.8 | 21.9 | 1410 | 25 | B2 | 28 | 0.06 | s1 | y | y | d2
18040006 |  | 17210 | -- | 128 F.O KTEST 16X8 DRY GAINE | 25 | 7 | Paron | 1700SEES+1602SEES | -- | 31.9 | 23 | No | 2018-04-05 | C_s1_d2 | 0.85 | 16.3 | 23.7 | 1473 | 28 | C | 40 | 0.07 | s1 | y | y | d2
18040007 |  | 17210 | -- | 32 F.O KTEST 4X8 DRY GAINE | 19.6 | 8 | Paron | 1700SEES+1602SEES | -- | 32.3 | 22.7 | No | 2018-04-05 | B2_s1_d2 | 0.75 | 13.2 | 16.8 | 1248 | 29 | B2 | 19 | 0.05 | s1 | y | y | d2
18040008 |  | 17210 | -- | 512 F.O KT 16X32 FILLED | 22.3 | 7 | Paron | 1700SEES | -- | 40.3 | 25 | No | 2018-04-09 | E ou F_s3_d2 | 3.3 | 119.8 | 256.5 | 1368 | 241 | E ou F | 648 | 1.34 | s3 | y | y | d2
18040009 |  | 17210 | -- | 16 F.O KT 4X4 FILLED | 13 | 12 | Paron | 1700SEES | -- | 45.4 | 23.2 | No | 2018-04-09 | E ou F_s2_d2 | 3.3 | 111.7 | 231.9 | 1305 | 234 | E ou F | 137 | 0.41 | s2 | y | y | d2
18040010 |  | 17210 | -- | 16 F.O KT 4X4 FILLED | 13.2 | 12 | Paron | RAVASAFE6F | -- | 44.9 | 24.5 | No | 2018-04-09 | E ou F_s2_d2 | 3.3 | 95.7 | 215.3 | 1455 | 191 | E ou F | 185 | 0.76 | s2 | y | y | d2
18040011 |  | 17188 | -- | 4-1.2-NF F 55-623-PRYSMIAN 255-CE 6521 | 18 | 8 | Paron | IX1400FR+3000GVFR+5300SEIT | -- | 47.5 | 21.9 | No | 2018-04-10 | B2_s1_d0 | 0.6 | 9.1 | 14.1 | 1209 | 35 | B2 | 9 | 0.02 | s1 | n | n | d0
18040012 |  | 17225 | -- | K22 6X1.6-SH-NF F 55-622-PRYSMIAN 255 | 18 | 8 | Paron | IX4800IT+3000GVFR+5300SEIT | -- | 45.3 | 22.6 | No | 2018-04-10 | B2_s1_d2 | 0.5 | 7.5 | 11.3 | 1500 | 34 | B2 | 7 | 0.01 | s1 | y | y | d2
18040013 |  | 17210 | -- | 16 F.O KT 4X4 DRY | 12.6 | 12 | Paron | 1700SEES | -- | 43.5 | 21.8 | No | 2018-04-10 | D_s1_d0 | 2 | 31.8 | 45.5 | 870 | 85 | D | 48 | 0.09 | s1 | n | n | d0
18040014 |  | 17149 | -- | K25 750V 1X1 -SH-NF F 55-625-255 | 3 | 165 | Paron | GFR1404+3%CATCT/2HP | -- | 45.9 | 20.1 | No | 2018-04-11 | D_s2_d0 | 2.5 | 26.9 | 35.4 | 930 | 57 | D | 63 | 0.09 | s2 | n | n | d0
18040015 |  | 17167 | -- | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.9 | 160 | Paron | 1602SEES | -- | 42.3 | 21.9 | No | 2018-04-16 | B2_s1_d1 | 0.5 | 8.3 | 19.8 | 633 | 76 | B2 | 25 | 0.07 | s1 | y | n | d1
18040016 |  | 17167 | -- | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.9 | 160 | Paron | 1602SEES | -- | 41.7 | 22.1 | No | 2018-04-16 | B2_s1_d0 | 0.5 | 5.2 | 12.3 | 639 | 50 | B2 | 9 | 0.01 | s1 | n | n | d0
18040017 |  | 17231 | -- | K25 750V 1X4.0 -SH-NF F 55-625-255 | 3.9 | 90 | Paron | 1602SEES | -- | 42.9 | 21 | No | 2018-04-18 | B2_s1_d0 | 0.7 | 7.5 | 14.5 | 666 | 55 | B2 | 12 | 0.03 | s1 | n | n | d0
18040018 |  | 17231 | -- | K25 750V 1X4.0 -SH-NF F 55-625-255 ( IRRADIÉ) | 3.9 | 90 | Paron | 1602SEES | -- | 46.7 | 20 | No | 2018-04-18 | B2_s1_d0 | 0.7 | 7.3 | 15.2 | 738 | 50 | B2 | 24 | 0.04 | s1 | n | n | d0
TN_2018_973 |  |  |  | CABLES RCT ARA-Z1 RZ1-K (AS) 0.6/1KV 3G2.5 | 10.74 | 14 | Vilanova | SXLPE+BEDDLSOH+SHEATHLSOH | CD | 66.4 | 12.6 | No | 2018-04-06 | B2_s1_d0 | 0.81 | 10.3 | 16.8 | 792 | 39.6 | B2 | 8.4 | 0.01 | s1 | n | n | d0
TN_2018_974 |  |  | 424602Z | AFUMEX CLASS RZ1-K (AS) 1KV 4G2.5 | 13.02 | 12 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 64.2 | 13 | No | 2018-04-06 | C_s1_d1 | 1.39 | 21.7 | 31.1 | 1341 | 47.9 | C | 25.9 | 0.05 | s1 | y | n | d1
TN_2018_975 |  |  | T1-H17590 | PRYSMIAN (G) FS17 SPEDY FLAM TOP 450 / 750V 1X240 | 25.93 | 6 | Vilanova | PENDINGTOCONFIRM | CD | 59.2 | 15.3 | No | 2018-04-06 | B2_s2_d0 | 0.78 | 8.6 | 13.8 | 696 | 51.1 | B2 | 212.4 | 0.4 | s2 | n | n | d0
TN_2018_976 |  |  | 08 57048 | REVI ECOCLASS RZ1-K (AS) 1KV 1X240 | 29.03 | 6 | Vilanova | COMPETITORSAMPLE | CD | 56.6 | 16.7 | No | 2018-04-06 | B2_s1_d2 | 0.52 | 9.3 | 12.7 | 1500 | 25.7 | B2 | 0.9 | 0 | s1 | n | y | d2
TN_2018_977 |  |  |  | TOP CABLE HO7Z1-K 1X2.5MM2 | 3.59 | 105 | Vilanova | COMPETITORSAMPLE | CD | 50.2 | 18.5 | No | 2018-04-06 | B2_s1_d0 | 0.96 | 9.1 | 23.2 | 669 | 80.7 | B2 | 48.5 | 0.07 | s1 | n | n | d0
TN_2018_978 |  | 82403082 | 437205Y | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 14.6 | 10 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 71.7 | 12.8 | No | 2018-04-09 | C_s1_d2 | 1.24 | 21 | 37.3 | 1377 | 38.2 | C | 34.6 | 0.05 | s1 | n | y | d2
TN_2018_979 |  |  | 08 58908 | REVI ECOCLASS RZ1-K (AS) 1KV 1X150 | 23.95 | 7 | Vilanova | COMPETITORSAMPLE | CD | 70 | 14.4 | No | 2018-04-09 | B2_s1_d0 | 0.27 | 6.2 | 9.1 | 1473 | 24.3 | B2 | 7 | 0.02 | s1 | n | n | d0
TN_2018_980 |  |  |  | MIGUELEZ AFIRENAS HO7Z1-K 1X2.5MM2 | 3.61 | 105 | Vilanova | COMPETITORSAMPLE | CD | 69.2 | 15.8 | No | 2018-04-09 | C_s1_d1 | 1.54 | 13.5 | 28.8 | 822 | 68.6 | C | 17.9 | 0.07 | s1 | y | n | d1
TN_2018_981 |  | 20165688 | 424706M | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.24 | 9 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 63.3 | 17.5 | No | 2018-04-09 | D_s2_d2 | 2.1 | 27.3 | 53.1 | 1494 | 48.6 | D | 50.4 | 0.12 | s2 | n | y | d2
TN_2018_982 |  |  |  | PRYSMIAN (G) FS17 1X1.5 SPEEDY FLAM TOP 400/750V | 2.9 | 165 | Vilanova | PENDINGTOCONFIRM | CD | 63.8 | 10.3 | No | 2018-04-10 | D_s2_d0 | 0.88 | 8.4 | 18.9 | 447 | 456.4 | D | 206.4 | 0.98 | s2 | n | n | d0
TN_2018_983 |  |  |  | FG16OR16 5G1.5 MM² - 0.6/1 KV ( LA TRIVENETA) | 10.96 | 14 | Vilanova | COMPETITORSAMPLE | CD | 55.7 | 13.8 | No | 2018-04-10 | B2_s2_d0 | 0.94 | 10.1 | 27.3 | 618 | 87.5 | B2 | 151.7 | 0.59 | s2 | n | n | d0
TN_2018_984 |  |  | 432460R | AFUMEX CLASS RZ1-K (AS) 1KV 1X150 | 22.2 | 7 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 53.5 | 15.2 | No | 2018-04-10 | B2_s1_d2 | 0.62 | 7.6 | 18.3 | 1494 | 17.6 | B2 | 0 | 0 | s1 | n | y | d2
TN_2018_985 |  |  |  | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 3.04 | 165 | Vilanova | PENDINGTOCONFIRM | CD | 75.3 | 14.3 | No | 2018-04-13 | B2_s1_d1 | 1.24 | 11.5 | 25 | 630 | 115.9 | B2 | 40.3 | 0.09 | s1 | y | n | d1
TN_2018_986 |  |  |  | REVI ECOCLASS RZ1-K (AS) 0.6/1KV 3G1.5 | 9.79 | 15 | Vilanova | SXLPE+SHEATHLSOH | CD | 79.7 | 15.5 | No | 2018-04-13 | B2_s1_d0 | 0.53 | 8.4 | 14.3 | 573 | 55.6 | B2 | 5.2 | 0.01 | s1 | n | n | d0
TN_2018_987 |  |  | 06 56282 | REVI ECOCLASS RZ1-K (AS) 1KV 3G2.5 | 10.79 | 14 | Vilanova | SXLPE+SHEATHLSOH | CD | 77.8 | 15.5 | No | 2018-04-13 | C_s1_d0 | 1.71 | 24.2 | 32.7 | 1155 | 45.7 | C | 32.9 | 0.05 | s1 | n | n | d0
TN_2018_988 |  | OP 64977 20227120 | 417842B | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.12 | 17 | Vilanova | GFR1404+PAPER+20AJ | CD | 73.3 | 14.6 | No | 2018-04-17 | B2_s1_d1 | 0.79 | 12.6 | 28.7 | 672 | 77.1 | B2 | 16.5 | 0.03 | s1 | y | n | d1
TN_2018_989 |  |  |  | REVI ECOCLASS 1X1.5 H07Z1-K (AS) TYPE2 AENOR HAR 750V | 2.91 | 165 | Vilanova | COMPETITORSAMPLE | CD | 72.8 | 14.9 | No | 2018-04-17 | C_s2_d0 | 1.98 | 19.7 | 34.8 | 714 | 88.3 | C | 76 | 0.16 | s2 | n | n | d0
TN_2018_990 |  |  |  | REVI ECOCLAS 1X2.5 H07Z1-K (AS) TYPE2 UNE EN 50525 AENOR HAR 750V | 3.77 | 90 | Vilanova | COMPETITORSAMPLE | CD | 66.6 | 17.3 | No | 2018-04-17 | B2_s1_d0 | 1.03 | 11.8 | 24 | 681 | 87.2 | B2 | 22.7 | 0.08 | s1 | n | n | d0
TN_2018_991 |  | OP 64977 20227120 | 417831P | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.23 | 17 | Vilanova | GFR1404+LANTOR+20AJ | CD | 56.5 | 20.3 | No | 2018-04-17 | B2_s1_d0 | 0.56 | 7.6 | 18.3 | 693 | 47.9 | B2 | 4.3 | 0.01 | s1 | n | n | d0
TN_2018_992 |  | OP 64978 20227121 | 419088F | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 17 | 9.03 | Vilanova | GFR1404+LANTOR+D263 | CD | 53.8 | 22 | No | 2018-04-17 | B2_s1_d0 | 0.44 | 7.4 | 13.1 | 621 | 55.7 | B2 | 10.3 | 0.01 | s1 | n | n | d0
TN_2018_993 |  | OP65709 20232526 | 402674P | AFUMEX RZ1FA3Z1-K 1KV ADIF 3X1.5 | 13.57 | 11 | Vilanova | PENDINGTOCONFIRM | CD | 58.9 | 18.1 | No | 2018-04-24 | B2_s1_d1 | 0.72 | 12.5 | 23 | 801 | 45.8 | B2 | 17.8 | 0.04 | s1 | y | n | d1
TN_2018_994 |  | 20260030 | 447589K | PRYSMIAN EPROTENAX DHVMV 2RH 6/10 KV 3X120 | 66.02 | 3 | Vilanova | PVC2400 | CD | 56.4 | 20.8 | No | 2018-04-24 | B2_s3_d2 | 0.8 | 11 | 12.2 | 1029 | 57.4 | B2 | 744.1 | 0.84 | s3 | n | y | d2
18040019 |  | 17245 | -- | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.8 | 180 | Paron | 1602SEES | -- | 48.2 | 21.1 | No | 2018-04-24 | B2_s1_d0 | 0.9 | 8.6 | 18.3 | 735 | 60 | B2 | 18 | 0.04 | s1 | n | n | d0
TN_2018_995 |  |  | 192130 | PRYSMIAN 255 10 2017 NF C33-226 150 AL 12/20 (24 KV) POPY G2.2 SCI ECO.15 C2T 10/50 RT | 21.41 | 6 | Vilanova | SXLPE+HE6062+MBPOLYTRIOX | CD | 41.4 | 24.1 | No | 2018-04-24 | _ _
TN_2018_996 |  | OP65709 20232526 | 402674P | AFUMEX RZ1FA3Z1-K 1KV ADIF 3X1.5 | 13.57 | 11 | Vilanova | PENDINGTOCONFIRM | OD | 58.4 | 19.8 | No | 2018-04-26 | B2_s1_d1 | 0.8 | 12.1 | 22.5 | 821 | 42.8 | B2 | 16.9 | 0.04 | s1 | y | n | d1
TN_2018_997 |  | 20260030 | 447589K | PRYSMIAN EPROTENAX DHVMV 2RH 6/10 KV 3X120 | 66.02 | 3 | Vilanova | PVC2400 | OD | 57.9 | 21.6 | No | 2018-04-26 | B2_s3_d2 | 0.83 | 10.3 | 12.8 | 1155 | 38.8 | B2 | 712.8 | 0.9 | s3 | n | y | d2
TN_2018_998 |  | OP 64978 2022721 | 419091J | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.18 | 17 | Vilanova | GFR1404+PAPER+D263 | CD | 75.7 | 17.8 | No | 2018-04-27 | B2_s1_d0 | 0.9 | 14 | 28.1 | 798 | 73.2 | B2 | 35.2 | 0.08 | s1 | n | n | d0
TN_2018_999 |  | OP64980 20227118 | 419076T | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.15 | 17 | Vilanova | XLPE+LANTOR+D263 | CD | 68.4 | 19.9 | No | 2018-04-27 | E ou F_s2_d2 | 3.3 | 70.8 | 190.8 | 1143 | 227 | E ou F | 105.8 | 0.32 | s2 | n | y | d2
TN_2018_1000 |  |  | TA-D34739 | FG18M16 AFUMEX GOLD 1KV 1X10 | 11.76 | 13 | Vilanova | INS:SD3500.FILLER:0400FEITAND5300SEITSCAPATAPE | CD | 58.8 | 22 | No | 2018-04-27 | B2_s1_d2 | 0.45 | 8.5 | 11.6 | 549 | 60.4 | B2 | 0.2 | 0 | s1 | n | y | d2
TN_2018_1001 |  | OP67627 20235313 | 443747J | MRZ1F3Z1-K 1KV ADIF 2X35 | 27.21 | 6 | Vilanova | CPRDMZ-E20AJ | CD | 61.2 | 14.4 | No | 2018-05-03 | B2_s1_d2 | 0.42 | 5.8 | 10.4 | 1500 | 20.4 | B2 | 8 | 0.01 | s1 | n | y | d2
TN_2018_1002 |  | OP67626 20232332 | 443783Y | RZ1F3Z1 3KV 3X25 AL ADIF | 30.95 | 6 | Vilanova | CPRDMZ-E20AJ | CD | 59.8 | 15 | No | 2018-05-03 | B2_s1_d2 | 0.77 | 11.6 | 21.9 | 1410 | 19.7 | B2 | 10.6 | 0.04 | s1 | n | y | d2
TN_2018_1003 |  | OP64981 20227122 | 419070L | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.19 | 17 | Vilanova | XLPE+PAPER+S663 | CD | 55.3 | 17.2 | No | 2018-05-03 | D_s2_d2 | 3.3 | 68.3 | 173.7 | 1299 | 175.4 | D | 98.1 | 0.27 | s2 | n | y | d2
TN_2018_1004 |  | OP64980 20227118 | 419079W | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.25 | 17 | Vilanova | XLPE+PAPER+D263 | CD | 51.1 | 19.2 | No | 2018-05-03 | E ou F_s2_d2 | 3.3 | 72 | 233.8 | 1167 | 269.8 | E ou F | 118.5 | 0.38 | s2 | n | y | d2
TN_2018_1005 |  | OP64981 20227122 | 340234V | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.53 | 15 | Vilanova | XLPE+LANTOR+S663 | CD | 47.2 | 21.2 | No | 2018-05-03 | D_s2_d2 | 3.3 | 61.3 | 167 | 1428 | 148.3 | D | 91.8 | 0.26 | s2 | n | y | d2
TN_2018_1006 |  | OP64979 20227123 | 340267F | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.35 | 17 | Vilanova | GFR1404+LANTOR+S663 | CD | 46.8 | 15.8 | No | 2018-05-04 | C_s1_d0 | 1.29 | 14.5 | 32.8 | 819 | 63.3 | C | 0.12 | 0.12 | s1 | n | n | d0
TN_2018_1007 |  | OP64979 20227123 | 419080X | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.25 | 17 | Vilanova | GFR1404+PAPER+S663 | CD | 46.7 | 16 | No | 2018-05-04 | B2_s1_d0 | 0.76 | 8.6 | 17 | 801 | 53.1 | B2 | 16.1 | 0.05 | s1 | n | n | d0
TN_2018_1008 |  | OP64976 20227119 | 340271K | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.33 | 17 | Vilanova | GFR1404+LANTOR+20AK | CD | 46.7 | 16.9 | No | 2018-05-04 | C_s1_d1 | 1.08 | 13.7 | 30.7 | 777 | 65 | C | 22.6 | 0.04 | s1 | y | n | d1
TN_2018_1009 |  | OP64976 20227119 | 340272L | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.22 | 17 | Vilanova | GFR1404+PAPER+20AK | CD | 45.5 | 18.4 | No | 2018-05-04 | B2_s1_d0 | 0.35 | 6.7 | 11.1 | 720 | 42.6 | B2 | 9.6 | 0.02 | s1 | n | n | d0
TN_2018_1010 |  |  | 175571N | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.39 | 15 | Vilanova | DMZ-EVERDE+CALOXOLPURO | CD | 67.5 | 16.9 | No | 2018-05-06 | C_s1_d2 | 1.99 | 27.2 | 35.4 | 882 | 70 | C | 33.1 | 0.08 | s1 | n | y | d2
TN_2018_1011 |  | 82321602 20193645 | 422568N | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 27.46 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 63.8 | 19.5 | No | 2018-05-06 | B2_s1_d0 | 0.47 | 5.1 | 8.5 | 1311 | 15.8 | B2 | 19.8 | 0.02 | s1 | n | n | d0
TN_2018_1012 |  |  | 436049S | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.57 | 14 | Vilanova | DMZ-ECALOXOL1% | CD | 65.8 | 19.5 | No | 2018-05-06 | C_s2_d2 | 1.68 | 23.3 | 34 | 1011 | 58.7 | C | 68 | 0.1 | s2 | n | y | d2
TN_2018_1013 |  |  | 380470E | AFUMEX CLASS RZ1-K (AS) 1KV 4G1.5 | 11.26 | 14 | Vilanova | DMZ-ECALOXOL1% | CD | 72.3 | 19.1 | No | 2018-05-06 | D_s1_d1 | 1.8 | 30.6 | 43.5 | 1458 | 60.4 | D | 32.3 | 0.05 | s1 | y | n | d1
TN_2018_1014 |  |  | TA-D34739 | FG18M16 AFUMEX GOLD 1KV 1X10 | 11.36 | 14 | Vilanova | INS:SD3500.FILLER:0400FEITAND5300SEITWITHOUTSCAPATAPE | CD | 79.6 | 17.4 | No | 2018-05-08 | B2_s1_d0 | 0.28 | 4.5 | 7.5 | 552 | 33 | B2 | 12.2 | 0.01 | s1 | n | n | d0
TN_2018_1015 |  |  |  | ALCOBRE RZ1-K (AS) 1KV 3G1.5 | 9.69 | 15 | Vilanova | COMPETITORSAMPLE | CD | 79.6 | 17.7 | No | 2018-05-08 | C_s1_d0 | 1.65 | 19.2 | 21.8 | 867 | 59.7 | C | 39 | 0.06 | s1 | n | n | d0
TN_2018_1016 |  |  |  | NEXANS ALSECURE RZ1-K (AS) 1KV 3G1.5 | 10.57 | 14 | Vilanova | COMPETITORSAMPLE | CD | 76.6 | 19.2 | No | 2018-05-08 | D_s1_d2 | 2.65 | 33.9 | 50.4 | 876 | 87.8 | D | 23.8 | 0.04 | s1 | n | y | d2
TN_2018_1017 |  |  | 366824X | ALPAM 2.0ST N0F0M2-48G 652 D (10361) | 12.61 | 12 | Vilanova | 1602SEES | CD | 74 | 20.8 | No | 2018-05-08 | B2_s1_d2 | 0.57 | 6.5 | 13.3 | 648 | 39.1 | B2 | 0 | 0 | s1 | n | y | d2
TN_2018_1018 |  |  | 446764N | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.3 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS+SKINSC | CD | 63.7 | 19.8 | No | 2018-05-10 | C_s1_d2 | 1.05 | 27.7 | 44.5 | 1500 | 44.3 | C | 8.2 | 0.01 | s1 | n | y | d2
18050001 |  | 17256 | -- | K22 24-1.6-SH-NF F 55-622-PRYSMIAN 255 | 27.5 | 6 | Paron | IX4800IT+3000GVFR+5300SEIT | -- | 53 | 20.9 | No | 2018-05-14 | B2_s1_d2 | 0.3 | 3.9 | 5.2 | 465 | 27 | B2 | 6 | 0.01 | s1 | y | y | d2
18050002 |  | 17256 | -- | K22 14-1.6-SH-NF F 55-622-PRYSMIAN 255 | 22 | 7 | Paron | IX4800IT+3000GVFR+5300SEIT | -- | 50.9 | 22.3 | No | 2018-05-14 | B2_s1_d2 | 0.4 | 3.9 | 5 | 1500 | 21 | B2 | 4 | 0.01 | s1 | y | y | d2
18050003 |  | 17269 | -- | K26 R 7/8" 50 10/2018 82460316 DRAKA | 28 | 6 | Paron | SXLPE+RUBANSCAPA+5300SEIT | -- | 49.9 | 22.9 | No | 2018-05-16 | C_s1_d2 | 1.25 | 25.1 | 46.5 | 1026 | 75 | C | 28 | 0.05 | s1 | y | y | d2
18050004 |  | 17277 | -- | ELECLINK 5X16MM | 28.4 | 6 | Paron | IX1000FR+3000GVFR+0400FEIT+5300SEIT | -- | 47.7 | 21.3 | No | 2018-05-18 | B2_s1_d0 | 0.3 | 2.5 | 3.9 | 564 | 13 | B2 | 8 | 0.01 | s1 | n | n | d0
18050005 |  | 17277 | -- | ELECLINK 5X16MM | 24 | 7 | Paron | IX1000FR+3000GVFR+5300SEIT | -- | 44.4 | 20.1 | No | 2018-05-18 | B2_s1_d2 | 0.4 | 3.5 | 5 | 1059 | 12 | B2 | 9 | 0.01 | s1 | y | y | d2
TN_2018_1019 |  |  |  | HI XDV (AS) PRYSMIAN 208 3X35+70 MASSIF (50E) | 33.54 | 5 | Vilanova | SXLPE+3300SPFR | CD | 74.2 | 18.1 | No | 2018-05-11 | C_s2_d2 | 1.91 | 20.4 | 48.8 | 597 | 201.4 | C | 205.3 | 0.35 | s2 | n | y | d2
TN_2018_1020 |  |  |  | HI XDV (AS) PRYSMIAN 208 RESONET 3X95 + 1X50 | 32.21 | 6 | Vilanova | SXLPE+3300SPFR | CD | 72.8 | 18.3 | No | 2018-05-11 | D_s2_d2 | 3.3 | 44.8 | 176 | 1320 | 231.6 | D | 382.4 | 1.18 | s2 | n | y | d2
TN_2018_1021 |  |  |  | HI XDV PRYSMIAN 208 ENEDIS 33 S210 1X35M+1X35 MASSIF | 19.15 | 8 | Vilanova | SXLPE+3300SPFR | CD | 68 | 19.9 | No | 2018-05-11 | E ou F_s2_d2 | 3.3 | 85.3 | 181.1 | 774 | 448.4 | E ou F | 302.5 | 0.61 | s2 | n | y | d2
TN_2018_1023 |  |  |  | HI XDV AU PRYSMIAN 208 1X35+1X35 | 19.65 | 8 | Vilanova | SXLPE+3300SPFR | CD | 61.1 | 22.1 | No | 2018-05-11 | __
TN_2018_1024 |  | OP 67804 20265344 | 447862G | AFUMEX CLASS O 1Z1C7Z1-K 1KV 37X2.5 | 34.56 | 5 | Vilanova | 1602+1602+LANTORLONGITUDINAL+AFUMEX2000SEES | CD | 61.2 | 16.2 | No | 2018-05-16 | B2_s1_d2 | 0.56 | 4.1 | 9.3 | 1500 | 10.5 | B2 | 0.3 | 0 | s1 | n | y | d2
TN_2018_1025 |  | OP66724 20257710 | 444206H | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.2 | 17 | Vilanova | AISLAMIENTO1602SEESIRRADIADOENPARON+PAPEL+CUBIERTA20AJ | CD | 59.4 | 16.9 | No | 2018-05-16 | C_s1_d2 | 1.91 | 22.6 | 36.9 | 921 | 68.4 | C | 42.3 | 0.09 | s1 | n | y | d2
TN_2018_1026 |  |  | 446764N | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 75.06 | 3 | Vilanova | XLPE+ALFOIL+60ACESGRIS | CD | 46 | 22.2 | No | 2018-05-16 | D_s1_d2 | 1.07 | 45.3 | 86.1 | 1494 | 73.6 | D | 13.8 | 0.03 | s1 | n | y | d2
TN_2018_1027 |  |  | 436049S | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.57 | 14 | Vilanova | DMZ-ECALOXOL1% | CD | 46.8 | 22.6 | No | 2018-05-16 | C_s1_d0 | 1.3 | 16.3 | 20.5 | 900 | 38.3 | C | 21.8 | 0.04 | s1 | n | n | d0
TN_2018_1028 |  | OP66724 20257710 | 459436T | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.67 | 15 | Vilanova | AISLAMIENTO1602SEESIRRADIADOENPARON+PAPEL+CUBIERTA1602SEES | CD | 56.6 | 19.5 | No | 2018-05-18 | B2_s1_d1 | 1.24 | 14.8 | 21.5 | 684 | 62.6 | B2 | 46.3 | 0.1 | s1 | y | n | d1
TN_2018_1029 |  | OP67592 20180297 | 444202D | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.07 | 17 | Vilanova | AISLAMIENTOXLPE+SKINGFR365+PAPEL+CUBIERTA20AJ | CD | 56.1 | 19.9 | No | 2018-05-18 | E ou F_s2_d2 | 3.3 | 75.1 | 212 | 1197 | 236.3 | E ou F | 85.6 | 0.23 | s2 | n | y | d2
TN_2018_1030 |  |  | 380470E | AFUMEX CLASS RZ1-K (AS) 1KV 4G1.5 | 11.26 | 14 | Vilanova | DMZ-ECALOXOL1% | CD | 53.9 | 21.6 | No | 2018-05-18 | C_s1_d0 | 1.84 | 29.6 | 40.4 | 1449 | 54.4 | C | 22.6 | 0.07 | s1 | n | n | d0
TN_2018_1031 |  |  |  | IRISTECH U-1000 R2V-U 2X1.5-NF-USE 26S | 9 | 17 | Vilanova | IX1100FR+2000SPIT | CD | 51.7 | 22.2 | No | 2018-05-18 | C_s2_d1 | 1.67 | 14.6 | 39 | 657 | 139.1 | C | 280 | 0.85 | s2 | y | n | d1
TN_2018_1032 |  |  |  | IRISTECH U-1000 RZU-R 1X25 NF-USE 26S | 10.81 | 14 | Vilanova | IX1100FR+1100FPFR+2000SPIT | CD | 48.3 | 22.9 | No | 2018-05-18 | D_s2_d2 | 2.1 | 22.3 | 34.5 | 1164 | 69 | D | 242.1 | 0.45 | s2 | n | y | d2
18050006 |  | 17277 | -- | 1X95MM2 ELECLINK | 20.1 | 8 | Paron | IX1400FR+5300SEIT | -- | 47.7 | 21.3 | No | 2018-05-18 | C_s1_d2 | 1.1 | 19.8 | 50.9 | 1350 | 49 | C | 37 | 0.14 | s1 | y | y | d2
18050007 |  | 17277 | -- | 1X95MM2 ELECLINK | 24.3 | 7 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 44.4 | 20.1 | No | 2018-05-18 | B2_s1_d0 | 0.35 | 5 | 5.9 | 705 | 19 | B2 | 13 | 0.02 | s1 | n | n | d0
18050008 |  | 17275 | -- | F.O KT 4X4 FILLED ( PROTO Nº16) | 11.6 | 13 | Paron | 1602SEES | -- | 68.3 | 20.5 | No | 2018-05-24 | E ou F_s2_d2 | 3.3 | 91.5 | 161.9 | 1176 | 185 | E ou F | 106 | 0.29 | s2 | y | y | d2
18050009 |  | 17275 | -- | F.O KT 4X4 FILLED ( PROTO Nº17) | 13.4 | 12 | Paron | 1602SEES | -- | 63.2 | 23.3 | No | 2018-05-24 | D_s1_d2 | 2.35 | 46.3 | 65 | 1032 | 96 | D | 46 | 0.09 | s1 | y | y | d2
TN_2018_1033 |  | OP67592 20180297 | 451384K | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.59 | 15 | Vilanova | AISLAMIENTOXLPE+SKINHFX521+PAPEL+CUBIERTA1602SEES | CD | 67.4 | 18.5 | No | 2018-05-22 | E ou F_s2_d2 | 3.3 | 70.4 | 163.2 | 1449 | 142.4 | E ou F | 65.1 | 0.17 | s2 | n | y | d2
TN_2018_1034 |  | OP67592 20180297 | 444186L | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 8.99 | 17 | Vilanova | AISLAMIENTOXLPE+SKIN1602SEES+PAPEL+CUBIERTA20AJ | CD | 75.9 | 18 | No | 2018-05-23 | E ou F_s2_d2 | 3.3 | 74 | 155.6 | 1350 | 149.3 | E ou F | 78.3 | 0.21 | s2 | n | y | d2
TN_2018_1035 |  | OP67592 20180297 | 441197Y | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.23 | 17 | Vilanova | AISLAMIENTOXLPE+SKINHFX521+PAPEL+CUBIERTA20AJ | CD | 73.5 | 18.8 | No | 2018-05-23 | D_s2_d2 | 3.3 | 68.8 | 171.2 | 1410 | 154.4 | D | 77.1 | 0.21 | s2 | n | y | d2
TN_2018_1036 |  | OP67517 20233799 | 455115R | AFUMEX EASY RZ1-K 0.6/1.0KV 4G240 | 62.41 | 3 | Vilanova | SXLPE+1602SEES | CD | 66.1 | 21.8 | No | 2018-05-23 | B2_s1_d2 | 0.52 | 5.6 | 9.4 | 1278 | 15.2 | B2 | 0 | 0 | s1 | n | y | d2
TN_2018_1037 |  | OP66578 20235882 | 440870G | LXHIOZ1 1X120 30KV | 40.67 | 5 | Vilanova | XLPE+1420FEES+6000SEES | CD | 63.7 | 22.9 | No | 2018-05-23 | C_s1_d2 | 1.22 | 21.8 | 31.6 | 975 | 55.1 | C | 23 | 0.08 | s1 | n | y | d2
TN_2018_1038 |  | OP67592 20180297 | 451386M | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.48 | 17 | Vilanova | AISLAMIENTOXLPE+SKIN1602SEES+PAPEL+CUBIERTA1602SEES | CD | 58.3 | 23.8 | No | 2018-05-23 | E ou F_s2_d2 | 3.3 | 75.3 | 155.7 | 1344 | 152.6 | E ou F | 64.3 | 0.2 | s2 | n | y | d2
TN_2018_1039 |  | OP67592 20180297 | 451344S | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.44 | 17 | Vilanova | AISLAMIENTOXLPE+SKINGFR365+PAPEL+CUBIERTA1602SEES | CD | 64.3 | 19.5 | No | 2018-05-25 | D_s2_d2 | 3.3 | 49.7 | 76 | 1500 | 104.1 | D | 71.1 | 0.11 | s2 | n | y | d2
TN_2018_1040 |  | OP67477 | 451402E | AFUMEX CLASS ATEX DZ1MZ1-K 2RH 1KV 19X1.5 | 23.36 | 7 | Vilanova | INS:IRN-267.BEDDING:GRI-141ANDSHEATH:60ABEXPERIMENTAL | CD | 62.6 | 20.1 | No | 2018-05-25 | B2_s1_d1 | 0.57 | 9.3 | 14.1 | 1500 | 45.4 | B2 | 7.7 | 0.02 | s1 | y | n | d1
TN_2018_1041 |  | OP82397169 | 448361Z | AFUMEX CLASS RZ1-K (AS) 1KV 1X150 | 22.69 | 7 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 55.1 | 22.5 | No | 2018-05-25 | C_s1_d2 | 0.79 | 16.4 | 39.4 | 1500 | 35.8 | C | 0 | 0 | s1 | y | y | d2
TN_2018_1042 |  | 20064278 | 451477L | PRYSMIAN SAP 2018 67476 RVMV-K 1KV NPI RH HCL <15% 3G2.5 | 14.73 | 10 | Vilanova | INS:XLPE.BEDDING6010SEESANDSHEATH:60ABEXPERIMENTAL | CD | 46.3 | 24.1 | No | 2018-05-25 | D_s1_d2 | 3.3 | 66.9 | 123.4 | 1431 | 118.1 | D | 17.3 | 0.03 | s1 | n | y | d2
18050010 |  | 17275 | -- | 32 F.O KT 8X4 FILLED (PROTO Nº18) | 13.1 | 12 | Paron | 1602SEES | -- | 52 | 26.4 | No | 2018-05-28 | E ou F_s2_d2 | 3.3 | 128.3 | 312.5 | 1038 | 426 | E ou F | 310 | 0.75 | s2 | y | y | d2
18050011 |  | 17275 | -- | 24 F.O TKEST 2X12 FILLED (PROTO Nº19) | 14.7 | 10 | Paron | 1602SEES | -- | 51.8 | 26.2 | No | 2018-05-28 | B2_s1_d2 | 0.7 | 10.9 | 16.8 | 819 | 37 | B2 | 37 | 0.05 | s1 | y | y | d2
18050012 |  | 17275 | -- | 24 F.O TKEST 2X12 DRY (PROTO Nº20) | 17.7 | 8 | Paron | 1602SEES | -- | 51.5 | 27.2 | No | 2018-05-28 | B2_s1_d2 | 0.7 | 13.4 | 20.3 | 1044 | 30 | B2 | 42 | 0.09 | s1 | y | y | d2
18050013 |  | 17294 | -- | ELECLINK 1X630 CU 45KV ( CÂBLE Nº2) | 65.8 | 3 | Paron | XLPE+5300SEIT+5300SEIT | -- | 60.9 | 23.3 | No | 2018-05-30 | B2_s1_d0 | 0.4 | 2.6 | 3.9 | 1023 | 7 | B2 | 7 | 0.01 | s1 | n | n | d0
18050014 |  | 17294 | -- | ELECLINK 1X630 CU 45KV ( CÂBLE Nº1) | 76 | 3 | Paron | XLPE+0400FEIT+5300SEIT | -- | 61.1 | 24.8 | No | 2018-05-30 | B2_s1_d0 | 0.6 | 3 | 4.3 | 1041 | 7 | B2 | 7 | 0.01 | s1 | n | n | d0
18060001 |  | 17275 | -- | 24 F.O TKEST 2X12 FILLED (PROTO Nº21) | 13 | 12 | Paron | 1602SEES | -- | 60.8 | 23.9 | No | 2018-06-01 | C_s1_d0 | 0.8 | 17.5 | 29.7 | 924 | 60 | C | 40 | 0.08 | s1 | n | n | d0
18060002 |  | 17275 | -- | 24 F.O TKEST 2X12 DRY (PROTO Nº22) | 14 | 11 | Paron | 1602SEES | -- | 62.2 | 23.3 | No | 2018-06-01 | B2_s1_d0 | 0.7 | 13.1 | 24.8 | 864 | 53 | B2 | 39 | 0.09 | s1 | n | n | d0
18060003 |  | 17275 | -- | 12 F.O TVT 1X12 FILLED (PROTO Nº24) | 14 | 11 | Paron | PE+1602SEES+10%LLDPE | -- | 52.3 | 25.3 | No | 2018-06-01 | E ou F_s1_d2 | 3.3 | 96.7 | 146.8 | 1233 | 169 | E ou F | 27 | 0.06 | s1 | y | y | d2
18060004 |  | 17275 | -- | 24 F.O T 6X4 FILLED (PROTO Nº25) | 9.6 | 15 | Paron | ECCOH5924 | -- | 55.9 | 24.6 | No | 2018-06-01 | D_s2_d0 | 3.3 | 36.5 | 52.5 | 771 | 114 | D | 70 | 0.1 | s2 | n | n | d0
TN_2018_1043 |  | OP67627 20235313 | 443747J | MRZ1F3Z1-K 1KV ADIF 2X35 | 27.21 | 6 | Vilanova | CPRDMZ-E20AJ | CD | 81.5 | 20.9 | No | 2018-05-29 | B2_s1_d2 | 0.47 | 6.3 | 10.1 | 1500 | 18 | B2 | 11.8 | 0.02 | s1 | n | y | d2
18050005 |  | 17282 | -- | 1000-3G10MM²-SH-NF F 55-625-255 | 17.7 | 8 | Paron | IX1100FR+0400FEIT+5300SEIT | -- | 60.2 | 24.9 | No | 2018-06-08 | B2_s1_d1 | 0.5 | 4.6 | 7.8 | 1494 | 18 | B2 | 11 | 0.02 | s1 | y | n | d1
18050006 |  | 17282 | -- | 1000-3G10MM²-SH-NF F 55-625-255 | 17.7 | 8 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 58.3 | 25.9 | No | 2018-06-08 | B2_s1_d0 | 0.45 | 4.2 | 6.2 | 720 | 21 | B2 | 10 | 0.01 | s1 | n | n | d0
18050007 |  | 17275 | -- | 32 F.O T 8X4 FILLED (PROTO Nº23) | 13 | 12 | Paron | 1602SEES+10%PE | -- | 53.8 | 26.9 | No | 2018-06-08 | E ou F_s2_d2 | 3.3 | 126.7 | 347 | 915 | 564 | E ou F | 269 | 0.83 | s2 | y | y | d2
TN_2018_1044 |  |  | 175571N | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.39 | 15 | Vilanova | DMZ-EVERDE+CALOXOLPURO | CD | 80.3 | 21.2 | No | 2018-05-29 | C_s1_d0 | 1.52 | 29.4 | 34.9 | 1086 | 63.5 | C | 24.9 | 0.04 | s1 | n | n | d0
TN_2018_1045 |  | OP67626 20232332 | 443783Y | RZ1F3Z1 3KV 3X25 AL ADIF | 30.95 | 6 | Vilanova | CPRDMZ-E20AJ | CD | 74.8 | 22.6 | No | 2018-05-29 | B2_s1_d2 | 0.75 | 10.9 | 19.6 | 1371 | 29 | B2 | 5 | 0.02 | s1 | n | y | d2
TN_2018_1046 |  |  |  | FS17 SPEEDY FLAM TOP 450/750V CCA S3 D1 A3 (ORANGE) | 2.92 | 165 | Vilanova | 2800SPITPVC | CD | 69.7 | 23.3 | No | 2018-05-29 | B2_s2_d0 | 0.75 | 3 | 10.8 | 468 | 64 | B2 | 200 | 0.97 | s2 | n | n | d0
TN_2018_1047 |  |  |  | FS17 SPEEDY FLAM TOP 450/750V CCA S3 D1 A3 (PINK) | 2.93 | 165 | Vilanova | 2800SPITPVC | CD | 65.8 | 24 | No | 2018-05-29 | B2_s2_d0 | 0.98 | 14.2 | 17.9 | 1479 | 110.3 | B2 | 223.6 | 0.93 | s2 | n | n | d0
TN_2018_1048 |  | OP67134 20231931 | 457326U | AFUMEX CLASS ATEX MRZ1MZ1-K 1KV 20X2.5 | 29.65 | 6 | Vilanova | XLPE+1602+1602 | CD | 72.6 | 20.6 | No | 2018-05-30 | B2_s1_d2 | 0.74 | 9.4 | 18.2 | 1497 | 21.1 | B2 | 26.1 | 0.05 | s1 | n | y | d2
TN_2018_1049 |  |  | T8F74891 | FG16OM16 3G1.5 MM² - 0.6/1 KV | 11.13 | 14 | Vilanova | CARTA+04AMFEIT+5300SEIT | CD | 75.3 | 20.8 | No | 2018-05-30 | B2_s1_d2 | 0.42 | 10.1 | 12.4 | 837 | 31.7 | B2 | 1.7 | 0.01 | s1 | n | y | d2
TN_2018_1050 |  | 20259297 | TM-C10285 | RG16H1M16 12/20KV 1X50 | 29.76 | 6 | Vilanova | PET+0400FEIT+LANTOR+MEGOLONS540 | CD | 68.1 | 20.9 | No | 2018-05-31 | B2_s1_d0 | 0.37 | 2.8 | 4.8 | 729 | 12 | B2 | 0.3 | 0 | s1 | n | n | d0
TN_2018_1051 |  | 20259295 | TM-C10285 | RG16H1M16 12/20KV 1X25 | 28.15 | 6 | Vilanova | PET+0400FEIT+LANTOR+MEGOLONS540 | CD | 63.6 | 22.1 | No | 2018-05-31 | B2_s1_d0 | 0.44 | 6.8 | 10.8 | 1497 | 16.9 | B2 | 0.1 | 0 | s1 | n | n | d0
TN_2018_1052 |  | 20259296 | TM-C10285 | RG16H1M16 12/20KV 1X50 | 29.95 | 6 | Vilanova | SCAPA+0400FEIT+LANTOR+5300SEIT | CD | 61.1 | 23.1 | No | 2018-05-31 | B2_s1_d0 | 0.38 | 3.9 | 4.8 | 1464 | 13.7 | B2 | 5.7 | 0.01 | s1 | n | n | d0
TN_2018_1053 |  | 20259294 | TM-C10285 | RG16H1M16 12/20KV 1X25 | 28.11 | 6 | Vilanova | SCAPA+0400FEIT+LANTOR+5300SEIT | CD | 57.9 | 23.9 | No | 2018-05-31 | B2_s1_d0 | 0.35 | 4.9 | 7.4 | 1488 | 12.2 | B2 | 5.2 | 0.01 | s1 | n | n | d0
TN_2018_1057 |  | OP67133 20259574 | 449791D | AFUMEX CLASS ATEX MRZ1MZ1-K 1KV 2X2.5 | 29.65 | 6 | Vilanova | SXLPE+1602SEES+1602SEES | CD | 75.8 | 18.7 | No | 2018-06-08 | C_s1_d2 | 0.86 | 16.2 | 26.4 | 1083 | 34.1 | C | 22.7 | 0.09 | s1 | n | y | d2
TN_2018_1058 |  | OP67134 20231931 | 457326U | AFUMEX CLASS ATEX MRZ1MZ1-K 1KV 20X2.5 | 29.65 | 6 | Vilanova | XLPE+1602+1602 | CD | 70.1 | 21.7 | No | 2018-06-08 | B2_s1_d2 | 0.62 | 10.5 | 19.4 | 1491 | 28.9 | B2 | 5.2 | 0.01 | s1 | n | y | d2
TN_2018_1059 |  | OP66578 20235882 | 440870G | LXHIOZ1 1X120 30KV | 40.67 | 5 | Vilanova | XLPE+1420FEES+6000SEES | OD | 36.1 | 28.5 | No | 2018-06-12 | C_s1_d2 | 1.36 | 22.1 | 48.6 | 1500 | 40.5 | C | 8.7 | 0.03 | s1 | n | y | d2
TN_2018_1060 |  | OP64581 20184155 | 391249W | LXHIOZ1 1X500 15KV | 50.35 | 4 | Vilanova | XLPE+1420FEES+6000SEES | OD | 73.9 | 20.4 | No | 2018-06-12 | B2_s1_d2 | 0.7 | 9.2 | 16.8 | 1170 | 22.6 | B2 | 16.3 | 0.04 | s1 | n | y | d2
TN_2018_1061 |  | 82465129 | 456880J | AFUMEX CLASS ATEX RZ1MZ1-K (AS) 1KV 3X6 | 16.9 | 9 | Vilanova | XLPE+1602+ARMOUR+LONGITUDINALTAPE+1602 | CD | 55.4 | 22.3 | No | 2018-06-19 | C_s1_d1 | 0.75 | 19.1 | 33.4 | 1389 | 32.9 | C | 8 | 0.02 | s1 | y | n | d1
TN_2018_1062 |  | 82465127 | 449766B | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K (AS+) 1KV 3G2.5 | 15.05 | 10 | Vilanova | XLPE+1602+ARMOUR+LONGITUDINALTAPE+1602 | CD | 57.3 | 25.3 | No | 2018-06-17 | B2_s1_d1 | 0.78 | 13 | 20.8 | 1053 | 30.4 | B2 | 11.7 | 0.03 | s1 | y | n | d1
TN_2018_1063 |  | 82465127 | 456892X | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K (AS+) 1KV 3G2.5 | 14.9 | 10 | Vilanova | XLPE+1602+ARMOUR+LONGITUDINALTAPE+1602 | CD | 55.8 | 25.7 | No | 2018-06-17 | C_s1_d2 | 0.75 | 19.8 | 28 | 1098 | 39.5 | C | 12.4 | 0.02 | s1 | n | y | d2
18060008 |  | 17314 | T8F74891 | FG16OM16 3G1.5 MM² - 0.6/1 KV | 11 | 14 | Paron | CARTA+04AMFEIT+5300SEIT | -- | 53.6 | 24.6 | No | 2018-06-19 | B2_s1_d2 | 0.7 | 8.2 | 17.6 | 879 | 38 | B2 | 12 | 0.03 | s1 | y | y | d2
18060009 |  | 17315 | -- | 48 F.O TVT 4X12 FILLED (PROTO Nº26) | 14.3 | 11 | Paron | 1602SEES+1602SEES | -- | 58.5 | 23.5 | No | 2018-06-19 | E ou F_s2_d1 | 3.3 | 76.7 | 112.8 | 1329 | 132 | E ou F | 69 | 0.13 | s2 | y | n | d1
18060010 |  | 17315 | -- | 72 F.O FXT VT 18X4 DRY (PROTO Nº27) | 10.4 | 15 | Paron | 1700SEES | -- | 55.8 | 24.7 | No | 2018-06-19 | C_s1_d2 | 1.55 | 8.7 | 21.5 | 636 | 82 | C | 32 | 0.08 | s1 | y | y | d2
TN_2018_1064 |  |  | 432933E | FIRS2.0 ST¦F0M2-48FO (10452) | 9.55 | 15 | Vilanova | 1602SEES | CD | 49.5 | 25.1 | No | 2018-06-19 | B2_s1_d2 | 0.62 | 4 | 11.4 | 564 | 43.1 | B2 | 1.8 | 0.01 | s1 | n | y | d2
TN_2018_1065 |  |  | 361362K | ALPAM2.0 ST¦N0F0M2-96FO (10361) | 12.1 | 13 | Vilanova | 1602SEES | CD | 46.6 | 26.1 | No | 2018-06-16 | C_s2_d2 | 1.15 | 22.2 | 42.4 | 1071 | 55 | C | 50.3 | 0.12 | s2 | n | y | d2
TN_2018_1066 |  |  | 430793D | FIRS2.0 ST¦F0M2-96FO (10452) | 11 | 14 | Vilanova | 1602SEES | CD | 45.3 | 27.1 | No | 2018-06-19 | B2_s1_d2 | 0.76 | 11.3 | 13.1 | 627 | 52 | B2 | 12.5 | 0.03 | s1 | n | y | d2
TN_2018_1067 |  | OP67503 20258703 | 457365L | EATST 14X4X0.9 B2CA | 28.25 | 6 | Vilanova | HDPE+LANTOR+1602SEES | CD | 61.4 | 22.1 | No | 2018-06-20 | B2_s1_d2 | 0.52 | 6.2 | 16 | 1491 | 14.9 | B2 | 6.5 | 0.03 | s1 | n | y | d2
TN_2018_1068 |  |  |  | RG16H1M16 12/20KV 1X25 | 27.19 | 6 | Vilanova | SCAPA+0400FEIT+5300SEIT | CD | 59.7 | 22.9 | No | 2018-06-20 | B2_s1_d2 | 0.57 | 5.5 | 10.8 | 1497 | 16.5 | B2 | 2.9 | 0.01 | s1 | n | y | d2
TN_2018_1069 |  | 67502 20258679 | 449730M | EATST 4X1.4 B2CA | 15.94 | 9 | Vilanova | HDPE+LANTOR+1602SEES | CD | 52 | 25.8 | No | 2018-06-22 | C_s1_d2 | 0.78 | 18.4 | 29.6 | 1119 | 37.8 | C | 17.4 | 0.04 | s1 | n | y | d2
TN_2018_1070 |  | 67504 20258714 | 455127D | EATST 10X4X1.4 B2CA | 35.58 | 5 | Vilanova | HDPE+LANTOR+1602SEES | CD | 51.4 | 27 | No | 2018-06-20 | B2_s1_d2 | 0.39 | 5.9 | 8.8 | 1179 | 23.3 | B2 | 6 | 0.01 | s1 | n | y | d2
TN_2018_1071 |  |  | 453026V | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.33 | 8 | Vilanova | XLPE+COPPERTAPE50%+MICATAPE50%+LANTORLONGITUDINAL+1602SEES | CD | 50.6 | 27.6 | No | 2018-06-20 | E ou F_s2_d2 | 3.3 | 79 | 219.6 | 1500 | 183 | E ou F | 69.4 | 0.19 | s2 | n | y | d2
18060011 |  | 17330 | -- | RED ELEC RHZ1-RA-2OL (AS) 1X2000MM2 127/220KV +T375AL | 122 | 2 | Paron | XLPE+TUBEAL+60ACESNATUREL+SKINSC | -- | 57.4 | 24.2 | No | 2018-06-21 | B2_s1_d2 | 0.9 | 7 | 10.5 | 909 | 23 | B2 | 14 | 0.02 | s1 | y | y | d2
18060012 |  | 17317 | 416073D | AFUMEX RZ1FA3Z1-K 1KV ADIF 1X300 | 33.6 | 5 | Paron | PENDINGTOCONFIRM | -- | 58.3 | 24.2 | No | 2018-06-21 | B2_s1_d2 | 0.6 | 7.6 | 10.2 | 1494 | 28 | B2 | 16 | 0.03 | s1 | y | y | d2
18060013 |  | 17317 | 402679V | AL AFUMEX RZ1FA3Z1-K 1KV ADIF 2X16 | 20.82 | 7 | Paron | LLDPE+6000SEES | -- | 58.2 | 26.5 | No | 2018-06-21 | D_s2_d2 | 1.85 | 27.1 | 93.4 | 1500 | 78 | D | 52 | 0.2 | s2 | y | y | d2
18060014 |  | 17317 | 417024M | AFUMEX RZ1FA3Z1-K 1KV ADIF 3X1.5 | 13.78 | 11 | Paron | LLDPE+6000SEES | -- | 43.4 | 23.5 | No | 2018-06-21 | E ou F_s2_d2 | 3.3 | 80.1 | 208 | 1500 | 173 | E ou F | 64 | 0.14 | s2 | y | y | d2
18060015 |  | 17347 | -- | K25 750V 1X1 -SH-NF F 55-625-255 | 3.1 | 150 | Paron | 1602SEES | -- | 44.2 | 24 | No | 2018-06-28 | B2_s2_d1 | 1.2 | 13.7 | 27.6 | 657 | 108 | B2 | 77 | 0.19 | s2 | y | n | d1
TN_2018_1072 |  | OP67391 20261851 | 425888X | AFUMEX CLASS RZ1-K (AS) 1KV 19X2.5 | 20.52 | 7 | Vilanova | GFR325+1602SEES | CD | 58.9 | 26.5 | No | 2018-06-22 | B2_s1_d0 | 0.56 | 11.6 | 22.9 | 1491 | 27.3 | B2 | 19.1 | 0.03 | s1 | n | n | d0
TN_2018_1073 |  |  | T8 E69136 | PRYSMIAN (P) 20234123 804515 16X1 | 23.55 | 7 | Vilanova | ID2900INSULATION+SD3500ITFILLER+SV3400ITINNERSHEATH+STEELTAPE+5300SEITSHEATH | CD | 62.5 | 27.7 | No | 2018-06-22 | C_s2_d2 | 0.8 | 19.4 | 34.5 | 1269 | 41.5 | C | 50.2 | 0.12 | s2 | n | y | d2
TN_2018_1074 |  | OP67389 20261839 | 389186D | AFUMEX CLASS RZ1-K (AS) 1KV 8X2.5 | 15.48 | 10 | Vilanova | GFR325+1602SEES | CD | 61.1 | 28.7 | No | 2018-06-22 | B2_s1_d2 | 0.84 | 14.9 | 26.6 | 1290 | 28.4 | B2 | 10.5 | 0.07 | s1 | n | y | d2
TN_2018_1075 |  | OP67390 20261840 | 256939G | AFUMEX CLASS RZ1-K (AS) 1KV 19X1 | 17.41 | 9 | Vilanova | GFR325+1602SEES | CD | 57.1 | 25 | No | 2018-06-25 | B2_s1_d0 | 0.77 | 11.4 | 22.7 | 1479 | 26.8 | B2 | 0.7 | 0.01 | s1 | n | n | d0
TN_2018_1076 |  | 82465124 | 460759A | AFUMEX CLASS ATEX RZ1MZ1-K (AS) 1KV 3G2.5 | 14.6 | 10 | Vilanova | XLPE+1602SEES+ARMOUR+LONGITUDINALTAPE+1602SEES | CD | 50.9 | 26.1 | No | 2018-06-25 | B2_s1_d2 | 0.76 | 12.3 | 19.9 | 1173 | 26.2 | B2 | 1.6 | 0.01 | s1 | n | y | d2
TN_2018_1077 |  |  | T0 E71965 | PRYSMIAN (P) 120235049 BOA SCMT 1X2X0.9 5300 | 9.97 | 15 | Vilanova | BP28D780+PET+PP+PE+ACC+PE+5300WITHOUTTAPE | CD | 43.7 | 27.1 | No | 2018-06-25 | C_s1_d2 | 1.25 | 18.5 | 40 | 717 | 95.9 | C | 23.6 | 0.05 | s1 | n | y | d2
TN_2018_1078 |  | OP68342 20231931 | 466799R | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K (AS+) 1KV 20X2.5 | 30.73 | 6 | Vilanova | 1602SEES+ARMOUR+GFR380 | CD | 56.7 | 25.6 | No | 2018-06-26 | B2_s1_d0 | 0.55 | 5.6 | 7.2 | 882 | 16 | B2 | 15.6 | 0.02 | s1 | n | n | d0
TN_2018_1079 |  |  | T0 E71965 | PRYSMIAN (P) 120235049 BOA SCMT 1X2X0.9 5300 | 10.32 | 15 | Vilanova | BP28D780+PET+PP+PE+ACC+PE+5300WITHTAPE | CD | 54.3 | 26.8 | No | 2018-06-26 | B2_s1_d2 | 0.87 | 13.4 | 29.8 | 663 | 83 | B2 | 13.3 | 0.03 | s1 | n | y | d2
TN_2018_1080 |  |  |  | CÂBLE 96FO (12X8) TKEST DRY | 24.48 | 7 | Vilanova | 1700SEES+1602SEES | OD | 54 | 27.8 | No | 2018-06-26 | C_s1_d2 | 0.85 | 15.2 | 20.6 | 1224 | 33.3 | C | 29 | 0.05 | s1 | n | y | d2
TN_2018_1081 |  | OP68343 20259574 | 466797N | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K (AS) 1KV 2X2.5 | 14.94 | 10 | Vilanova | 1602SEES+ARMOUR+GFR380 | CD | 70.9 | 24.3 | No | 2018-06-28 | C_s1_d0 | 0.79 | 17.5 | 22.5 | 1290 | 41 | C | 16.2 | 0.02 | s1 | n | n | d0
TN_2018_1082 |  | OP67390 20261840 | 256939G | AFUMEX CLASS RZ1-K (AS) 1KV 19X1 | 17.41 | 9 | Vilanova | GFR325+1602SEES | CD | 70.2 | 24.7 | No | 2018-06-28 | B2_s1_d0 | 0.76 | 9 | 17.6 | 1500 | 21 | B2 | 0 | 0 | s1 | n | n | d0
TN_2018_1083 |  | OP67391 20261851 | 425888X | AFUMEX CLASS RZ1-K (AS) 1KV 19X2.5 | 20.52 | 7 | Vilanova | GFR325+1602SEES | CD | 63.8 | 26.7 | No | 2018-06-28 | B2_s1_d0 | 0.35 | 4.2 | 5.7 | 624 | 17.6 | B2 | 0.9 | 0 | s1 | n | n | d0
TN_2018_1084 |  | OP67389 20261839 | 389186D | AFUMEX CLASS RZ1-K (AS) 1KV 8X2.5 | 15.48 | 10 | Vilanova | GFR325+1602SEES | CD | 59.9 | 28.1 | No | 2018-06-28 | B2_s1_d1 | 0.78 | 15 | 21.9 | 1332 | 42.3 | B2 | 7.5 | 0.02 | s1 | y | n | d1
TN_2018_1085 |  | OP67913 20261708 | 464920Y | RHOZ1MZ1-K 500V 1X2X1.5 | 12.47 | 13 | Vilanova | 1602SEES+ARMOUR+GFR380 | CD | 57.5 | 29.2 | No | 2018-06-28 | B2_s1_d2 | 0.69 | 9.5 | 16.2 | 936 | 35.6 | B2 | 15.6 | 0.03 | s1 | n | y | d2
18070001 |  | 17346 | -- | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.77 | 180 | Paron | 1602SEES | -- | 68 | 24.5 | No | 2018-07-03 | B2_s1_d0 | 0.74 | 7.1 | 14.2 | 621 | 60 | B2 | 13 | 0.03 | s1 | n | n | d0
18070002 |  | 17356 | -- | DRAKA 2018 32FO 10D KT MOVISTAR | 13.3 | 12 | Paron | MEGOLONS548 | -- | 60.9 | 25.1 | No | 2018-07-04 | E ou F_s2_d2 | 3.3 | 117.1 | 234.8 | 1218 | 262 | E ou F | 237 | 0.67 | s2 | y | y | d2
18070003 |  | 17356 | -- | DRAKA 2018 16FO 10D KT MOVISTAR | 11.8 | 13 | Paron | MEGOLONS548 | -- | 60.2 | 26.8 | No | 2018-07-04 | E ou F_s2_d2 | 3.3 | 81.9 | 134.2 | 1296 | 140 | E ou F | 108 | 0.21 | s2 | y | y | d2
TN_2018_1086 |  | OP67917 20267203 | 453471D | RHOZ1MZ1-K 500V 10X3X1.5 | 30.64 | 6 | Vilanova | 1602SEES+ARMOURED+GFR380 | CD | 71.3 | 26.6 | No | 2018-07-02 | B2_s1_d2 | 0.62 | 6.2 | 10.6 | 1266 | 23.4 | B2 | 8.7 | 0.01 | s1 | n | y | d2
TN_2018_1087 |  | OP67915 20261712 | 450768R | RHOZ1MZ1-K 500V 20X3X1.5 | 42.22 | 6 | Vilanova | 1602SEES+ARMOURED+GFR380 | CD | 70.2 | 27.1 | No | 2018-07-02 | B2_s1_d1 | 0.7 | 9.3 | 13.8 | 1467 | 26 | B2 | 3.8 | 0.01 | s1 | y | n | d1
TN_2018_1088 |  | OP67914 20261711 | 450769S | RHOZ1MZ1-K 500V 20X2X1.5 | 37.93 | 5 | Vilanova | 1602SEES+ARMOURED+GFR380 | CD | 53.9 | 28.4 | No | 2018-07-02 | B2_s1_d1 | 0.63 | 6.6 | 10.4 | 1368 | 22.2 | B2 | 11.6 | 0.02 | s1 | y | n | d1
TN_2018_1089 |  | OP67916 20267202 | 414896Z | RHOZ1MZ1-K 500V 6X3X1.5 | 26.64 | 6 | Vilanova | 1602SEES+ARMOURED+GFR380 | CD | 74.6 | 24.6 | No | 2018-07-03 | B2_s1_d2 | 0.44 | 14 | 24.7 | 1500 | 30.4 | B2 | 8.2 | 0.02 | s1 | n | y | d2
TN_2018_1090 |  | OP66972 | 461062E | FG16OM16 3G1.5 MM² - 0.6/1 KV | 11.15 | 14 | Vilanova | PAPER+03AAFDIT+5300SEIT | CD | 74.7 | 24.5 | No | 2018-07-03 | B2_s1_d1 | 0.47 | 9 | 17.9 | 804 | 41.3 | B2 | 2.7 | 0.01 | s1 | y | n | d1
TN_2018_1091 |  | OP66972 | 461086F | FG16OM16 3G1.5 MM² - 0.6/1 KV | 11.05 | 14 | Vilanova | CARTA+04AMFEIT+5300SEIT | CD | 68.1 | 26.9 | No | 2018-07-03 | B2_s1_d2 | 0.55 | 10.4 | 19.5 | 804 | 49.7 | B2 | 12.6 | 0.02 | s1 | n | y | d2
TN_2018_1092 |  | OP67989 20267728 | 450493S | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K RH 24X1.5 | 30.4 | 6 | Vilanova | 1602SEES+ARMOURED+GFR380 | CD | 63.5 | 29.5 | No | 2018-07-03 | B2_s1_d2 | 0.54 | 10.1 | 20.7 | 1500 | 31.2 | B2 | 5.6 | 0.02 | s1 | n | y | d2
TN_2018_1093 |  | OP66973 | 461067K | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.84 | 11 | Vilanova | PAPER+03AAFDIT+5300SEIT | CD | 55.1 | 24.3 | No | 2018-07-06 | B2_s1_d1 | 0.55 | 12.6 | 23.2 | 1002 | 37 | B2 | 13.9 | 0.03 | s1 | y | n | d1
TN_2018_1094 |  | OP66974 | 461068L | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.46 | 12 | Vilanova | VILEDONK3452+03AAFDIT+5300SEIT | CD | 48.5 | 26 | No | 2018-07-06 | B2_s1_d2 | 0.72 | 12.1 | 21.5 | 1056 | 39.4 | B2 | 8.2 | 0.02 | s1 | n | y | d2
TN_2018_1095 |  | OP66973 | 461060C | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.53 | 11 | Vilanova | CARTA+04AMFEIT+5300SEIT | CD | 42.2 | 27.8 | No | 2018-07-06 | C_s1_d2 | 0.84 | 18.3 | 30.2 | 1050 | 47.4 | C | 22.8 | 0.06 | s1 | n | y | d2
18070004 |  | 17347 | -- | K25 750V 1X1 -SH-NF F 55-625-255 | 3.1 | 150 | Paron | 1602SEES | -- | 55.1 | 24.1 | No | 2018-07-10 | C_s2_d0 | 1.2 | 14.2 | 30.4 | 648 | 110 | C | 60 | 0.22 | s2 | n | n | d0
18070005 |  | 17367 | -- | RED ELEC RHZ1-RA-2OL(AS) 1X630MM2 127/220KV | 101 | 2 | Paron | XLPE+TUBEAL+60ACESNATUREL+SKINSC | -- | 52.2 | 22.5 | No | 2018-07-12 | B2_s1_d2 | 0.8 | 8.6 | 11.3 | 879 | 26 | B2 | 5 | 0.01 | s1 | y | y | d2
18070006 |  | 17347 | -- | K25 750V 1X1 -SH-NF F 55-625-255 ( IRRADIÉ) | 3.1 | 150 | Paron | 1602SEES | -- | 52.6 | 22.5 | No | 2018-07-12 | D_s2_d0 | 2.6 | 29.1 | 52.3 | 639 | 172 | D | 80 | 0.15 | s2 | n | n | d0
TN_2018_1096 |  | OP66795 | 461073S | FG16OM16 3G10 MM² - 0.6/1 KV | 17.03 | 9 | Vilanova | 5300SEIT+04AMFEIT+VILEDONK3452 | CD | 63.7 | 24.8 | No | 2018-07-10 | B2_s1_d2 | 0.71 | 9.6 | 20.4 | 1497 | 30.3 | B2 | 4.2 | 0.01 | s1 | n | y | d2
TN_2018_1097 |  | OP66794 | 461070N | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.97 | 11 | Vilanova | 5300SEIT+04AMFEIT+VILEDONK3452 | CD | 65.8 | 25.3 | No | 2018-07-10 | C_s1_d2 | 0.78 | 18.2 | 29.1 | 1143 | 41.4 | C | 12.7 | 0.02 | s1 | n | y | d2
TN_2018_1098 |  | OP66795 | 461057Z | FG16OM16 3G10 MM² - 0.6/1 KV | 16.94 | 9 | Vilanova | 5300SEIT+03AAFDIT+VILEDONK3452 | CD | 50.6 | 27.9 | No | 2018-07-10 | B2_s1_d2 | 0.52 | 5.7 | 11.7 | 1470 | 20.7 | B2 | 1.4 | 0 | s1 | n | y | d2
TN_2018_1099 |  | 82500454 20232383 | 462199R | HEPEHZ1F3Z1-OLC(AS) 3X50MM² 10KV | 47.83 | 4 | Vilanova | INS:ID71AAIT+INNERSHEATH1420SEES+1602SEES+LANTOR+SHEATH1602SEES | CD | 56.2 | 30.2 | No | 2018-07-10 | B2_s1_d2 | 0.58 | 6.9 | 10.3 | 888 | 19.5 | B2 | 0 | 0 | s1 | n | y | d2
TN_2018_1100 |  |  |  | CÂBLE 96FO (12X8) TKEST DRY | 24.86 | 7 | Vilanova | PENDINGTOCONFIRM | OD | 72.2 | 24.6 | No | 2018-07-11 | C_s1_d1 | 0.76 | 25 | 40.2 | 1431 | 42.7 | C | 31.5 | 0.05 | s1 | y | n | d1
TN_2018_1101 |  |  |  | DRAKA 2018 16FO D KT MOVISTAR 278785 | 11.65 | 13 | Vilanova | PENDINGTOCONFIRM | OD | 59.2 | 26.9 | No | 2018-07-11 | D_s2_d1 | 3.3 | 67.9 | 115.2 | 1389 | 113.4 | D | 117.4 | 0.23 | s2 | y | n | d1
TN_2018_1102 |  |  |  | 24 TKEST DRY | 17.8 | 8 | Vilanova | PENDINGTOCONFIRM | OD | 57.7 | 27.5 | No | 2018-07-11 | B2_s1_d0 | 0.75 | 13.8 | 20.1 | 1407 | 32.9 | B2 | 10.4 | 0.04 | s1 | n | n | d0
TN_2018_1103 |  |  |  | DRAKA 2018 32FO 10D KT MOVISTAR 378785 | 13.41 | 12 | Vilanova | PENDINGTOCONFIRM | OD | 53.4 | 28.5 | No | 2018-07-11 | E ou F_s2_d2 | 3.3 | 117.3 | 227.7 | 1335 | 220 | E ou F | 151.2 | 0.3 | s2 | n | y | d2
18070007 |  | 17369 | -- | AFUMEX TECNUC-PESS-926-PRYSMIAN 255-12P1.00MM²- CU CI5-BLG- LSOH-03/0.5(0.6)-CST 74.C.068-K3 | 22.5 | 7 | Paron |  | -- | 48 | 23.8 | No | 2018-07-12 | B2_s1_d0 | 0.25 | 2.7 | 4 | 663 | 12 | B2 | 5 | 0.01 | s1 | n | n | d0
18070008 |  | 17365 | -- | K25 750V 1X4.0 -SH-NF F 55-625-255 ( IRRADIÉ) | 3.84 | 90 | Paron | 1602SEES | -- | 53.3 | 25.6 | No | 2018-07-16 | B2_s1_d0 | 0.6 | 6.1 | 15.1 | 669 | 58 | B2 | 10 | 0.04 | s1 | n | n | d0
18070009 |  | 17365 | -- | K25 750V 1X2.5-SH-NF F 55-625-255 ( IRRADIÉ) | 3.84 | 90 | Paron | 1602SEES | -- | 57 | 26.3 | No | 2018-07-16 | B2_s1_d0 | 0.6 | 3.6 | 10.2 | 639 | 41 | B2 | 5 | 0.01 | s1 | n | n | d0
18070010 |  | 17356 | -- | 32FO 8X4 KT FILLED ( PROTO Nº 32) | 13.8 | 11 | Paron | MEGOLONS548 | -- | 50 | 25.1 | No | 2018-07-17 | E ou F_s2_d2 | 3.3 | 109.5 | 205 | 1245 | 220 | E ou F | 231 | 0.62 | s2 | y | y | d2
18070011 |  | 17356 | -- | 16FO 4X4 KT FILLED ( PROTO Nº 33) | 12 | 13 | Paron | MEGOLONS548 | -- | 44 | 26.1 | No | 2018-07-17 | D_s2_d2 | 3.3 | 66.6 | 108.1 | 1500 | 109 | D | 98 | 0.18 | s2 | y | y | d2
18070012 |  | 17368 | -- | K209 ΜGAINE 6 FO M6 (SILEC) | 13 | 12 | Paron | VPE913+RUBANPOLY+FRP+TPR248+RUBANACIER+TPS246 | -- | 40.9 | 26.9 | No | 2018-07-17 | B2_s1_d1 | 0.4 | 7.4 | 15.4 | 1002 | 28 | B2 | 15 | 0.03 | s1 | y | n | d1
18070013 |  | 17365 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 ( IRRADIÉ) | 3.1 | 150 | Paron | 1602SEES | -- | 44.4 | 25 | No | 2018-07-19 | B2_s1_d0 | 0.9 | 9.2 | 21.8 | 804 | 52 | B2 | 19 | 0.07 | s1 | n | n | d0
18070014 |  | 17369 | -- | AFUMEX TECNUC-PK3CB384-PRYSMIAN 255-19*1.5- CU C I2-BLG- LSOH-0.3/0.5(0.6)-CST | 19.4 | 8 | Paron | IX2200+3100GV+SW3100 | -- | 44.8 | 25.2 | No | 2018-07-19 | B2_s1_d1 | 0.5 | 6.1 | 15.7 | 1494 | 13 | B2 | 18 | 0.05 | s1 | y | n | d1
18070015 |  | 17369 | -- | AFUMEX TECNUC-PK3PS794-PRYSMIAN 255-12P1.00MM²- CU CI5-BLG- LSOH-0.3/0.5(0.6)-CST | 23 | 7 | Paron | IX2200+3100GV+SW3100 | -- | 42.7 | 26.1 | No | 2018-07-19 | B2_s1_d0 | 0.5 | 2.8 | 6.5 | 1500 | 7 | B2 | 13 | 0.04 | s1 | n | n | d0
18070016 |  | 17369 | -- | AFUMEX TECNUC-PK3CB384-PRYSMIAN 255-3*35- CU C I2-BLG- LSOH-0.6/1(1.2)-CST | 23.5 | 7 | Paron | IX2200+3100GV+SW3100 | -- | 37.5 | 27.9 | No | 2018-07-19 | B2_s1_d0 | 0.5 | 3.6 | 5.3 | 1479 | 9 | B2 | 10 | 0.01 | s1 | n | n | d0
TN_2018_1104 |  | 82586500 20215936 | 10 - G79542 | FG16OM16 24G1.5 MM² - 0.6/1 KV | 22.32 | 7 | Vilanova | S-XLPE+LANTORTAPE+03AAFDIT+5300FEIT | CD | 53.7 | 23.8 | No | 2018-07-13 | B2_s1_d2 | 0.59 | 7.1 | 17.4 | 1497 | 23.4 | B2 | 2.8 | 0.01 | s1 | n | y | d2
TN_2018_1105 |  | 68106 20267289 | 07 - D37343 | FG16OM16 4X1.5 MM² - 0.6/1 KV | 11.7 | 13 | Vilanova | SXLPE+03AAFDIT+5300SEIT | CD | 51.9 | 24.7 | No | 2018-07-13 | C_s1_d1 | 1.12 | 17.1 | 26.1 | 1005 | 38.3 | C | 16.3 | 0.03 | s1 | y | n | d1
TN_2018_1106 |  | 68105 20167290 | 07 - D36293 | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.36 | 12 | Vilanova | SXLPE+03AAFDIT+5300SEIT | CD | 47.8 | 27.5 | No | 2018-07-13 | B2_s1_d2 | 0.88 | 14.5 | 21.2 | 984 | 40.4 | B2 | 13.6 | 0.03 | s1 | n | y | d2
TN_2018_1107 |  | 68107 20267288 | 08 - G70498 | FG16OM16 3X1.5 MM² - 0.6/1 KV | 10.28 | 15 | Vilanova | SXLPE+03AAFDIT+5300SEIT | CD | 43.4 | 29.2 | No | 2018-07-13 | C_s1_d1 | 1.42 | 23.5 | 32.9 | 945 | 73.1 | C | 36.1 | 0.06 | s1 | y | n | d1
TN_2018_1108 |  | 68104 20268114 | 08 - F71250 | FS18OR18 3G1.5 500V | 6.66 | 21 | Vilanova | 2200IPITINSULATION+05ABFPITASFILLER+2000SPIT | CD | 41.3 | 30.3 | No | 2018-07-13 | B2_s2_d0 | 0.71 | 2.6 | 8.1 | 435 | 62.2 | B2 | 69 | 0.4 | s2 | n | n | d0
TN_2018_1109 |  | OP68343 20259574 | 466797N | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K (AS) 1KV 2X2.5 | 14.94 | 10 | Vilanova | 1602SEES+ARMOUR+GFR380 | OD | 50.1 | 26.2 | No | 2018-07-17 | B2_s1_d2 | 0.78 | 13.2 | 20.1 | 1203 | 27.2 | B2 | 25.4 | 0.06 | s1 | n | y | d2
TN_2018_1110 |  | OP68342 20231931 | 466799R | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K (AS+) 1KV 20X2.5 | 30.73 | 6 | Vilanova | 1602SEES+ARMOUR+GFR380 | OD | 54.2 | 28.1 | No | 2018-07-17 | B2_s1_d0 | 0.55 | 6.8 | 10.5 | 1461 | 20.2 | B2 | 20.6 | 0.03 | s1 | n | n | d0
TN_2018_1111 |  | OP67390 20261840 | 256939G | AFUMEX CLASS RZ1-K (AS) 1KV 19X1 | 17.41 | 9 | Vilanova | GFR325+1602SEES | OD | 55.3 | 28.9 | No | 2018-07-17 | C_s1_d0 | 0.75 | 16.5 | 30.3 | 1479 | 43.1 | C | 3.8 | 0.01 | s1 | n | n | d0
TN_2018_1112 |  | OP67391 20261851 | 425888X | AFUMEX CLASS RZ1-K (AS) 1KV 19X2.5 | 20.52 | 7 | Vilanova | GFR325+1602SEES | OD | 54.6 | 29.6 | No | 2018-07-17 | B2_s1_d0 | 0.44 | 5.7 | 8.7 | 1461 | 19.8 | B2 | 3.7 | 0.01 | s1 | n | n | d0
TN_2018_1113 |  | OP67389 20261839 | 389186D | AFUMEX CLASS RZ1-K (AS) 1KV 8X2.5 | 15.48 | 10 | Vilanova | GFR325+1602SEES | OD | 56.4 | 26.7 | No | 2018-07-18 | B2_s1_d0 | 0.57 | 9.4 | 18 | 1416 | 23.7 | B2 | 23.9 | 0.03 | s1 | n | n | d0
TN_2018_1114 |  | OP68343 20259574 | 466797N | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K (AS) 1KV 2X2.5 | 14.94 | 10 | Vilanova | 1602SEES+ARMOUR+GFR380 | OD | 62.2 | 27.8 | No | 2018-07-18 | C_s1_d0 | 0.77 | 21.6 | 29.1 | 1080 | 47.7 | C | 23 | 0.04 | s1 | n | n | d0
TN_2018_1115 |  | 82500454 20232383 | 462199R | HEPEHZ1F3Z1-OLC(AS) 3X50MM² 10KV | 47.83 | 4 | Vilanova | INS:ID71AAIT+INNERSHEATH1420SEES+1602SEES+LANTOR+SHEATH1602SEES | OD | 70 | 26.5 | No | 2018-07-19 | B2_s1_d2 | 0.54 | 7.6 | 12.4 | 849 | 22.5 | B2 | 9 | 0.02 | s1 | n | y | d2
TN_2018_1116 |  | 82609367 | -- | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.59 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 64.9 | 26.3 | No | 2018-07-20 | D_s2_d2 | 2.07 | 30 | 40.9 | 1239 | 70.1 | D | 55.6 | 0.09 | s2 | y | y | d2
TN_2018_1117 |  | 82537659 | -- | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.04 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 50.2 | 28.1 | No | 2018-07-20 | D_s1_d2 | 3.3 | 55.6 | 141.8 | 1500 | 118.2 | D | 36.1 | 0.06 | s1 | y | y | d2
TN_2018_1118 |  | 68406 20226650 | 467684C | AFUMEX CLASS 1KV Z1Z1-K (AS) 14X1.5MM2 | 17.08 | 9 | Vilanova | INS:CPRSHEATHAFUMEX100082355+PAPER+SHEATH20ALSEES1000053456 | CD | 55.6 | 30 | No | 2018-07-20 | B2_s1_d1 | 0.87 | 13.2 | 18 | 1341 | 27.2 | B2 | 19.8 | 0.04 | s1 | y | n | d1
TN_2018_1119 |  | 68408 20226649 | 467748X | AFUMEX CLASS 1KV Z1Z1-K (AS) 24X1.5MM2 | 22 | 7 | Vilanova | INS:CPRSHEATHAFUMEX100082355+PAPER+SHEATH20ALSEES1000053456 | CD | 58.5 | 25 | No | 2018-07-22 | C_s1_d2 | 0.84 | 20.1 | 26.1 | 951 | 47.5 | C | 12 | 0.02 | s1 | n | y | d2
TN_2018_1120 |  | 68407 20226647 | 470375C | AFUMEX CLASS 1KV Z1Z1-K (AS) 16X2.5MM2 | 20.77 | 7 | Vilanova | INS:CPRSHEATHAFUMEX100082355+PAPER+SHEATH20ALSEES1000053456 | CD | 70.2 | 25.2 | No | 2018-07-22 | B2_s1_d2 | 0.55 | 8 | 10.6 | 846 | 21.4 | B2 | 0 | 0 | s1 | n | y | d2
TN_2018_1121 |  | 68108 20268115 | 07 - F83984 | FS18OR18 3G1.5 500V | 6.79 | 21 | Vilanova | 2200IPITINSULATION+0800FPITASFILLER+2100SPIT | CD | 59.3 | 26.4 | No | 2018-07-22 | B2_s2_d0 | 0.74 | 3.1 | 10.2 | 864 | 25.6 | B2 | 95.5 | 0.5 | s2 | n | n | d0
18070017 |  | 17378 | -- | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.24 | 13 | Paron | SXLPE+1420FEES+1602SEES | -- | 61.1 | 25.1 | No | 2018-07-25 | D_s1_d2 | 2.1 | 30.7 | 43.5 | 1185 | 65 | D | 41 | 0.09 | s1 | y | y | d2
18070018 |  | 17378 | -- | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.84 | 14 | Paron | SXLPE+1420FEES+1602SEES | -- | 58.5 | 26 | No | 2018-07-25 | C_s2_d2 | 1.9 | 26.2 | 38.1 | 873 | 68 | C | 71 | 0.21 | s2 | y | y | d2
18070044 |  |  | -- | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.6 | 14 | Manlleu | SXLPE+1420FEES+1602SEES | -- | 48 | 25 | No | 2018-07-26 | C_s1_d0 | 1.37 | 20 | 25.5 | 978 | 56.7 | C | 30.9 | 0.1 | s1 | n | n | d0
18070045 |  |  | -- | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11.8 | 13 | Manlleu | SXLPE+1420FEES+1602SEES | -- | 48 | 25.1 | No | 2018-07-26 | C_s1_d1 | 1.46 | 25.4 | 33.1 | 1299 | 57 | C | 24.6 | 0.06 | s1 | y | n | d1
18070019 |  | 17394 | -- | EUROTUNNEL COAX 1X630 CU 25KV | 74.5 | 3 | Paron | :ISHTPS218+ANTIFONGIQUEINTERCIDEOBF10SPCDEKRAHNFRANCE | -- | 57.7 | 27.2 | No | 2018-07-27 | B2_s1_d0 | 0.46 | 4 | 6 | 1050 | 8.8 | B2 | 8.6 | 0.01 | s1 | n | n | d0
18070020 |  | 17388 | -- | CÂBLE L1082-1 (FO) | 4.05 | 75 | Paron | 1700SEES+ECCOH5702 | -- | 52.1 | 28.8 | No | 2018-07-27 | D_s1_d1 | 3.3 | 34.9 | 51.6 | 774 | 122 | D | 40 | 0.06 | s1 | y | n | d1
TN_2018_1122 |  | OP68414 20234256 | 249673J | AFUMEX CLASS O 1Z1C7Z1-K 1KV 37X1 | 29.76 | 6 | Vilanova | INS:CPRSHEATHAFUMEX100082355;INNER:CPRSHEATHAFUMEX100082355;LANTORLONGITUDINALTAPE;OUTERSHEATH20ALSEES1000053456 | CD | 68.8 | 23.8 | No | 2018-07-25 | C_s1_d2 | 0.78 | 14.1 | 30.5 | 1482 | 25.8 | C | 4.1 | 0.02 | s1 | n | y | d2
TN_2018_1123 |  | OP68415 20265344 | 467716M | AFUMEX CLASS O 1Z1C7Z1-K 1KV 37X2.5 | 35.19 | 5 | Vilanova | INS:CPRSHEATHAFUMEX100082355;INNER:CPRSHEATHAFUMEX100082355;LANTORLONGITUDINALTAPE;OUTERSHEATH20ALSEES1000053456 | CD | 55.9 | 24.8 | No | 2018-07-25 | B2_s1_d2 | 0.7 | 10.5 | 21.7 | 1500 | 21.1 | B2 | 1 | 0.01 | s1 | n | y | d2
TN_2018_1124 |  | OP68413 20234257 | 445412U | AFUMEX CLASS O 1Z1C7Z1-K 1KV 2X16 | 20.01 | 8 | Vilanova | INS:CPRSHEATHAFUMEX100082355;INNER:CPRSHEATHAFUMEX100082355;LANTORLONGITUDINALTAPE;OUTERSHEATH20ALSEES1000053456 | CD | 60 | 26.8 | No | 2018-07-25 | C_s1_d2 | 1.61 | 28.5 | 51.3 | 1416 | 51.4 | C | 18.4 | 0.04 | s1 | n | y | d2
TN_2018_1125 |  | OP68412 20234258 | 465226F | AFUMEX CLASS O 1Z1C7Z1-K 1KV 14X1 | 19.86 | 8 | Vilanova | INS:CPRSHEATHAFUMEX100082355;INNER:CPRSHEATHAFUMEX100082355;LANTORLONGITUDINALTAPE;OUTERSHEATH20ALSEES1000053456 | CD | 54.5 | 27.9 | No | 2018-07-25 | C_s1_d2 | 1.2 | 26 | 43.8 | 1479 | 47.7 | C | 15.9 | 0.06 | s1 | n | y | d2
TN_2018_1126 |  | OP67913 20261708 | 464920Y | RHOZ1MZ1-K 500V 1X2X1.5 | 12.47 | 13 | Vilanova | 1602SEES+ARMOUR+GFR380 | CD | 45.1 | 29.9 | No | 2018-07-25 | B2_s1_d1 | 0.52 | 6.4 | 11.9 | 810 | 25.3 | B2 | 4.5 | 0.01 | s1 | y | n | d1
TN_2018_1127 |  | OP67916 20267202 | 414896Z | RHOZ1MZ1-K 500V 6X3X1.5 | 26.64 | 6 | Vilanova | 1602SEES+ARMOURED+GFR380 | CD | 47.4 | 26.8 | No | 2018-07-26 | B2_s1_d2 | 0.56 | 10.3 | 24.3 | 1491 | 21.2 | B2 | 8.6 | 0.05 | s1 | n | y | d2
TN_2018_1128 |  | OP67917 20267203 | 453471D | RHOZ1MZ1-K 500V 10X3X1.5 | 30.64 | 6 | Vilanova | 1602SEES+ARMOURED+GFR380 | CD | 42.2 | 28.5 | No | 2018-07-26 | B2_s1_d1 | 0.54 | 5.9 | 8.7 | 1380 | 15.1 | B2 | 15.6 | 0.02 | s1 | y | n | d1
TN_2018_1129 |  | OP68409 20229627 | 467749Y | AFUMEX CLASS 1KV Z1Z1-K (AS) 24X2.5MM2 | 24.86 | 7 | Vilanova | INS:CPRSHEATHAFUMEX100082355+PAPER+SHEATH20ALSEES1000053456 | CD | 39.9 | 30.1 | No | 2018-07-26 | B2_s1_d2 | 0.88 | 13.6 | 18.4 | 1179 | 27.7 | B2 | 13.9 | 0.05 | s1 | n | y | d2
TN_2018_1130 |  | 20270853 | T8-F71107 | FG16M16 1X10 MM² - 0.6/1 KV | 9.66 | 15 | Vilanova | S-XLPE+TNT+03ACFDIT+5300SEIT | CD | 35.8 | 31.4 | No | 2018-07-26 | B2_s1_d1 | 0.83 | 11.9 | 20.8 | 864 | 45.5 | B2 | 18 | 0.04 | s1 | y | n | d1
TN_2018_1131 |  | 20270854 | T8-F71115 | FG16OM16 3G1.5 MM² - 0.6/1 KV | 11 | 14 | Vilanova | S-XLPE+TALCUM+03ACFDIT+5300SEIT | CD | 70.5 | 24.5 | No | 2018-07-27 | C_s1_d2 | 1.37 | 22.1 | 38 | 897 | 64.4 | C | 18.1 | 0.03 | s1 | n | y | d2
TN_2018_1132 |  | 20270855 | T0-G79545 | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.68 | 11 | Vilanova | S-XLPE+TALCUM+03ACFDIT+5300SEIT | CD | 59.4 | 24.8 | No | 2018-07-27 | C_s1_d2 | 0.75 | 18.3 | 28.8 | 1059 | 44.2 | C | 28.1 | 0.05 | s1 | n | y | d2
TN_2018_1133 |  | OP67997 20267847 | 326295U | PRYSMIAN AFUMEX RHZ1MZ1 (AS) 10KV 3X150 | 67.94 | 3 | Vilanova | 1602SEES | CD | 67.9 | 27.6 | No | 2018-07-27 | B2_s1_d2 | 0.51 | 3.9 | 5.4 | 1383 | 11 | B2 | 0.9 | 0 | s1 | n | y | d2
TN_2018_1134 |  | OP68513 20232769 | 458130T | AFUMEX CLASS RZ1-K (AS) 1KV 1X120 | 19.81 | 8 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 65.9 | 29 | No | 2018-07-27 | D_s1_d2 | 3.3 | 31 | 78.8 | 1479 | 66.9 | D | 24.6 | 0.1 | s1 | n | y | d2
180700821 |  | 17356 | -- | 32FO 8X4 KT FILLED ( PROTO Nº 36) | 13.2 | 12 | Paron | MEGOLONS548 | -- | 61.1 | 25.4 | No | 2018-07-31 | D_s2_d2 | 3.3 | 60.4 | 97 | 1497 | 100 | D | 125 | 0.21 | s2 | y | y | d2
180700822 |  | 17356 | -- | 16FO 4X4 KT FILLED ( PROTO Nº 37) | 12 | 13 | Paron | MEGOLONS548 | -- | 60.4 | 25.6 | No | 2018-07-31 | D_s2_d2 | 2.2 | 39.1 | 51 | 918 | 87 | D | 86 | 0.19 | s2 | y | y | d2
180700823 |  | 17356 | -- | 32FO 8X4 KT FILLED ( PROTO Nº 38) | 13.44 | 12 | Paron | MEGOLOND312 | -- | 58.4 | 25.8 | No | 2018-07-31 | C_s2_d1 | 1.9 | 25.9 | 33.7 | 861 | 65 | C | 113 | 0.19 | s2 | y | n | d1
18080001 |  | 17356 | -- | 16 FO 4X4 FILLED (PROTO N° 39) | 12 | 13 | Paron | MEGOLOND312 | -- | 57.2 | 25.2 | No | 2018-08-02 | B2_s2_d1 | 1 | 13.2 | 23.9 | 819 | 57 | B2 | 59 | 0.15 | s2 | y | n | d1
18080002 |  | 17356 | -- | 32 FO 8X4 FILLED (PROTO N° 40) | 13.44 | 12 | Paron | 1602SEES | -- | 57.7 | 25.8 | No | 2018-08-02 | E ou F_s2_d2 | 3.3 | 118.1 | 217.7 | 1086 | 285 | E ou F | 191 | 0.38 | s2 | y | y | d2
18080003 |  | 17356 | -- | 16 FO 4X4 FILLED (PROTO N° 41) | 12 | 13 | Paron | 1602SEES | -- | 51.5 | 27.7 | No | 2018-08-02 | E ou F_s2_d2 | 3.3 | 88.2 | 129.2 | 1245 | 156 | E ou F | 62 | 0.15 | s2 | y | y | d2
18080004 |  | 17369 | -- | AFUMEX TECNUC-PK3CB380-PRYSMIAN 255-7*1.5- CU C I2-BLG- LSOH-0.3/0.5(0.6)-CST 74.C.068 | 14 | 11 | Paron | IX2200+3100GV+SW3100 | -- | 42.2 | 29.2 | No | 2018-08-02 | B2_s1_d2 | 0.5 | 7.1 | 12.5 | 891 | 21 | B2 | 26 | 0.08 | s1 | y | y | d2
18080005 |  | 17369 | -- | AFUMEX TECNUC-PK3CB094-PRYSMIAN 255-3*1.5- CU C I2-- LSOH-0.3/0.5(0.6)-CST 74.C.068 | 11 | 14 | Paron | IX2200+3100GV+SW3100 | -- | 67 | 24 | No | 2018-08-29 | B2_s1_d0 | 0.9 | 11.1 | 18 | 975 | 34 | B2 | 38 | 0.06 | s1 | n | n | d0
18080006 |  | 17388 | -- | ALTICE DRAKA 1 OF 6657 A2 82 OF 82644998 | 4.6 | 60 | Paron | 1700SEES+ECCOH5702 | -- | 62.7 | 24.8 | No | 2018-08-29 | C_s1_d1 | 1.3 | 16.6 | 36.2 | 585 | 127 | C | 30 | 0.08 | s1 | y | n | d1
18080007 |  | 17369 | -- | AFUMEX TECNUC-PK3BB494-PRYSMIAN 255-3G1.5- CU C I2- LSOH-0.6/1(1.2)-CST 74.C.068 | 10.8 | 14 | Paron | IX2200+3100GV+SW3100 | -- | 54.2 | 22 | No | 2018-08-30 | C_s2_d1 | 1.8 | 23.4 | 31.5 | 1155 | 49 | C | 76 | 0.17 | s2 | y | n | d1
18080008 |  | 17369 | -- | AFUMEX TECNUC-PK3PS514-PRYSMIAN 255-1P1.00MM²- CU C I5 -BLG- LSOH-0.3/0.5(0.6)-CST 74.C.068 | 9.85 | 15 | Paron | IX2200+3100GV+SW3100 | -- | 57 | 22.3 | No | 2018-08-30 | B2_s1_d1 | 0.6 | 5.1 | 12.1 | 621 | 38 | B2 | 21 | 0.07 | s1 | y | n | d1
18080019 |  | 17394 | -- | EUROTUNNEL COAX 1X630 CU 25KV | 73.3 | 3 | Manlleu | :ISHTPS218+ANTIFONGIQUEINTERCIDEOBF10SPCDEKRAHNFRANCE | -- | 50 | 20 | No | 2018-08-30 | B2_s1_d0 | 0.62 | 3.5 | 4.9 | 795 | 11.3 | B2 | 6.1 | 0.01 | s1 | n | n | d0
18090001 |  | 17415 | -- | PRYSMIAN (P) P/N 20204260 -CAVO REC LSOH 6KV 1*70/35+4*1.5 FG7H10M2 2018 | 33 | 6 | Paron | HEPR+ID2900IT+SV27AHIT | -- | 60.2 | 21.8 | No | 2018-09-04 | B2_s1_d2 | 0.5 | 10.3 | 26.9 | 1500 | 22 | B2 | 41 | 0.15 | s1 | y | y | d2
TN_2018_1135 |  | OP68392 20166925 | 475290V | AFUMEX FIRS MDZ1MZ1-K 1.8/3KV 1X300 MM² | 44.4 | 4 | Vilanova |  | CD | 59.8 | 26 | No | 2018-08-01 | B2_s1_d2 | 0.46 | 7.6 | 9.8 | 1392 | 19.2 | B2 | 0 | 0 | s1 | n | y | d2
TN_2018_1136 |  |  | T8-F71189 | FS18OR18 3G1.5 500V | 7.04 | 21 | Vilanova | 2800GPIT+05ABFPIT+2000SPIT | CD | 72.9 | 24.8 | No | 2018-08-29 | B2_s2_d0 | 0.71 | 7.2 | 13.1 | 414 | 138.3 | B2 | 54.3 | 0.41 | s2 | n | n | d0
TN_2018_1137 |  |  | 248845J | CU-HEPRZ1(AS) 1X50MM2 12/20KV | 32.17 | 6 | Vilanova | HEPR+1420FEES+6000SEES | CD | 71.1 | 25.1 | No | 2018-08-29 | D_s1_d2 | 2.09 | 49.7 | 86.5 | 1386 | 82.8 | D | 7.1 | 0.02 | s1 | n | y | d2
TN_2018_1138 |  | 8246628 | 442692M | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 27.88 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 58.6 | 27.9 | No | 2018-08-29 | B2_s1_d1 | 0.62 | 6.5 | 16.7 | 1500 | 13.9 | B2 | 3.3 | 0.01 | s1 | y | n | d1
TN_2018_1139 |  |  |  | FS17 1X1.5 | 2.95 | 165 | Vilanova | 2800GPIT+2200IPITASSKIN | CD | 57.1 | 29 | No | 2018-08-29 | B2_s2_d0 | 0.75 | 6.1 | 16.3 | 456 | 134.6 | B2 | 222.8 | 1.03 | s2 | n | n | d0
TN_2018_1140 |  | OF253 |  | PRYSMIAN RHZ1-RA 2OL (AS) 76/132KV 1X400 | 74.96 | 3 | Vilanova | 6000SEES | CD | 58.35 | 29.9 | No | 2018-08-29 | D_s1_d2 | 1.02 | 31.3 | 54.5 | 1440 | 52.3 | D | 40 | 0.06 | s1 | n | y | d2
TN_2018_1142 |  |  | 235684D | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.92 | 165 | Vilanova | 1602SEES | CD | 73.1 | 26.3 | No | 2018-09-03 | B2_s2_d0 | 1.17 | 15 | 28.4 | 672 | 111.5 | B2 | 57.4 | 0.14 | s2 | n | n | d0
TN_2018_1141 |  |  | 235873J | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.96 | 165 | Vilanova | 1602SEES+5%PE | CD | 74.1 | 24.7 | No | 2018-09-03 | C_s2_d0 | 1.35 | 17.9 | 36.3 | 693 | 132 | C | 64.4 | 0.16 | s2 | n | n | d0
TN_2018_1143 |  |  | 235610Y | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.95 | 165 | Vilanova | 1602SEES+10%PE | CD | 73 | 26.1 | No | 2018-09-03 | C_s2_d1 | 1.96 | 22.9 | 40 | 780 | 134.7 | C | 74.1 | 0.15 | s2 | y | n | d1
TN_2018_1144 |  | OP68355 20269300 | 476835Z | MRZ1F3Z1-K 1KV 1X300 | 36.18 | 5 | Vilanova | CUC5+MICA+XLPE+INNERSHEATH1602SEES+TAPECO/ALCORRUGATED+LANTORLONGITUDINAL+SHEATHGFR380 | CD | 71.1 | 27.6 | No | 2018-09-03 | B2_s1_d1 | 0.81 | 12.4 | 15.6 | 1491 | 54.7 | B2 | 12.7 | 0.03 | s1 | y | n | d1
TN_2018_1145 |  | OP68047 20268300 | 249894Z | AFUMEX CLASS ATEX RZ1OZ1MZ1-K 2RH 1KV 24X2.5 | 33.3 | 6 | Vilanova | XLPE+1602SEES+COPPERTAPE+GFR380+WIREARMOUREDANDSTEEL+GFR380 | CD | 82.1 | 22.5 | No | 2018-09-04 | B2_s1_d0 | 0.48 | 9.4 | 11.7 | 1437 | 47.5 | B2 | 4.7 | 0.01 | s1 | n | n | d0
TN_2018_1146 |  | OP68048 20238302 | 455276R | AFUMEX CLASS ATEX RZ1OZ1MZ1-K 2RH 1KV 3X50 | 37.5 | 5 | Vilanova | XLPE+1602SEES+COPPERTAPE+GFR380+WIREARMOUREDANDSTEEL+GFR380 | CD | 82.5 | 24.2 | No | 2018-09-04 | B2_s1_d0 | 0.6 | 10.9 | 15.4 | 1500 | 33.6 | B2 | 0 | 0 | s1 | n | n | d0
TN_2018_1147 |  | OP68392 20166925 | 476841F | AFUMEX FIRS MDZMZ1-K 3KV 1X300/60 | 43.383 | 5 | Vilanova | GFR380 | CD | 71.9 | 27 | No | 2018-09-04 | B2_s1_d1 | 0.87 | 12.1 | 13 | 750 | 65.2 | B2 | 33.7 | 0.04 | s1 | y | n | d1
TN_2018_1148 |  | OP67919 20261723 | 470119Z | MRHOZ1MZ1-K 500V 10X3X1.5 | 35.6 | 5 | Vilanova | CU+MICA+XLPE+PET/ALTAPE+1602+ARMOURED+GFR380 | CD | 59.3 | 28.8 | No | 2018-09-04 | B2_s1_d2 | 0.58 | 10.8 | 12.2 | 1491 | 67 | B2 | 0.3 | 0 | s1 | n | y | d2
TN_2018_1149 |  | OP68406 20226650 | 467684C | AFUMEX CLASS 1KV Z1Z1-K (AS) 14X1.5MM2 | 17.08 | 9 | Vilanova | INS:CPRSHEATHAFUMEX100082355+PAPER+SHEATH20ALSEES1000053456 | CD | 62.9 | 25.8 | No | 2018-09-05 | B2_s1_d2 | 0.86 | 13.7 | 17.8 | 996 | 34.8 | B2 | 15 | 0.03 | s1 | n | y | d2
TN_2018_1150 |  | OP68407 20226647 | 470375C | AFUMEX CLASS 1KV Z1Z1-K (AS) 16X2.5MM2 | 20.77 | 7 | Vilanova | INS:CPRSHEATHAFUMEX100082355+PAPER+SHEATH20ALSEES1000053456 | OD | 60.1 | 27.3 | No | 2018-09-05 | B2_s1_d1 | 0.77 | 10.5 | 17.5 | 1383 | 31.3 | B2 | 14 | 0.03 | s1 | y | n | d1
TN_2018_1151 |  | OP68406 20226650 | 467684C | AFUMEX CLASS 1KV Z1Z1-K (AS) 14X1.5MM2 | 17.08 | 9 | Vilanova | INS:CPRSHEATHAFUMEX100082355+PAPER+SHEATH20ALSEES1000053456 | OD | 57.8 | 28.5 | No | 2018-09-05 | C_s1_d1 | 0.93 | 24 | 33.4 | 1095 | 47.2 | C | 7.3 | 0.03 | s1 | y | n | d1
TN_2018_1152 |  | OP67997 20267847 | 326295U | PRYSMIAN AFUMEX RHZ1MZ1 (AS) 10KV 3X150 | 67.94 | 3 | Vilanova | 1602SEES | OD | 59.4 | 29.4 | No | 2018-09-05 | B2_s1_d0 | 0.54 | 4.6 | 6.7 | 1377 | 15.6 | B2 | 24.4 | 0.03 | s1 | n | n | d0
TN_2018_1153 |  | OP67990 20267729 | 476813A | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K RH 1KV 3X35 | 31.73 | 6 | Vilanova | CU+MICA+XLPE+1602+ARMOURED+GFR380 | CD | 67.6 | 25.4 | No | 2018-09-06 | B2_s1_d2 | 0.64 | 13.5 | 19.4 | 1500 | 53.2 | B2 | 6.8 | 0.01 | s1 | n | y | d2
TN_2018_1154 |  | OP68246 | 478617L | AFUMEX RZ1F3Z1 AL 3KV 3X16 | 29.12 | 6 | Vilanova | CUC5+MICA+XLPE+INNERSHEATH1602SEES+TAPECO/ALCORRUGATED+LANTORLONGITUDINAL+SHEATHGFR380 | CD | 61.3 | 26.9 | No | 2018-09-06 | C_s1_d2 | 0.91 | 19.2 | 30.1 | 1497 | 80 | C | 15.8 | 0.06 | s1 | n | y | d2
TN_2018_1155 |  | OP67988 20267727 | 460021Y | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K RH 1KV 3X95 | 47.72 | 4 | Vilanova | CU+MICA+XLPE+1602+ARMOURED+GFR380 | CD | 58.8 | 27.9 | No | 2018-09-06 | B2_s1_d0 | 0.62 | 10.2 | 11.7 | 465 | 65.2 | B2 | 5 | 0.01 | s1 | n | n | d0
TN_2018_1156 |  | OP67918 20261713 | 475305L | MRHOZ1MZ1-K 500V 1X2X1.5 | 12.63 | 12 | Vilanova | CU+MICA+XLPE+PET/ALTAPE+1602+ARMOURED+GFR380 | CD | 56.3 | 28.7 | No | 2018-09-06 | C_s1_d2 | 0.78 | 17 | 24.6 | 852 | 106.4 | C | 18.1 | 0.03 | s1 | n | y | d2
18090003 |  | 17418 | -- | FR-N1 X1G1-U- 3G1.5 MM² ( BALDASARI) | 9.7 | 15 | Paron | SXLPE+LSOH | -- | 55.5 | 20.9 | No | 2018-09-10 | B2_s1_d1 | 0.7 | 6.1 | 16.5 | 657 | 46 | B2 | 14 | 0.05 | s1 | y | n | d1
18090004 |  | 17418 | -- | FR-N1 X1G1-U- 5G1.5 MM² ( BALDASARI) | 10.6 | 14 | Paron | SXLPE+LSOH | -- | 59.3 | 21.4 | No | 2018-09-10 | D_s2_d1 | 3 | 43.9 | 63.8 | 1464 | 84 | D | 76 | 0.14 | s2 | y | n | d1
18090005 |  | 17394 | -- | EUROTUNNEL COAX 1X630 CU 25KV | 74.5 | 3 | Paron | :ISHTPS218+ANTIFONGIQUEINTERCIDEOBF10SPCDEKRAHNFRANCE | -- | 53.5 | 19.5 | No | 2018-09-17 | B2_s1_d0 | 0.4 | 3.6 | 5.2 | 897 | 11 | B2 | 5 | 0.01 | s1 | n | n | d0
1809007 |  | 17428 | -- | AFUMEX PLUS PA- 1X1²- 750V- SH- 255- ESS1026HH | 3.3 | 135 | Paron | 1602SEES | -- | 56.5 | 24.4 | No | 2018-09-19 | D_s2_d0 | 2.29 | 29.5 | 45.9 | 840 | 131 | D | 145 | 0.3 | s2 | n | n | d0
TN_2018_1157 |  |  | T8-F71169 | FG16M16 1X10 MM² - 0.6/1 KV | 9.87 | 15 | Vilanova | S-XLPE-TNT-03ACFDIT-5300SEIT | CD | 73.8 | 22.1 | No | 2018-09-13 | B2_s1_d2 | 0.93 | 12.1 | 17.5 | 843 | 49.3 | B2 | 13.5 | 0.06 | s1 | n | y | d2
TN_2018_1158 |  | OP67989 20267728 | 450493S | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K RH 24X1.5 | 30.4 | 6 | Vilanova | 1602SEES+ARMOURED+GFR380 | CD | 72.8 | 22.5 | No | 2018-09-13 | B2_s1_d2 | 0.54 | 11.9 | 20.1 | 1500 | 39.7 | B2 | 9.5 | 0.01 | s1 | n | y | d2
TN_2018_1159 |  |  | T8-F71111 | FG16M16 1X10 MM² - 0.6/1 KV | 10.28 | 15 | Vilanova | S-XLPE-TNT-03ACFDIT-5300SEIT | CD | 73.2 | 24.5 | No | 2018-09-13 | B2_s1_d1 | 0.52 | 11.6 | 17.8 | 801 | 44.1 | B2 | 15.4 | 0.02 | s1 | y | n | d1
TN_2018_1160 |  | OP68049 20268301 | 470554X | AFUMEX CLASS ATEX RZ1OZ1MZ1-K 2RH 1KV 3X95 | 47.33 | 4 | Vilanova | XLPE+1602SEES+COPPERTAPE+GFR380+WIREARMOUREDANDSTEEL+GFR380 | CD | 69.9 | 25.6 | No | 2018-09-13 | B2_s1_d2 | 0.8 | 14.8 | 17.5 | 1497 | 108 | B2 | 15.7 | 0.04 | s1 | n | y | d2
TN_2018_1161 |  |  | T8-F71112 | FG16M16 1X10 MM² - 0.6/1 KV | 10.29 | 15 | Vilanova | S-XLPE-TNT-03ADFDIT-5300SEIT | CD | 64.8 | 27.5 | No | 2018-09-13 | B2_s1_d1 | 0.72 | 10.6 | 19.4 | 1029 | 41.1 | B2 | 6.2 | 0.02 | s1 | y | n | d1
TN_2018_1162 |  |  | T8-F71120 | FG16M16 1X10 MM² - 0.6/1 KV | 10.82 | 14 | Vilanova | S-XLPE-TNT-03ADFDIT-5300SEIT | CD | 72.1 | 24.5 | No | 2018-09-17 | B2_s1_d1 | 0.75 | 14.3 | 21.9 | 813 | 49.8 | B2 | 1.4 | 0.01 | s1 | y | n | d1
TN_2018_1163 |  |  | T8-F71099 | FG16OM16 3G1.5 MM² - 0.6/1 KV | 10.92 | 14 | Vilanova | S-XLPE-TALCUM-03ADFDIT-5300SEIT | CD | 58.8 | 25.8 | No | 2018-09-17 | C_s1_d0 | 0.76 | 21.1 | 27.2 | 885 | 68.4 | C | 20.1 | 0.04 | s1 | n | n | d0
TN_2018_1164 |  | OP69047 2027202 | 472234Y | RHOZ1MZ1-K 500V 6X3X1.5 | 27.08 | 6 | Vilanova | PENDINGTOCONFIRM | CD | 65.5 | 27.1 | No | 2018-09-17 | B2_s1_d2 | 0.54 | 13.2 | 17.4 | 1500 | 77.8 | B2 | 7.8 | 0.03 | s1 | n | y | d2
TN_2018_1165 |  |  | T7-F87670 | FG16M16 1X10 MM² - 0.6/1 KV | 10.97 | 14 | Vilanova | SXLPE+03AAFDIT+5300SEIT | CD | 62.9 | 27.9 | No | 2018-09-17 | B2_s1_d0 | 0.45 | 13 | 17.1 | 927 | 55.4 | B2 | 0.4 | 0 | s1 | n | n | d0
TN_2018_1166 |  |  | T0-G85113 | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.72 | 11 | Vilanova | S-XLPE-TALCUM-03ADFDIT-5300SEIT | CD | 79.6 | 22.1 | No | 2018-09-18 | C_s1_d2 | 0.83 | 19.5 | 28.7 | 1197 | 39.8 | C | 9.2 | 0.05 | s1 | n | y | d2
TN_2018_1167 |  |  | T8-F71164 | FG16M16 1X10 MM² - 0.6/1 KV | 10.22 | 15 | Vilanova | S-XLPE-TNT-03ACFDIT-5300SEIT | CD | 79.8 | 22 | No | 2018-09-18 | B2_s2_d0 | 0.69 | 12.8 | 18.6 | 564 | 73.1 | B2 | 51.3 | 0.05 | s2 | n | n | d0
TN_2018_1168 |  |  | T7-F89013 | FG16M16 1X10 MM² - 0.6/1 KV | 10.03 | 15 | Vilanova | S-XLPE-TNT-03ADFDIT-5300SEIT | CD | 81.8 | 23.2 | No | 2018-09-18 | B2_s1_d1 | 0.53 | 13.3 | 20.1 | 492 | 106.7 | B2 | 0 | 0 | s1 | y | n | d1
TN_2018_1169 |  | OP67988 20267727 | 460021Y | AFUMEX CLASS FIRS ATEX MRZ1MZ1-K RH 1KV 3X95 | 47.72 | 4 | Vilanova | CU+MICA+XLPE+1602+ARMOURED+GFR380 | OD | 75.8 | 24.2 | No | 2018-09-19 | B2_s1_d0 | 0.46 | 11.8 | 13.8 | 546 | 69.5 | B2 | 0.1 | 0 | s1 | n | n | d0
TN_2018_1170 |  | OP68047 20268300 | 249894Z | AFUMEX CLASS ATEX RZ1OZ1MZ1-K 2RH 1KV 24X2.5 | 33.3 | 6 | Vilanova | XLPE+1602SEES+COPPERTAPE+GFR380+WIREARMOUREDANDSTEEL+GFR380 | OD | 70.7 | 26.1 | No | 2018-09-19 | B2_s1_d0 | 0.58 | 11.9 | 14.7 | 492 | 76.9 | B2 | 4.9 | 0.01 | s1 | n | n | d0
TN_2018_1171 |  | OP67913 20261708 | 464920Y | RHOZ1MZ1-K 500V 1X2X1.5 | 12.47 | 13 | Vilanova | 1602SEES+ARMOUR+GFR380 | OD | 62.8 | 27.4 | No | 2018-09-19 | B2_s1_d2 | 0.84 | 8.9 | 24.2 | 810 | 145.7 | B2 | 7.3 | 0.03 | s1 | n | y | d2
TN_2018_1172 |  | OP66297 20235313 | 406885S | MRZ1F3Z1-K (AS+) 1KV 3X1.5 | 14.92 | 10 | Vilanova | CUC5+MICA+SXLPE+1602SEES+STEELSNCORRUGATED+LANTORTAPE+1602SEES | OD | 55.6 | 28.3 | No | 2018-09-19 | B2_s1_d1 | 0.88 | 12.8 | 17.6 | 975 | 45.1 | B2 | 4.1 | 0.02 | s1 | y | n | d1
TN_2018_1173 |  | OP68355 20269300 | 476835Z | MRZ1F3Z1-K 1KV 1X300 | 36.18 | 5 | Vilanova | CUC5+MICA+XLPE+INNERSHEATH1602SEES+TAPECO/ALCORRUGATED+LANTORLONGITUDINAL+SHEATHGFR380 | OD | 71.7 | 27.6 | No | 2018-09-20 | B2_s1_d0 | 0.7 | 12.4 | 15.6 | 1491 | 54.7 | B2 | 12.7 | 0.03 | s1 | n | n | d0
TN_2018_1174 |  | OP67914 20261711 | 450769S | RHOZ1MZ1-K 500V 20X2X1.5 | 37.93 | 5 | Vilanova | 1602SEES+ARMOURED+GFR380 | OD | 69.6 | 24.5 | No | 2018-09-20 | B2_s1_d0 | 0.58 | 14.5 | 16.4 | 1116 | 74.1 | B2 | 9 | 0.02 | s1 | n | n | d0
TN_2018_1175 |  | OP67915 20261712 | 450768R | RHOZ1MZ1-K 500V 20X3X1.5 | 42.22 | 6 | Vilanova | 1602SEES+ARMOURED+GFR380 | OD | 64.1 | 27.1 | No | 2018-09-20 | C_s1_d0 | 0.72 | 15.9 | 19.6 | 1494 | 71.7 | C | 13.1 | 0.02 | s1 | n | n | d0
TN_2018_1176 |  | OP69047 2027202 | 472234Y | RHOZ1MZ1-K 500V 6X3X1.5 | 27.08 | 6 | Vilanova | PENDINGTOCONFIRM | OD | 60.1 | 28.6 | No | 2018-09-20 | B2_s1_d1 | 0.69 | 12.1 | 16.4 | 1497 | 86.5 | B2 | 4.3 | 0.01 | s1 | y | n | d1
TN_2018_1177 |  | OP67917 20267203 | 453471D | RHOZ1MZ1-K 500V 10X3X1.5 | 30.64 | 6 | Vilanova | 1602SEES+ARMOURED+GFR380 | OD | 58 | 28.9 | No | 2018-09-20 | B2_s1_d1 | 0.6 | 12.5 | 15.7 | 1488 | 61.5 | B2 | 2.7 | 0.01 | s1 | y | n | d1
TN_2018_1178 |  | OP67913 20261708 | 464920Y | RHOZ1MZ1-K 500V 1X2X1.5 | 12.47 | 13 | Vilanova | 1602SEES+ARMOUR+GFR380 | OD | 62.6 | 22.6 | No | 2018-09-21 | B2_s1_d2 | 0.83 | 12.1 | 27.9 | 858 | 84.5 | B2 | 11.3 | 0.03 | s1 | n | y | d2
TN_2018_1179 |  | OP67913 20261708 | 464920Y | RHOZ1MZ1-K 500V 1X2X1.5 | 12.47 | 13 | Vilanova | 1602SEES+ARMOUR+GFR380 | OD | 60.8 | 26.2 | No | 2018-09-21 | B2_s1_d1 | 0.89 | 12.8 | 19.5 | 960 | 40.8 | B2 | 23.4 | 0.04 | s1 | y | n | d1
18100001 |  | 17443 | -- | 1000-1X240MM²-SH-NF F55-625-255 | 31.5 | 6 | Paron | ID3100FR+0400FEIT+5300SEIT | -- | 45.6 | 18.3 | No | 2018-10-01 | B2_s1_d0 | 0.48 | 5.6 | 7.7 | 852 | 20 | B2 | 7 | 0.01 | s1 | n | n | d0
18100002 |  | 17388 | -- | CÂBLE L1082-1 (FO) | 4.08 | 75 | Paron | 1700SEES+ECCOH5702 | -- | 46.6 | 17.5 | No | 2018-10-01 | D_s2_d1 | 2.9 | 25.5 | 43.6 | 741 | 130 | D | 53 | 0.13 | s2 | y | n | d1
18100003 |  | 17368 | -- | K209 ΜGAINE 24 FO M6 (SILEC) | 13 | 12 | Paron | VPE913+RUBANPOLY+FRP+TPR248+RUBANACIER+TPS246 | -- | 44.4 | 18.3 | No | 2018-10-01 | B2_s1_d0 | 0.49 | 6.3 | 12.2 | 708 | 33 | B2 | 16 | 0.04 | s1 | n | n | d0
TN_2018_1180 |  |  | T7-F86372 | FG16OM16 2G1.5 MM² - 0.6/1 KV | 10.1 | 15 | Vilanova | SXLPE+03AAFDIT+5300SEIT | CD | 66.5 | 18.8 | No | 2018-09-27 | C_s1_d2 | 0.86 | 18.1 | 28.5 | 729 | 66.6 | C | 28.5 | 0.04 | s1 | n | y | d2
TN_2018_1181 |  |  | T9-F96247 | FG16OM16 2X25 MM² - 0.6/1 KV | 21.35 | 7 | Vilanova | SXLPE+03AAFDIT+5300SEIT | CD | 66.3 | 18.8 | No | 2018-09-27 | B2_s1_d0 | 0.38 | 7.5 | 10.7 | 1500 | 24.8 | B2 | 5.6 | 0.01 | s1 | n | n | d0
18100005 |  | 17429 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 ( IRRADIÉ) | 3.3 | 135 | Paron | 1602SEES | -- | 51.9 | 19.6 | No | 2018-10-04 | C_s2_d1 | 1.95 | 22.2 | 39.5 | 696 | 126 | C | 132 | 0.33 | s2 | y | n | d1
18100006 |  | 17429 | -- | K25 750V 1X2.5-SH-NF F 55-625-255 ( IRRADIÉ) | 3.84 | 90 | Paron | 1602SEES | -- | 44.6 | 19.8 | No | 2018-10-04 | C_s2_d0 | 1.15 | 14.2 | 33.3 | 618 | 112 | C | 65 | 0.21 | s2 | n | n | d0
18100007 |  | 17429 | -- | K25 750V 1X4.0 -SH-NF F 55-625-255 ( IRRADIÉ) | 4.38 | 75 | Paron | 1602SEES | -- | 49.6 | 19.4 | No | 2018-10-09 | C_s2_d0 | 1.4 | 16.2 | 31.3 | 780 | 73 | C | 63 | 0.17 | s2 | n | n | d0
18100008 |  | 17429 | -- | K25 750V 1X6.0 -SH-NF F 55-625-255 ( IRRADIÉ) | 5.36 | 30 | Paron | 1602SEES | -- | 50 | 19.9 | No | 2018-10-09 | B2_s1_d0 | 0.87 | 5.1 | 16.9 | 546 | 93 | B2 | 14 | 0.05 | s1 | n | n | d0
18100009 |  | 17429 | -- | 750-1X16MM²-SH-NF F 55-625-255-ESS-923AA/CE 6499 | 7.46 | 21 | Paron | 1602SEES | -- | 55.2 | 19.9 | No | 2018-10-09 | B2_s1_d0 | 0.39 | 3.8 | 8.8 | 528 | 51 | B2 | 14 | 0.02 | s1 | n | n | d0
18100011 |  | 17460 | -- | 1000-1X35MM²-SH-NF F55-625-255 | 13.7 | 11 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 62.7 | 22.1 | No | 2018-10-11 | B2_s1_d2 | 0.39 | 2.8 | 5.5 | 957 | 22 | B2 | 3 | 0.01 | s1 | y | y | d2
18100012 |  | 17450 | -- | K22 6X1.6-SH-NF F 55-622-PRYSMIAN 255 | 18 | 8 | Paron | IX4800IT+3000GVFR+5300SEIT | -- | 62.7 | 21.3 | No | 2018-10-11 | B2_s1_d2 | 0.49 | 6.1 | 8.8 | 1500 | 29 | B2 | 9 | 0.01 | s1 | y | y | d2
18100014 |  | 17463 | -- | RED ELEC RHZ1-RA-2OL(AS) 1X630MM2 127/220KV | 97.5 | 2 | Paron | XLPE+TUBEAL+60ACESNATUREL+SKINSC | -- | 67 | 21.1 | No | 2018-10-12 | B2_s1_d0 | 0.52 | 5.9 | 10.3 | 750 | 23 | B2 | 9 | 0.01 | s1 | n | n | d0
18100015 |  | 17463 | -- | RTE- 1X630MM2 AL PR-11-AL-52/90(100) KV | 70 | 3 | Paron | XLPE+ALFOIL+60ACESNOIR+SKINSC | -- | 67.1 | 21 | No | 2018-10-12 | B2_s1_d2 | 1.09 | 14.9 | 19.1 | 927 | 40 | B2 | 40 | 0.09 | s1 | y | y | d2
TN_2018_1182 |  | OP67920 20261724 | 256823F | MRHOZ1MZ1-K 500V 20X2X1.5 | 41.04 | 5 | Vilanova | CU+MICA+SXLPE+1602SEESINTERNALSHEATH+STEELARMOURED+EXTERNALSHEATHGFR380 | CD | 38.5 | 17.3 | No | 2018-10-02 | B2_s1_d1 | 0.76 | 10.8 | 15.6 | 1392 | 45.7 | B2 | 11.2 | 0.03 | s1 | y | n | d1
TN_2018_1183 |  | OP67921 20267204 | 470501P | MRHOZ1MZ1-K 500V 20X3X1.5 | 45.99 | 4 | Vilanova | CU+MICA+SXLPE+1602SEESINTERNALSHEATH+STEELARMOURED+EXTERNALSHEATHGFR380 | CD | 38.9 | 17.3 | No | 2018-10-02 | B2_s1_d1 | 0.72 | 8 | 9.4 | 822 | 35.5 | B2 | 14.3 | 0.02 | s1 | y | n | d1
TN_2018_1184 |  |  | T7-F86371 | FG16OR16 5G1.5MM² - 0.6/1 KV | 13.18 | 12 | Vilanova | SXLPE+05ABFPIT+2000SPIT | CD | 75.7 | 19.2 | No | 2018-10-02 | C_s2_d1 | 1.6 | 20.4 | 35.8 | 819 | 72.6 | C | 311.4 | 0.69 | s2 | y | n | d1
TN_2018_1185 |  |  | T8-F71281 | FG16OR16 5G6 MM² - 0.6/1 KV | 17.06 | 9 | Vilanova | SXLPE+03AAFDIT+5300SEIT | CD | 30.3 | 23.9 | No | 2018-10-02 | B2_s2_d1 | 0.83 | 11 | 15.4 | 1107 | 46.5 | B2 | 142.8 | 0.24 | s2 | y | n | d1
TN_2018_1186 |  |  | 481440E | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.48 | 15 | Vilanova | 1602+CALOXOL | CD | 63.8 | 19.2 | No | 2018-10-04 | D_s1_d0 | 2.3 | 31.1 | 39.5 | 1035 | 69.2 | D | 38.6 | 0.1 | s1 | n | n | d0
TN_2018_1187 |  | OP67918 20261713 | 475305L | MRHOZ1MZ1-K 500V 1X2X1.5 | 12.63 | 12 | Vilanova | CU+MICA+XLPE+PET/ALTAPE+1602+ARMOURED+GFR380 | CD | 61.4 | 19.4 | No | 2018-10-04 | B2_s1_d1 | 0.78 | 10.9 | 17.9 | 855 | 38.3 | B2 | 23.2 | 0.04 | s1 | y | n | d1
TN_2018_1188 |  |  | 481407U | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.42 | 15 | Vilanova | 1602+CALOXOL | CD | 55.7 | 21.4 | No | 2018-10-04 | D_s1_d2 | 2.3 | 33.8 | 45.3 | 1251 | 65.8 | D | 49.4 | 0.08 | s1 | n | y | d2
TN_2018_1189 |  | OP67919 20261723 | 470119Z | MRHOZ1MZ1-K 500V 10X3X1.5 | 35.6 | 5 | Vilanova | CU+MICA+XLPE+PET/ALTAPE+1602+ARMOURED+GFR380 | CD | 53 | 23.8 | No | 2018-10-04 | B2_s1_d2 | 0.49 | 11.6 | 14.4 | 453 | 76.3 | B2 | 8.9 | 0.01 | s1 | n | y | d2
TN_2018_1190 |  |  | 472422C | PRYSMIAN 36 2018 OPTICAL CABLE 72FO G652D FIRS | 16.86 | 9 | Vilanova | NÚCLEOPRESÖVCONCUBIERTAAFUMEX1602SEES | CD | 54.6 | 25.3 | No | 2018-10-04 | C_s1_d2 | 0.5 | 15.1 | 19.9 | 816 | 50.7 | C | 8.2 | 0.02 | s1 | n | y | d2
TN_2018_1191 |  | 68107 20267288 | 08 - G70498 | FG16OM16 3X1.5 MM² - 0.6/1 KV | 10.28 | 15 | Vilanova | SXLPE+03AAFDIT+5300SEIT | CD | 74.2 | 17.8 | No | 2018-10-09 | C_s1_d1 | 1.15 | 21.8 | 34.2 | 771 | 73.4 | C | 34.6 | 0.06 | s1 | y | n | d1
TN_2018_1192 |  | 68106 20267289 | 07 - D37343 | FG16OM16 4X1.5 MM² - 0.6/1 KV | 11.7 | 13 | Vilanova | SXLPE+03AAFDIT+5300SEIT | CD | 77.7 | 19 | No | 2018-10-09 | C_s1_d1 | 0.85 | 15.1 | 24 | 1026 | 55 | C | 12.6 | 0.03 | s1 | y | n | d1
TN_2018_1193 |  | 68105 20167290 | 07 - D36293 | FG16OM16 5G1.5 MM² - 0.6/1 KV | 13.36 | 12 | Vilanova | SXLPE+03AAFDIT+5300SEIT | CD | 67.7 | 22.1 | No | 2018-10-09 | C_s1_d2 | 1.15 | 26.2 | 34.9 | 1014 | 76.6 | C | 21.5 | 0.04 | s1 | n | y | d2
TN_2018_1194 |  | 82586500 20215936 | 10 - G79542 | FG16OM16 24G1.5 MM² - 0.6/1 KV | 22.32 | 7 | Vilanova | S-XLPE+LANTORTAPE+03AAFDIT+5300FEIT | CD | 72.6 | 24.6 | No | 2018-10-11 | B2_s1_d0 | 0.45 | 8.4 | 14.4 | 1500 | 27.9 | B2 | 0 | 0 | s1 | n | n | d0
TN_2018_1195 |  |  | T1-H16079 | FG16M16 - 1X50 MM² - 0.6/1 KV | 15.54 | 9 | Vilanova | S-XLPE-TNT-03AAFDIT-5300SEIT | CD | 68.9 | 25.5 | No | 2018-10-11 | B2_s1_d1 | 0.5 | 10.1 | 17.2 | 1500 | 31 | B2 | 5.2 | 0.01 | s1 | y | n | d1
TN_2018_1196 |  |  |  | 53 AFO 16X32 KT FILLED | 22.55 | 7 | Vilanova | MEGOLONS548 | OD | 70.7 | 19.6 | No | 2018-10-15 | C_s2_d1 | 1.2 | 27 | 48.1 | 1500 | 47.4 | C | 67.9 | 0.15 | s2 | y | n | d1
TN_2018_1197 |  |  |  | 42 AFO 1X8 TKEST DRY | 15.22 | 10 | Vilanova | MEGOLONS548+MEGOLONS548 | OD | 66.6 | 20.8 | No | 2018-10-15 | C_s1_d0 | 0.82 | 15.6 | 20.7 | 1035 | 56.6 | C | 26.7 | 0.06 | s1 | n | n | d0
TN_2018_1198 |  |  |  | 46 AFO 1X6 TVT FILLED | 14.47 | 11 | Vilanova | MEGOLONS548+MEGOLONS548 | OD | 61.9 | 22.6 | No | 2018-10-15 | B2_s1_d0 | 0.83 | 14.8 | 19.6 | 1113 | 50.1 | B2 | 31 | 0.04 | s1 | n | n | d0
TN_2018_1199 |  |  |  | 44 AFO 12X8 TKEST DRY | 18.84 | 8 | Vilanova | MEGOLONS548+MEGOLONS548 | OD | 54.3 | 25.5 | No | 2018-10-15 | C_s1_d0 | 1.2 | 17 | 23.9 | 1209 | 43.9 | C | 46.8 | 0.08 | s1 | n | n | d0
TN_2018_1200 |  |  |  | 48 AFO 8X8 TVT FILLED | 13.59 | 11 | Vilanova | MEGOLONS548+MEGOLONS548 | OD | 65.7 | 19.5 | No | 2018-10-16 | D_s2_d0 | 1.74 | 41.2 | 52.1 | 876 | 98.4 | D | 79.1 | 0.13 | s2 | n | n | d0
TN_2018_1201 |  |  |  | 50 AFO 16X5 TVT FILLED | 14.61 | 10 | Vilanova | MEGOLONS548+MEGOLONS548 | OD | 62.9 | 21.2 | No | 2018-10-16 | C_s2_d1 | 1.12 | 20.3 | 30.9 | 1050 | 47.8 | C | 75.2 | 0.13 | s2 | y | n | d1
TN_2018_1202 |  |  |  | 52 AFO 16X32 KT FILLED | 20.6 | 7 | Vilanova | MEGOLONS548+MEGOLONS548 | OD | 56.4 | 23.4 | No | 2018-10-16 | D_s2_d2 | 3.3 | 50.9 | 127.8 | 1497 | 106.8 | D | 154.3 | 0.45 | s2 | n | y | d2
18100016 |  | 17462 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 | 2.96 | 165 | Paron | GV42SCFR | -- | 50.6 | 20.9 | No | 2018-10-19 | B2_s1_d2 | 0.79 | 6.6 | 19.3 | 702 | 48 | B2 | 30 | 0.09 | s1 | y | y | d2
18100017 |  | 17462 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 | 2.99 | 165 | Paron | GV42ABFR | -- | 54.4 | 20.1 | No | 2018-10-19 | B2_s1_d1 | 0.88 | 6.2 | 21.5 | 726 | 53 | B2 | 36 | 0.1 | s1 | y | n | d1
TN_2018_1203 |  | OP68316 20269758 | 489703L | AFUMEX CLASS CIRCUITO SERIE DHZ1 (AS) 5KV 1X6 | 17.3 | 9 | Vilanova | EPR+COPPER+LANTOR+1602 | OD | 42.8 | 29.2 | No | 2018-10-16 | E ou F_s2_d2 | 3.3 | 89.3 | 231.7 | 1500 | 195.8 | E ou F | 84.2 | 0.17 | s2 | n | y | d2
TN_2018_1204 |  |  |  | 51 AFO 16X5 TVT FILLED | 15.8 | 10 | Vilanova | MEGOLONS548+MEGOLONS548 | OD | 71.6 | 19.4 | No | 2018-10-18 | C_s2_d0 | 0.86 | 20.8 | 32 | 1023 | 55.6 | C | 65.4 | 0.11 | s2 | n | n | d0
TN_2018_1205 |  |  |  | 49 AFO 8X8 TVT FILLED | 15.32 | 10 | Vilanova | MEGOLONS548+MEGOLONS548 | OD | 67.4 | 20.9 | No | 2018-10-18 | C_s2_d0 | 1.21 | 28 | 43.7 | 1122 | 58.5 | C | 66.3 | 0.14 | s2 | n | n | d0
TN_2018_1206 |  |  |  | 43 AFO 1X8 TKEST DRY | 17.13 | 9 | Vilanova | MEGOLONS548+MEGOLONS548 | OD | 60.3 | 23.6 | No | 2018-10-18 | C_s1_d0 | 0.84 | 21 | 30.4 | 1494 | 45.9 | C | 31.1 | 0.06 | s1 | n | n | d0
TN_2018_1207 |  |  |  | 47 AFO 1X6 TVT FILLED | 15.41 | 10 | Vilanova | MEGOLONS548+MEGOLONS548 | OD | 58.1 | 24.9 | No | 2018-10-18 | C_s1_d0 | 0.88 | 15.4 | 21.3 | 1200 | 43 | C | 25.2 | 0.06 | s1 | n | n | d0
TN_2018_1208 |  | OP69089 20269340 | 489748K | AL-AFUMEX RZ1F3Z1 3X16 3KV ADIF | 28.54 | 6 | Vilanova | LONGITUDINALLANTOR+GFR380 | CD | 76 | 20 | No | 2018-10-19 | B2_s1_d2 | 0.61 | 12.5 | 18 | 1488 | 34.3 | B2 | 13.8 | 0.06 | s1 | n | y | d2
TN_2018_1209 |  |  |  | 45 AFO 12X8 TKEST DRY | 20.84 | 7 | Vilanova | MEGOLONS548+MEGOLONS548 | OD | 76.5 | 21.3 | No | 2018-10-19 | C_s1_d0 | 0.55 | 15.5 | 22.1 | 1251 | 36.1 | C | 10.4 | 0.04 | s1 | n | n | d0
TN_2018_1210 |  | OP69071 20258703 | 489676G | EATST 14X0.9 | 28.23 | 6 | Vilanova | LANTORLONGITUDINAL+1602 | OD | 63.4 | 21.6 | No | 2018-10-22 | B2_s1_d2 | 0.62 | 5.8 | 8.6 | 687 | 25.3 | B2 | 0.6 | 0.01 | s1 | n | y | d2
TN_2018_1211 |  | OP69091 202677728 | 491661P | AFUMEX CLASS ATEX MRZ1MZ1-K 1KV 24X1.5 | 29.04 | 6 | Vilanova | SXLPE+LANTORHELICOIDAL+GFR380 | OD | 49.8 | 24.1 | No | 2018-10-22 | B2_s1_d2 | 0.74 | 9.2 | 25.4 | 1497 | 22.4 | B2 | 13.1 | 0.04 | s1 | n | y | d2
TN_2018_1212 |  | OP69098 20266802 | 483778W | AFUMEX CLASS ATEX RZ1OZ1MZ1-K 2RH 1KV 3X95 | 46.7 | 4 | Vilanova | LANTORHELICOIDAL+GFR380 | OD | 29 | 34.5 | No | 2018-10-22 | B2_s1_d1 | 0.6 | 6.4 | 9 | 840 | 16.7 | B2 | 7.2 | 0.01 | s1 | y | n | d1
18100018 |  | 17474 | -- | CEBEC 1442 XGB 3G1.5 0.6/1KV NBN HD 604 ( BALDASSARI) | 9.6 | 15 | Paron | SXLPE+BEDDLSOH+SHEATHLSOH | -- | 37.1 | 19.7 | No | 2018-10-23 | B2_s1_d1 | 0.95 | 10 | 23.1 | 765 | 50 | B2 | 36 | 0.09 | s1 | y | n | d1
18100019 |  | 17426 | -- | TERNA 1X2500 AL-XLPE-20-AL-320/340 KV DC | 125 | 2 | Paron | XLPE+TUBEAL+FR6082+SKINSC | -- | 24.5 | 31.1 | No | 2018-10-23 | C_s1_d2 | 1.34 | 21.5 | 28.1 | 756 | 63 | C | 21 | 0.03 | s1 | y | y | d2
TN_2018_1213 |  | OP69070 20258679 | 480860Z | EATST 4X1.4 | 14.34 | 11 | Vilanova | 1602SEES | OD | 58.4 | 18 | No | 2018-10-23 | C_s2_d2 | 1.25 | 26.5 | 43.9 | 1044 | 65.1 | C | 62.9 | 0.16 | s2 | n | y | d2
TN_2018_1214 |  | OP69072 20258714 | 486449Z | EATST 10X4X1.4 | 33.64 | 5 | Vilanova | 1602SEES | OD | 53.3 | 20.2 | No | 2018-10-23 | B2_s1_d0 | 0.44 | 6.7 | 8.3 | 912 | 30.2 | B2 | 2.8 | 0.01 | s1 | n | n | d0
TN_2018_1215 |  | OP68317 20269759 | 481084T | AFUMEX CLASS CIRCUITO SERIE DHZ1 (AS) 5KV 1X6 | 17.35 | 9 | Vilanova | EPR+COPPER+1602 | OD | 39.1 | 27.8 | No | 2018-10-24 | E ou F_s2_d2 | 3.3 | 131.8 | 328 | 1428 | 294.5 | E ou F | 136.4 | 0.43 | s2 | n | y | d2
TN_2018_1216 |  | OP69070 20258679 | 465488R | EATST 4X1.4 | 14.89 | 10 | Vilanova | LANTORLONGITUDINAL+1602 | OD | 58.2 | 18.4 | No | 2018-10-24 | C_s1_d2 | 0.97 | 22.7 | 33.3 | 1023 | 49.7 | C | 38.2 | 0.08 | s1 | n | y | d2
TN_2018_1217 |  | OP69091 202677728 | 491661P | AFUMEX CLASS ATEX MRZ1MZ1-K 1KV 24X1.5 | 29.04 | 6 | Vilanova | SXLPE+LANTORHELICOIDAL+GFR380 | OD | 54.5 | 20.1 | No | 2018-10-24 | B2_s1_d2 | 0.69 | 8 | 14.1 | 1500 | 21.6 | B2 | 9.8 | 0.03 | s1 | n | y | d2
TN_2018_1218 |  | 82690336 | 483998K | PRYSMIAN VOLTALENE RHVMAV-TR 2RH 1X150 20 KV | 41.4 | 5 | Vilanova | 6010SEES+CUWIRES+2400SPFR | CD | 46.3 | 23.2 | No | 2018-10-24 | B2_s3_d2 | 1.33 | 12.4 | 24.3 | 1494 | 38.1 | B2 | 875.5 | 1.17 | s3 | n | y | d2
TN_2018_1219 |  |  | 476244G | PRYSMIAN EPROTENAX DHVMAV RH 1X300 10KV | 45.6 | 4 | Vilanova | PENDINGTOCONFIRM | CD | 49.2 | 19.2 | No | 2018-10-25 | B2_s3_d2 | 0.85 | 11 | 13 | 717 | 47.5 | B2 | 831.1 | 1.06 | s3 | n | y | d2
TN_2018_1220 |  |  | 465641G | PRYSMIAN EPROTENAX DHV RH 1X400 10KV | 41.04 | 5 | Vilanova | PENDINGTOCONFIRM | CD | 47 | 20.8 | No | 2018-10-25 | D_s3_d2 | 1.6 | 29.6 | 76.6 | 1500 | 63.8 | D | 1284.2 | 2.32 | s3 | n | y | d2
18100020 |  | 17502 | -- | 1000-4X240MM²-SH-NF F55-625-255 | 63 | 3 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 36.2 | 20.9 | No | 2018-10-29 | B2_s1_d0 | 0.52 | 2.8 | 3.8 | 951 | 9 | B2 | 13 | 0.02 | s1 | n | n | d0
18100021 |  | 17502 | -- | 1000-3X95MM²+1X50MM²-SH-NF F55-625-255 | 39.5 | 5 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 35.5 | 21.1 | No | 2018-10-29 | B2_s1_d0 | 0.33 | 3.3 | 4.7 | 837 | 12 | B2 | 3 | 0.01 | s1 | n | n | d0
TN_2018_1221 |  | OP69195 20278784 | 487869T | MRZF3Z1-K 1KV 4G2.5 | 16.67 | 9 | Vilanova | 1602+STEELTAPE+LANTORLONGITUDINAL+1602 | CD | 49.5 | 12.3 | No | 2018-10-29 | C_s1_d2 | 0.67 | 17.8 | 32 | 1203 | 38.3 | C | 20.4 | 0.05 | s1 | n | y | d2
TN_2018_1222 |  | OP69072 20258714 | 486375U | EATST 10X4X1.4 | 33.78 | 5 | Vilanova | LANTORLONGITUDINAL+1602 | CD | 48.2 | 13.5 | No | 2018-10-29 | B2_s1_d2 | 0.58 | 6.1 | 7.5 | 1005 | 26.4 | B2 | 5.5 | 0.01 | s1 | n | y | d2
TN_2018_1223 |  | OP69130 20278783 | 492825E | MRZ1F3Z1-K 1KV 4G50 | 35.89 | 5 | Vilanova | CU+MICA+XLPE+1602+STEELTAPESN+LONGITUDINALLANTOR+1602 | CD | 46.5 | 14.3 | No | 2018-10-29 | B2_s1_d0 | 0.57 | 6.9 | 9.5 | 762 | 29.4 | B2 | 21.9 | 0.03 | s1 | n | n | d0
TN_2018_1224 |  | OP82646440 | 494797Y | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18 | 8 | Vilanova | COPPERTAPE50%+MICA+LANTOR+1602 | CD | 45.6 | 14.9 | No | 2018-10-29 | D_s1_d2 | 3.3 | 44.3 | 123 | 1500 | 102.5 | D | 46.2 | 0.13 | s1 | n | y | d2
TN_2018_1225 |  | OP69091 202677728 | 491661P | AFUMEX CLASS ATEX MRZ1MZ1-K 1KV 24X1.5 | 29.04 | 6 | Vilanova | SXLPE+LANTORHELICOIDAL+GFR380 | CD | 45 | 15.5 | No | 2018-10-30 | B2_s1_d2 | 0.75 | 8.3 | 14.1 | 1488 | 22.6 | B2 | 14.5 | 0.03 | s1 | n | y | d2
TN_2018_1226 |  | UF723718 OF68833 | 489603C | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44.38 | 5 | Vilanova | XLPE+1420FEES+6000SEES | CD | 40.7 | 17.7 | No | 2018-10-30 | D_s1_d2 | 2.05 | 48.1 | 73.8 | 1482 | 81 | D | 16.7 | 0.03 | s1 | n | y | d2
18110001 |  | 17477 | -- | BRANCHEMENT ENEDIS 3X35+35M | 25 | 7 | Paron | SXLPE+ALFOIL+6000SEES | -- | 38 | 22.4 | No | 2018-11-05 | D_s1_d2 | 1.8 | 30 | 80.1 | 1491 | 68 | D | 21 | 0.05 | s1 | y | y | d2
TN_2018_1227 |  |  | 235607V | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.93 | 165 | Vilanova | 1602SEES+1%CALOXOL | CD | 67.6 | 16.6 | No | 2018-11-05 | C_s2_d1 | 1.56 | 18.1 | 37.2 | 720 | 120.2 | C | 82.7 | 0.21 | s2 | y | n | d1
TN_2018_1228 |  |  | 435225D | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.92 | 165 | Vilanova | 1602SEES | CD | 68.1 | 17.5 | No | 2018-11-05 | C_s2_d1 | 1.53 | 14.1 | 34.2 | 627 | 121.6 | C | 50.9 | 0.14 | s2 | y | n | d1
TN_2018_1229 |  |  | 235696S | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.96 | 165 | Vilanova | 1602SEES+1.9%CALOXOL+10%PE | CD | 70.2 | 18.6 | No | 2018-11-05 | D_s1_d1 | 3.3 | 51.8 | 84.4 | 1071 | 150.1 | D | 45.1 | 0.07 | s1 | y | n | d1
TN_2018_1230 |  |  | 235761M | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.95 | 165 | Vilanova | 1602SEES+1%CALOXOL+10%PE | CD | 69.2 | 19.6 | No | 2018-11-05 | D_s1_d1 | 3.3 | 50.2 | 76.9 | 1182 | 138 | D | 42.3 | 0.07 | s1 | y | n | d1
TN_2018_1231 |  | OP67919 20261723 | 470119Z | MRHOZ1MZ1-K 500V 10X3X1.5 | 35.6 | 5 | Vilanova | CU+MICA+XLPE+PET/ALTAPE+1602+ARMOURED+GFR380 | OD | 59.3 | 28.8 | No | 2018-11-06 | B2_s1_d1 | 0.8 | 10.8 | 12.2 | 1491 | 67 | B2 | 0.3 | 0 | s1 | y | n | d1
TN_2018_1232 |  | OP67921 20267204 | 470501P | MRHOZ1MZ1-K 500V 20X3X1.5 | 45.99 | 4 | Vilanova | CU+MICA+SXLPE+1602SEESINTERNALSHEATH+STEELARMOURED+EXTERNALSHEATHGFR380 | OD | 58.5 | 16.1 | No | 2018-11-06 | B2_s1_d2 | 0.72 | 6.3 | 8.8 | 624 | 30.5 | B2 | 19 | 0.03 | s1 | n | y | d2
TN_2018_1233 |  | OP67918 20261713 | 475305L | MRHOZ1MZ1-K 500V 1X2X1.5 | 12.63 | 12 | Vilanova | CU+MICA+XLPE+PET/ALTAPE+1602+ARMOURED+GFR380 | OD | 36.1 | 25.4 | No | 2018-11-06 | B2_s1_d1 | 0.92 | 14.8 | 25 | 933 | 47.6 | B2 | 5.2 | 0.01 | s1 | y | n | d1
TN_2018_1234 |  | OP67920 20261724 | 256823F | MRHOZ1MZ1-K 500V 20X2X1.5 | 41.04 | 5 | Vilanova | CU+MICA+SXLPE+1602SEESINTERNALSHEATH+STEELARMOURED+EXTERNALSHEATHGFR380 | OD | 40.3 | 21.6 | No | 2018-11-06 | B2_s1_d2 | 0.9 | 11.8 | 20 | 1500 | 35.9 | B2 | 11.9 | 0.03 | s1 | n | y | d2
TN_2018_1235 |  | OP67921 20267204 | 470501P | MRHOZ1MZ1-K 500V 20X3X1.5 | 45.99 | 4 | Vilanova | CU+MICA+SXLPE+1602SEESINTERNALSHEATH+STEELARMOURED+EXTERNALSHEATHGFR380 | OD | 59 | 14 | No | 2018-11-07 | B2_s1_d2 | 0.89 | 8.1 | 11.3 | 720 | 41.2 | B2 | 22.3 | 0.03 | s1 | n | y | d2
TN_2018_1236 |  | OP67920 20261724 | 256823F | MRHOZ1MZ1-K 500V 20X2X1.5 | 41.04 | 5 | Vilanova | CU+MICA+SXLPE+1602SEESINTERNALSHEATH+STEELARMOURED+EXTERNALSHEATHGFR380 | OD | 58.4 | 14.6 | No | 2018-11-07 | B2_s1_d0 | 0.73 | 6.3 | 9.8 | 1311 | 23.9 | B2 | 18.4 | 0.03 | s1 | n | n | d0
TN_2018_1237 |  | OP69098 20266802 | 483778W | AFUMEX CLASS ATEX RZ1OZ1MZ1-K 2RH 1KV 3X95 | 46.7 | 4 | Vilanova | LANTORHELICOIDAL+GFR380 | OD | 56.9 | 16.5 | No | 2018-11-07 | B2_s1_d0 | 0.58 | 4.6 | 8.1 | 1089 | 14.4 | B2 | 1.4 | 0 | s1 | n | n | d0
TN_2018_1238 |  | OP69091 202677728 | 491661P | AFUMEX CLASS ATEX MRZ1MZ1-K 1KV 24X1.5 | 29.04 | 6 | Vilanova | SXLPE+LANTORHELICOIDAL+GFR380 | OD | 47.3 | 19.7 | No | 2018-11-07 | B2_s1_d2 | 0.67 | 9.5 | 22.7 | 1500 | 25.3 | B2 | 9.5 | 0.03 | s1 | n | y | d2
TN_2018_1239 |  | OP67921 20267204 | 470501P | MRHOZ1MZ1-K 500V 20X3X1.5 | 45.99 | 4 | Vilanova | CU+MICA+SXLPE+1602SEESINTERNALSHEATH+STEELARMOURED+EXTERNALSHEATHGFR380 | OD | 45 | 24 | No | 2018-11-07 | B2_s1_d1 | 0.56 | 3.9 | 8.1 | 825 | 19.9 | B2 | 9.7 | 0.02 | s1 | y | n | d1
TN_2018_1240 |  | OP69091 202677728 | 491661P | AFUMEX CLASS ATEX MRZ1MZ1-K 1KV 24X1.5 | 29.04 | 6 | Vilanova | SXLPE+LANTORHELICOIDAL+GFR380 | OD | 32.7 | 26 | No | 2018-11-07 | B2_s1_d2 | 0.82 | 6.1 | 13.6 | 1497 | 17.3 | B2 | 13 | 0.04 | s1 | n | y | d2
TN_2018_1241 |  | OP69091 202677728 | 491661P | AFUMEX CLASS ATEX MRZ1MZ1-K 1KV 24X1.5 | 29.04 | 6 | Vilanova | SXLPE+LANTORHELICOIDAL+GFR380 | OD | 65.5 | 15.6 | No | 2018-11-08 | B2_s1_d1 | 0.61 | 7.7 | 13.5 | 1494 | 19.6 | B2 | 9.4 | 0.01 | s1 | y | n | d1
TN_2018_1242 |  | 82690336 | 483998K | PRYSMIAN VOLTALENE RHVMAV-TR 2RH 1X150 20 KV | 41.4 | 5 | Vilanova | 6010SEES+CUWIRES+2400SPFR | OD | 63.9 | 16.8 | No | 2018-11-08 | B2_s3_d2 | 0.72 | 14.1 | 18.3 | 1161 | 49 | B2 | 807.4 | 1.19 | s3 | n | y | d2
TN_2018_1243 |  |  | 476244G | PRYSMIAN EPROTENAX DHVMAV 2RH 1X300 10KV | 45.6 | 4 | Vilanova | PENDINGTOCONFIRM | OD | 62.7 | 17.4 | No | 2018-11-08 | B2_s3_d2 | 0.81 | 9.5 | 15.5 | 690 | 50.3 | B2 | 880.7 | 1.25 | s3 | n | y | d2
18110002 |  | 17547 | -- | 1800-S-1*16-SH-NF F 55-625-255 | 15.4 | 10 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 20.5 | 21.9 | No | 2018-11-19 | C_s1_d2 | 0.7 | 16.3 | 28.3 | 1140 | 41 | C | 18 | 0.04 | s1 | y | y | d2
18110003 |  | 17502 | -- | 1000-3G16MM²-SH-NF F55-625-255 | 20.3 | 8 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 24.7 | 20.9 | No | 2018-11-19 | B2_s1_d0 | 0.49 | 7.9 | 8.7 | 774 | 29 | B2 | 8 | 0.01 | s1 | n | n | d0
TN_2018_1244 |  | OP82467468 20165688 | 487169G | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.36 | 8 | Vilanova | COPPERTAPE50%+MICA+LANTOR+1602 | CD | 73.1 | 16.6 | No | 2018-11-13 | D_s1_d2 | 2.75 | 35.8 | 80.3 | 1485 | 76.6 | D | 45.1 | 0.12 | s1 | n | y | d2
|  | OP82467468 20165688 | 487169G | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 19 | 8 | CEIS | COPPERTAPE50%+MICA+LANTOR+1602 | -- | 30 | 23.05 | No | 2019-05-16 | D_s1_d2 | 1.2 | 31.4 | 64 | 1431 | 56.6 | D | 25.8 | 0.08 | s1 | n | y | d2
TN_2018_1245 |  | OP69129 20278786 | 497607C | MRZ1F3Z1-K 1KV 8X1.5 | 19.32 | 8 | Vilanova | CU+MICA+XLPE+1602SEES+FLEJEACEROSN+COLA+LONGITUDINALTAPELANTOR+1602SEES | CD | 79.9 | 17.6 | No | 2018-11-18 | B2_s1_d2 | 0.75 | 10.6 | 19.9 | 1290 | 21.4 | B2 | 23.2 | 0.06 | s1 | n | y | d2
TN_2018_1246 |  | UF723718 OF68833 | 489603C | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44.38 | 5 | Vilanova | XLPE+1420FEES+6000SEES | CD | 56.3 | 18.2 | No | 2018-11-18 | C_s1_d2 | 1.28 | 28.3 | 47.4 | 1497 | 48.8 | C | 12.1 | 0.02 | s1 | n | y | d2
TN_2018_1247 |  | 20165688 | 495565H | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 16.57 | 9 | Vilanova | TPR-54 | CD | 73.1 | 14.6 | No | 2018-11-19 | E ou F_s2_d2 | 3.3 | 123.7 | 358.3 | 1500 | 298.6 | E ou F | 157.4 | 0.35 | s2 | n | y | d2
TN_2018_1248 |  | 20165688 | 497614K | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.22 | 8 | Vilanova | TPR-54 | CD | 65.3 | 16.4 | No | 2018-11-19 | E ou F_s2_d2 | 3.3 | 79.2 | 209.2 | 1500 | 174.3 | E ou F | 114.5 | 0.25 | s2 | n | y | d2
TN_2018_1249 |  | OP69635 20234257 | 495579Y | AFUMEX CLASS O 1Z1C7Z1-K 1KV 2X16 | 19.38 | 8 | Vilanova | TPR-54 | CD | 38.1 | 25.7 | No | 2018-11-19 | D_s1_d2 | 1.5 | 32.5 | 55.3 | 1314 | 60.5 | D | 33 | 0.07 | s1 | n | y | d2
TN_2018_1250 |  | OP82707928 20267849 | 497594N | PRYSMIAN EPROTENAX DHV-RH 1X400/25 10KV | 40.49 | 5 | Vilanova | HEPR+FKN939B | CD | 52.1 | 19.8 | No | 2018-11-19 | B2_s3_d2 | 1.05 | 11.1 | 26.6 | 1500 | 31.8 | B2 | 519.4 | 0.92 | s3 | n | y | d2
1811004 |  | 17559 | -- | HO7Z1-U AFUMEX PLUS FRANCE 1X1 | 3.1 | 150 | Paron | GV42ABR | -- | 22.7 | 32 | No | 2018-11-23 | D_s2_d1 | 3.3 | 33.7 | 51.3 | 975 | 116 | D | 69 | 0.09 | s2 | y | n | d1
1811005 |  | 17559 | -- | HO7Z1-U AFUMEX PLUS FRANCE 1X1 | 3.06 | 150 | Paron | GV42ACR | -- | 31 | 22.9 | No | 2018-11-23 | D_s2_d2 | 3.3 | 61.8 | 168.2 | 1026 | 232 | D | 75 | 0.13 | s2 | y | y | d2
18110006 |  | 17548 | -- | K22 2X1.6-SH-NF F 55-622-PRYSMIAN 255 | 14.4 | 11 | Paron | 5300SEIT | -- | 36.9 | 22.6 | No | 2018-11-24 | B2_s1_d2 | 0.5 | 6.8 | 12.5 | 1158 | 25 | B2 | 17 | 0.04 | s1 | y | y | d2
18110007 |  | 17548 | -- | K22 2X1.6-SH-NF F 55-622-PRYSMIAN 255 | 14.3 | 11 | Paron | 5300SEIT | -- | 35.8 | 22.6 | No | 2018-11-24 | B2_s1_d2 | 0.68 | 5.8 | 12.9 | 1290 | 13 | B2 | 16 | 0.04 | s1 | y | y | d2
18110008 |  | 17531 | -- | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.9 | 165 | Paron | 1602SEES | -- | 33 | 23.2 | No | 2018-11-27 | B2_s1_d0 | 1.1 | 7.5 | 21.9 | 714 | 56 | B2 | 30 | 0.08 | s1 | n | n | d0
18110009 |  | 17575 | -- | HO7Z1-K AFUMEX PLUS EX VILANOVA 1X1.5 | 2.9 | 165 | Paron | 1602SEES | -- | 23.5 | 32.4 | No | 2018-11-27 | C_s2_d0 | 1.68 | 13.1 | 29.6 | 705 | 78 | C | 87 | 0.22 | s2 | n | n | d0
4952 |  | -- | OF5096956 | FG16OM16 2G1.5 MM² - 0.6/1 KV | 9.4 | 17 | Manlleu | SXLPE+03AAFDIT+5300SEIT | -- | 39 | 20.8 | No | 2018-11-23 | C_s1_d2 | 1.06 | 15.1 | 25.7 | 939 | 63 | C | 34.5 | 0.04 | s1 | y | y | d2
4949 |  | -- | OF5096955 | FG16OM16 3G1.5 MM² - 0.6/1 KV | 10.8 | 14 | Manlleu | SXLPE+03AAFDIT+5300SEIT | -- | 39 | 20.5 | No | 2018-11-23 | C_s1_d1 | 1.21 | 19.1 | 34.2 | 972 | 54.4 | C | 27.4 | 0.07 | s1 | y | n | d1
4951 |  | -- | T8-G72663 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.8 | 12 | Manlleu | SXLPE+05ADFPIT+2000SPIT | -- | 43 | 19.8 | No | 2018-11-23 | C_s3_d2 | 1.38 | 18.4 | 38.7 | 801 | 81.5 | C | 415.7 | 0.88 | s3 | y | y | d2
4959 |  |  | -- | FG16OR16 2X1.5 MM² - 0.6/1 KV | 9.1 | 17 | Manlleu | SXLPE+05ABFPIT+2000SPIT | -- | 35 | 19 | No | 2018-11-27 | B2_s2_d0 | 0.83 | 6.1 | 18.8 | 540 | 79.3 | B2 | 236.6 | 0.51 | s2 | n | n | d0
4960 |  |  | -- | FG16OR16 2X1.5 MM² - 0.6/1 KV | 9.1 | 17 | Manlleu | SXLPE+05ABFPIT+2000SPIT | -- | 41 | 20.5 | No | 2018-11-27 | B2_s2_d0 | 1.09 | 7.5 | 24.3 | 639 | 97.9 | B2 | 281.9 | 0.79 | s2 | n | n | d0
4953 |  |  | T7-F86998 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.2 | 14 | Manlleu | SXLPE+05ABFPIT+2000SPIT | -- | 34 | 20.5 | No | 2018-11-27 | C_s2_d1 | 1.47 | 15.7 | 33.6 | 837 | 76.5 | C | 246.2 | 0.51 | s2 | y | n | d1
4958 |  |  | -- | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.7 | 12 | Manlleu | SXLPE+05ABFPIT+2000SPIT | -- | 34 | 21 | No | 2018-11-28 | B2_s2_d1 | 1.1 | 11.9 | 25.6 | 705 | 63.2 | B2 | 359.9 | 0.86 | s2 | y | n | d1
4954 |  |  | T7/F88757 | FG16OR16 3G1.5 MM² - 0.6/1 KV | 9.4 | 17 | Manlleu | SXLPE+05ABFPIT+2000SPIT | -- | 35 | 19 | No | 2018-11-28 | C_s2_d1 | 1.66 | 16.4 | 37.8 | 675 | 118.7 | C | 359.9 | 0.86 | s2 | y | n | d1
4956 |  |  | T7/F88766 | FG16OR16 3G1.5 MM² - 0.6/1 KV | 9.7 | 15 | Manlleu | SXLPE+05ABFPIT+2000SPIT | -- | 36 | 19 | No | 2018-11-28 | B2_s2_d1 | 1.14 | 8.4 | 24.8 | 693 | 84 | B2 | 225 | 0.51 | s2 | y | n | d1
4955 |  |  | T7-F88765 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.3 | 14 | Manlleu | SXLPE+05ABFPIT+2000SPIT | -- | 36 | 19 | No | 2018-11-28 | C_s2_d1 | 1.52 | 17.1 | 32.1 | 837 | 90.5 | C | 339.6 | 0.68 | s2 | y | n | d1
4957 |  |  | T7/F87023 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.4 | 14 | Manlleu | SXLPE+05ABFPIT+2000SPIT | -- | 38 | 17.8 | No | 2018-11-28 | C_s3_d2 | 1.92 | 24.9 | 40.3 | 765 | 24.9 | C | 453.1 | 0.7 | s3 | y | y | d2
69622 |  |  | 502656R | AL - AFUMEX DHZ1 (AS) 1X400 3.6/6KV | 41.9 | 5 | Manlleu | HEPR+1420FEES+6000SEES | -- | 41 | 20.3 | No | 2018-12-03 | B2_s1_d0 | 0.61 | 2.3 | 3.7 | 624 | 11.4 | B2 | 10.4 | 0.02 | s1 | n | n | d0
1820002 |  | 17473 | -- | 1X0.50 MM² CL5 CUET (IRRADIE) | 3.18 | 135 | Paron | 1602SEES | -- | 36.3 | 23.9 | No | 2018-10-05 | D_s2_d0 | 3.3 | 44.5 | 53.8 | 894 | 159 | D | 174 | 0.3 | s2 | n | n | d0
1820001 |  | 17473 | -- | 1X0.50 MM² CL5 CUET (IRRADIE) | 3.23 | 135 | Paron | IE4000ES | -- | 34.7 | 23.5 | No | 2018-10-05 | E ou F_s2_d1 | 3.3 | 72.8 | 179.3 | 912 | 296 | E ou F | 74 | 0.22 | s2 | y | n | d1
TN_2018_1252 |  | 996967 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.81 | 180 | Vilanova | 1602SEES+SKINTPR-53 | CD | 64.5 | 19.2 | No | 2018-12-05 | D_s2_d0 | 3.3 | 42.5 | 49 | 768 | 134.5 | D | 60.8 | 0.1 | s2 | n | n | d0
TN_2018_1256 |  | 996967 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.93 | 165 | Vilanova | 1602SEES+CALOXOL+SKINTPR-53 | CD | 74.5 | 13.4 | No | 2018-12-05 | D_s2_d0 | 2.56 | 29 | 50.5 | 765 | 135 | D | 98.4 | 0.17 | s2 | n | n | d0
18120003 |  | 17581 | -- | CÂBLE 96FO (12X8) TKEST DRY | 19.2 | 8 | Paron | TPR-37 | -- | 39.2 | 23.7 | No | 2018-12-07 | B2_s2_d1 | 0.69 | 13.3 | 18.9 | 1077 | 27 | B2 | 88 | 0.17 | s2 | y | n | d1
18120004 |  | 17581 | -- | 32FO KT | 13.3 | 12 | Paron | TPR-55 | -- | 40.3 | 23.2 | No | 2018-12-07 | E ou F_s2_d2 | 3.3 | 124.7 | 275.8 | 1278 | 282 | E ou F | 297 | 1.05 | s2 | y | y | d2
18120005 |  | 17581 | -- | 1*6FO KT | 11.4 | 14 | Paron | MEGOLONS548 | -- | 38 | 23.7 | No | 2018-12-07 | C_s2_d1 | 1.64 | 22.5 | 36.3 | 921 | 61 | C | 65 | 0.17 | s2 | y | n | d1
18120006 |  | 17581 | -- | CÂBLE 96FO (12X8) TKEST DRY | 19.3 | 8 | Paron | TPR-55 | -- | 42.5 | 22.2 | No | 2018-12-07 | B2_s2_d1 | 0.69 | 14.2 | 20.2 | 1050 | 28 | B2 | 73 | 0.14 | s2 | y | n | d1
4993 |  |  | T8-G72663 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.8 | 12 | Manlleu | SXLPE+05ADFPIT+2000SPIT | -- | 46 | 20.1 | No | 2018-12-04 | B2_s3_d1 | 1.16 | 13 | 27.7 | 720 | 64.4 | B2 | 506.8 | 0.86 | s3 | y | n | d1
4995 |  |  | 5096957 | FG16OR16 3G1.5 MM² - 0.6/1 KV ( GENERAL CAVI) | 10.6 | 14 | Manlleu | COMPETITORSAMPLE | - | 43 | 19 | No | 2018-12-05 | C_s3_d1 | 1.52 | 13.1 | 34.6 | 693 | 89.7 | C | 673.6 | 1.31 | s3 | y | n | d1
4994 |  |  | 5096958 | FG16OR16 3G1.5 MM² - 0.6/1 KV ( LA TRIVENETA) | 9.4 | 17 | Manlleu | COMPETITORSAMPLE | - | 44 | 19 | No | 2018-12-05 | B2_s3_d0 | 1.12 | 6.9 | 27.3 | 645 | 81.5 | B2 | 468.8 | 1.05 | s3 | n | n | d0
4996 |  |  | 5096959 | FG16OR16 3G1.5 MM² - 0.6/1 KV ( ICEL CAVI) | 10.4 | 15 | Manlleu | COMPETITORSAMPLE | - | 47 | 19 | No | 2018-12-05 | B2_s3_d1 | 1.22 | 11.6 | 26.9 | 702 | 74.7 | B2 | 569.9 | 1.04 | s3 | y | n | d1
TN_2018_1251 |  | 69638 | 495577W | AFUMEX CLASS O 1Z1C7Z1-K 1KV 37X1.5 | 29.39 | 6 | Vilanova | TPR-54 | CD | 50.4 | 22 | No | 2018-12-04 | B2_s1_d2 | 0.73 | 10 | 15.8 | 1497 | 20.8 | B2 | 5.1 | 0.03 | s1 | y | y | d2
TN_2018_1253 |  |  | 5096704 | EXZHELLENT RZ1-K (AS) 1KV 2X16 | 16.83 | 9 | Vilanova | SXLPE+SKINTPR45+TPR45+TPR54 | CD | 72 | 14.3 | No | 2018-12-05 | B2_s1_d0 | 0.75 | 9.3 | 12.7 | 1335 | 31 | B2 | 14.7 | 0.04 | s1 | n | n | d0
TN_2018_1254 |  | 69636 | 495566J | AFUMEX CLASS O 1Z1C7Z1-K 1KV 14X1 | 18.89 | 8 | Vilanova | TPR-54 | CD | 71.1 | 15 | No | 2018-12-05 | C_s1_d0 | 1.12 | 16.6 | 32 | 1110 | 44 | C | 37.1 | 0.12 | s1 | n | n | d0
TN_2018_1255 |  | 69637 | 495575U | AFUMEX CLASS O 1Z1C7Z1-K 1KV 37X2.5 | 33.84 | 5 | Vilanova | TPR-54 | CD | 67.7 | 17.5 | No | 2018-12-05 | B2_s1_d2 | 0.79 | 7.4 | 13.9 | 1479 | 23.3 | B2 | 0 | 0 | s1 | y | y | d2
TN_2018_1257 |  |  | 5096705 | EXZHELLENT RZ1-K (AS) 1KV 5G16 | 22.4 | 7 | Vilanova | SXLPE+SKINTPR45+TPR45+TPR54 | CD | 64.4 | 12.4 | No | 2018-12-07 | B2_s1_d0 | 0.35 | 5.9 | 7.4 | 990 | 18.6 | B2 | 0.3 | 0 | s1 | n | n | d0
TN_2018_1258 |  |  | 5096702 | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.78 | 15 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 63.8 | 12.3 | No | 2018-12-07 | B2_s1_d0 | 1.08 | 11.7 | 21 | 723 | 55.1 | B2 | 42 | 0.09 | s1 | n | n | d0
TN_2018_1259 |  |  | 5096703 | EXZHELLENT RZ1-K (AS) 1KV 5G1.5 | 11.72 | 13 | Vilanova | SXLPE+SKINTPR45+PAPELKRAFT+TPR54 | CD | 60.3 | 14.7 | No | 2018-12-07 | D_s1_d1 | 2.25 | 30.6 | 42.5 | 1425 | 59.8 | D | 36.7 | 0.09 | s1 | y | n | d1
TN_2018_1260 |  |  | 5096701 | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.16 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 55.9 | 16.4 | No | 2018-12-07 | D_s1_d1 | 2.59 | 37.1 | 64.7 | 1470 | 65.4 | D | 49.4 | 0.11 | s1 | y | n | d1
TN_2018_1261 |  |  | 495585E | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 26.36 | 6 | Vilanova | TPR-54 | CD | 48.8 | 19 | No | 2018-12-07 | C_s1_d2 | 1.1 | 15.8 | 35.9 | 1491 | 30.2 | C | 9.2 | 0.03 | s1 | y | y | d2
|  |  | 474352A | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.32 | 13 | CEIS | SXLPE+1420FEES+1602SEES | CD | 45 | 21.89 | No | 2018-10-16 | D_s1_d2 | 2.05 | 35.6 | 57.3 | 936 | 84.2 | D | 36.6 | 0.07 | s1 | y | y | d2
TN_2018_1262 |  |  | 495563F | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 26.55 | 6 | Vilanova | TPR-54 | CD | 68.2 | 12.4 | No | 2018-12-09 | B2_s1_d1 | 0.65 | 6.3 | 10.9 | 1500 | 23.1 | B2 | 0.2 | 0 | s1 | y | n | d1
TN_2018_1263 |  |  | 496640B | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 14.43 | 11 | Vilanova | TPR-54 | CD | 58.3 | 13 | No | 2018-12-09 | D_s1_d2 | 2.23 | 32.4 | 64.1 | 1500 | 53.4 | D | 39.9 | 0.1 | s1 | y | y | d2
TN_2018_1264 |  | 68773 | 495564G | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 26.74 | 6 | Vilanova | TPR-54+1602SEES | CD | 59.2 | 13.7 | No | 2018-12-09 | D_s1_d2 | 1.5 | 31.1 | 65.1 | 1251 | 68.5 | D | 29.8 | 0.07 | s1 | y | y | d2
TN_2018_1265 |  | 69401 | 495588H | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 14.56 | 10 | Vilanova | TPR-54+1602SEES | CD | 58.5 | 15.9 | No | 2018-12-09 | D_s1_d2 | 2.05 | 27.6 | 63.2 | 1494 | 63.2 | D | 34.5 | 0.11 | s1 | y | y | d2
TN_2018_1266 |  | 68571 | 495562E | AFUMEX CLASS RZ1-K (AS) 1KV 1X150 | 21.01 | 7 | Vilanova | TPR-54+1602SEES | CD | 53.5 | 18.5 | No | 2018-12-09 | C_s1_d2 | 1.38 | 25.5 | 58.1 | 1488 | 50.5 | C | 11.3 | 0.06 | s1 | y | y | d2
TN_2018_1267 |  | 68572 | 495568L | AFUMEX CLASS RZ1-K (AS) 1KV 1X185 | 24.79 | 7 | Vilanova | TPR-54+1602SEES | CD | 62.5 | 11.7 | No | 2018-12-10 | D_s1_d2 | 1.83 | 35.6 | 123 | 1500 | 102.5 | D | 39.9 | 0.21 | s1 | y | y | d2
TN_2018_1268 |  |  | 493371Y | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 13.51 | 11 | Vilanova | TPR-54 | CD | 60.6 | 12.4 | No | 2018-12-10 | E ou F_s2_d2 | 3.3 | 74.4 | 222.1 | 1458 | 198.7 | E ou F | 73.1 | 0.26 | s2 | y | y | d2
TN_2018_1269 |  |  | 450650M | PRYSMIAN DMA C33-251 XH10Z1 (CBE FRT) 1X500/16 8.7/15 | 49.55 | 4 | Vilanova | XLPE+1420FEES+6000SEES | CD | 65.9 | 14.3 | No | 2018-12-10 | D_s1_d2 | 1.73 | 42.5 | 68.1 | 1377 | 68.5 | D | 21.1 | 0.05 | s1 | y | y | d2
TN_2018_1270 |  |  | 1549179 | CEBEC 967 XVB 0.6/1KV 3G2.5 REPERO | 9.14 | 17 | Vilanova | COMPETITORSAMPLE | CD | 51.5 | 16.2 | No | 2018-12-10 | D_s3_d2 | 2.47 | 28.1 | 57.9 | 594 | 197 | D | 689.6 | 1.35 | s3 | y | y | d2
|  |  |  | BLINDEX Z1C4Z1-K 1KV (AS) 4G16MM2 | 20.42 | 8 | Manlleu |  | -- | 41 | 20 | No | 2018-12-11 | B2_s1_d1 | 0.74 | 7.8 | 12.6 | 582 | 14 | B2 | 13.6 | 0.04 | s1 | y | n | d1
|  | 82741124 | 465577M | PRYSMIAN EPROTENAX DHVMV 2RH 3X185 10KV | 70.9 | 3 | Manlleu | HEPR+2400SPES | -- | 38 | 20 | No | 2018-11-12 | B2_s3_d1 | 0.73 | 9.1 | 9.9 | 1398 | 48.4 | B2 | 961.3 | 1.02 | s3 | y | n | d1
18120007 |  | 17583 | Roll | HO7Z1-K AFUMEX PLUS EX ITALI 1X1.5 | 2.93 | 165 | Paron | 1602SEES | -- | 26.2 | 20.8 | No | 2018-12-13 | C_s2_d1 | 1.69 | 15.5 | 32.2 | 732 | 88 | C | 57 | 0.14 | s2 | y | n | d1
|  | 82720422 | -- | PRYSMIAN EPROTENAX DHVMV 2RH 3X95 20KV | 67.7 | 3 | Manlleu | HEPR+2400SPES | -- | 39 | 20 | No | 2018-12-12 | B2_s3_d1 | 0.69 | 7.9 | 9.2 | 1398 | 42 | B2 | 906.8 | 0.99 | s3 | y | n | d1
|  | 82741109 | 474173F | PRYSMIAN EPROTENAX DHVMV 2RH 3X95 10KV | 62.3 | 3 | Manlleu | HEPR+2400SPES | -- | 46 | 20 | No | 2018-12-12 | B2_s3_d1 | 0.81 | 9.9 | 12 | 699 | 50.5 | B2 | 793.1 | 0.9 | s3 | y | n | d1
|  |  |  | AL - AFUMEX DHZ1 (AS) 1X400 3.6/6KV | 41.4 | 5 | Manlleu | HEPR+1420FEES+6000SEES | -- | 40 | 20 | No | 2018-12-12 | B2_s1_d1 | 0.64 | 3.6 | 5.4 | 915 | 12 | B2 | 0 | 0.02 | s1 | y | n | d1
|  | 82707928 | 497594N | PRYSMIAN EPROTENAX DHV-RH 1X400/25 10KV | 40.2 | 5 | Manlleu | HEPR+FKN939B | -- | 38 | 20 | No | 2018-12-12 | B2_s3_d1 | 0.97 | 5.8 | 13 | 1500 | 26.7 | B2 | 448.5 | 0.76 | s3 | y | n | d1
TN_2018_1271 |  | 82403406 | 438321L | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 13.12 | 12 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 63.6 | 14.3 | No | 2018-12-13 | C_s1_d1 | 1.23 | 18.5 | 29.7 | 1020 | 41.3 | C | 20.2 | 0.04 | s1 | y | n | d1
TN_2018_1272 |  | 82416349 | 437569U | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.2 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 63 | 14.9 | No | 2018-12-13 | B2_s1_d0 | 1 | 14.9 | 22.3 | 975 | 35.2 | B2 | 18.3 | 0.03 | s1 | n | n | d0
TN_2018_1273 |  | 82403240 | 429194R | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.38 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 70.7 | 14.4 | No | 2018-12-13 | C_s1_d2 | 0.93 | 15.3 | 22.9 | 1008 | 37 | C | 10.7 | 0.03 | s1 | n | y | d2
TN_2018_1274 |  | 82493723 | 450947K | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.45 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 73.6 | 11.7 | No | 2018-12-14 | C_s1_d2 | 1.07 | 17.8 | 23.8 | 921 | 41 | C | 16.5 | 0.03 | s1 | n | y | d2
TN_2018_1275 |  |  | 464940V | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.53 | 8 | Vilanova | COPPERTAPE50%+MICA+LANTOR+1602 | CD | 49.8 | 12.3 | No | 2018-12-17 | D_s1_d2 | 1.3 | 35.8 | 78.1 | 1467 | 72.8 | D | 7.4 | 0.04 | s1 | n | y | d2
TN_2018_1276 |  | 5096716 |  | TOP CABLE TOXFREE ZH C RZ1-K (AS) 1KV 3G1.5 | 10.59 | 14 | Vilanova | COMPETITORSAMPLE | CD | 49.2 | 12.5 | No | 2018-12-17 | C_s1_d0 | 1.44 | 18 | 26.1 | 726 | 69.4 | C | 21.8 | 0.04 | s1 | n | n | d0
TN_2018_1277 |  | 5096709 |  | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G1.5MM2 | 11.44 | 14 | Vilanova | COMPETITORSAMPLE | CD | 50.3 | 12.9 | No | 2018-12-17 | C_s2_d0 | 1.6 | 19.9 | 27.8 | 855 | 54.5 | C | 58.6 | 0.09 | s2 | n | n | d0
TN_2018_1278 |  | 5096715 |  | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G1.5MM2 | 10.61 | 14 | Vilanova | COMPETITORSAMPLE | CD | 48.8 | 14.3 | No | 2018-12-17 | C_s2_d0 | 1.16 | 18 | 25.2 | 825 | 56.7 | C | 74.3 | 0.15 | s2 | n | n | d0
TN_2018_1279 |  | 5096714 |  | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G2.5MM2 | 11.46 | 14 | Vilanova | COMPETITORSAMPLE | CD | 48.4 | 16 | No | 2018-12-17 | B2_s1_d0 | 0.45 | 12.6 | 21.8 | 786 | 66.9 | B2 | 18.3 | 0.04 | s1 | n | n | d0
18120009 |  | 996967 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.92 | 165 | Paron | 1602SEES+CALOXOL+SKINTPR-53 | -- | 25 | 19.7 | No | 2018-12-15 | D_s2_d1 | 2.85 | 31.2 | 53.9 | 846 | 113 | D | 106 | 0.2 | s2 | y | n | d1
18120010 |  | 996967 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.81 | 180 | Paron | 1602SEES+SKINTPR-53 | -- | 18.9 | 26.7 | No | 2018-12-15 | D_s2_d1 | 2.2 | 17.6 | 32.1 | 666 | 91 | D | 105 | 0.24 | s2 | y | n | d1
18120011 |  | 996967 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.92 | 165 | Paron | TPR-52+SKINTPR-53 | -- | 18.4 | 25.9 | No | 2018-12-15 | C_s2_d1 | 1.98 | 18.5 | 34 | 807 | 83 | C | 64 | 0.16 | s2 | y | n | d1
|  | 996967 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.81 | 180 | Manlleu | 1602SEES+SKINTPR-53 | -- | 43 | 20 | No | 2018-12-17 | D_s2_d0 | 3.15 | 28.7 | 52.7 | 771 | 123 | D | 52.4 | 0.1 | s2 | n | n | d0
|  | 996967 | Roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.82 | 180 | Manlleu | 1602SEES+CALOXOL+SKINTPR-53 | -- | 42 | 20 | No | 2018-12-17 | D_s2_d0 | 2.83 | 29.2 | 53.6 | 846 | 114.2 | D | 68.2 | 0.13 | s2 | n | n | d0
4955 |  |  | T7-F88765 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.3 | 14 | Manlleu | SXLPE+05ABFPIT+2000SPIT | -- | 44 | 20 | No | 2018-12-17 | C_s2_d2 | 1.56 | 17.1 | 34.1 | 753 | 83.6 | C | 391.8 | 0.74 | s2 | s | n | d2
TN_2018_1280 |  | 5096717 | -- | TOP CABLE TOXFREE ZH C RZ1-K (AS) 1KV 3G2.5 | 10.95 | 14 | Vilanova | COMPETITORSAMPLE | CD | 62.2 | 10.5 | No | 2018-12-18 | C_s1_d0 | 1.42 | 26.1 | 36.2 | 732 | 84.3 | C | 21.3 | 0.08 | s1 | n | n | d0
TN_2018_1281 |  |  | 081970K | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 1X150MM² | 21.84 | 7 | Vilanova | COMPETITORSAMPLE | CD | 60.5 | 11.2 | No | 2018-12-18 | B2_s1_d0 | 0.3 | 4.9 | 5.7 | 555 | 24.8 | B2 | 25.8 | 0.03 | s1 | n | n | d0
TN_2018_1282 |  |  | 105984E | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 1X240MM² | 27.26 | 6 | Vilanova | COMPETITORSAMPLE | CD | 60.7 | 13.3 | No | 2018-12-18 | C_s1_d2 | 0.77 | 11.2 | 36.4 | 1500 | 30.3 | C | 21.9 | 0.04 | s1 | n | y | d2
TN_2018_1283 |  | 5096708 | -- | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G1.5MM2 | 10.63 | 14 | Vilanova | COMPETITORSAMPLE | CD | 59.7 | 14.8 | No | 2018-12-18 | B2_s1_d0 | 0.64 | 7.7 | 19.8 | 723 | 48.4 | B2 | 24.7 | 0.05 | s1 | n | n | d0
TN_2018_1284 |  |  | A08-08-1166 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 1X150 | 21.7 | 7 | Vilanova | COMPETITORSAMPLE | CD | 57.7 | 16.1 | No | 2018-12-18 | B2_s1_d0 | 0.21 | 3.1 | 4.9 | 687 | 14.7 | B2 | 15.3 | 0.02 | s1 | n | n | d0
TN_2018_1285 |  |  | 31-10-0974 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 1X240 | 27.1 | 6 | Vilanova | COMPETITORSAMPLE | CD | 58.5 | 15.8 | No | 2018-12-18 | B2_s1_d0 | 0.65 | 8 | 16.6 | 1500 | 20.5 | B2 | 36.5 | 0.03 | s1 | n | n | d0
18120012 |  | 17584 | roll | ORANGE DRAKA 39/2018 L110 12 FO G657 A2 OHC FRC | 5.1 | 30 | Paron | ECCOH5970 | -- | 37.2 | 21.4 | No | 2018-12-19 | B2_s1_d1 | 1.23 | 6.4 | 26.4 | 573 | 131 | B2 | 22 | 0.07 | s1 | y | n | d1
|  |  | TMC10274 | RG16H1M16 18/30KV 1X35 | 36.5 | 5 | Manlleu | SCAPA+0400FEIT+LANTOR+5300SEIT | -- | 38 | 20 | No | 2018-12-18 | B2_s1_d2 | 0.68 | 4.9 | 10.7 | 1284 | 10.9 | B2 | 14.8 | 0.03 | s1 | y | y | d2
TN_2018_1286 |  | 20259297 | TI-C02497 | RG16H1M16 12/20KV 1X50 | 29.88 | 6 | Vilanova | PET+0400FEIT+LANTOR+MEGOLONS540 | CD | 69 | 13.5 | No | 2018-12-19 | B2_s1_d0 | 0.52 | 7.7 | 9.1 | 918 | 27.1 | B2 | 5.3 | 0.01 | s1 | n | n | d0
TN_2018_1287 |  | 20259294 | TL-C37600 | RG16H1M16 12/20KV 1X25 | 28.19 | 6 | Vilanova | SCAPA+0400FEIT+LANTOR+5300SEIT | CD | 67.6 | 13.6 | No | 2018-12-19 | B2_s1_d0 | 0.4 | 4.5 | 5.8 | 909 | 19.1 | B2 | 0.4 | 0 | s1 | n | n | d0
TN_2018_1288 |  | 20269822 | TL-C05647 | RG16H1M16 18/30KV 1X35 | 36.53 | 5 | Vilanova | SCAPA+0400FEIT+LANTOR+5300SEIT | CD | 63.5 | 14.7 | No | 2018-12-19 | B2_s1_d2 | 0.51 | 5.8 | 7.5 | 1386 | 14 | B2 | 3.8 | 0.01 | s1 | n | y | d2
TN_2018_1289 |  | OP69195 20278784 | 487869T | MRZF3Z1-K 1KV 4G2.5 | 16.67 | 9 | Vilanova | 1602+STEELTAPE+LANTORLONGITUDINAL+1602 | CD | 61 | 15.6 | No | 2018-12-19 | B2_s1_d2 | 0.69 | 11.6 | 18.3 | 1182 | 22.8 | B2 | 29.9 | 0.05 | s1 | n | y | d2
TN_2018_1290 |  | 20232062 | TM-C08130 | RG16H1M16 18/30KV 1X630 | 60.27 | 4 | Vilanova | SCAPA+0400FEIT+5300SEIT | CD | 51.6 | 17.5 | No | 2018-12-19 | B2_s1_d2 | 0.59 | 8.6 | 10.1 | 969 | 31.1 | B2 | 4.6 | 0.01 | s1 | n | y | d2
TN_2018_1291 |  |  | TM-C10279 | RG16H1M16 12/20KV 1X630 | 55.2 | 4 | Vilanova | SCAPA+0400FEIT+5300SEIT | CD | 59 | 12 | No | 2018-12-20 | B2_s1_d1 | 0.38 | 8.8 | 11.6 | 1212 | 21 | B2 | 1 | 0 | s1 | y | n | d1
TN_2018_1292 |  |  | T7/F88766 | FG16OR16 3G1.5 MM² - 0.6/1 KV | 9.9 | 15 | Vilanova | SXLPE+05ABFPIT+2000SPIT | CD | 58.9 | 11.9 | No | 2018-12-20 | C_s2_d0 | 1.28 | 15.8 | 26.4 | 585 | 247.5 | C | 238.1 | 0.67 | s2 | n | n | d0
TN_2018_1293 |  |  | T7-F88765 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.5 | 13 | Vilanova | SXLPE+05ABFPIT+2000SPIT | CD | 59.2 | 12 | No | 2018-12-20 | C_s2_d2 | 1.53 | 22.1 | 38.4 | 816 | 82.1 | C | 315.1 | 0.69 | s2 | y | y | d2
TN_2018_1294 |  |  | T7-F86998 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.46 | 14 | Vilanova | SXLPE+05ABFPIT+2000SPIT | CD | 58.7 | 12.7 | No | 2018-12-20 | D_s3_d2 | 2 | 39 | 60 | 1080 | 105.5 | D | 448.4 | 0.79 | s3 | y | y | d2
4956 |  |  | T7/F88766 | FG16OR16 3G1.5 MM² - 0.6/1 KV | 10 | 15 | Manlleu | SXLPE+05ABFPIT+2000SPIT | -- | 44 | 20 | No | 2018-12-17 | C_s2_d0 | 1.54 | 11.2 | 37.5 | 618 | 118.4 | C | 363.9 | 0.84 | s2 | n | n | d0
4953 |  |  | T7-F86998 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.4 | 14 | Manlleu | SXLPE+05ABFPIT+2000SPIT | -- | 39 | 19 | No | 2018-12-18 | D_s3_d1 | 2.03 | 23.5 | 38.2 | 861 | 110.7 | D | 467.8 | 0.73 | s3 | y | n | d1
TN_2019_1295 |  |  | 505863B | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 41.45 | 5 | Vilanova | HEPR+1420FEES+6000SEES | CD | 50.1 | 11.7 | No | 2019-01-04 | D_s1_d2 | 1.07 | 41.4 | 64.8 | 1407 | 67.8 | D | 6.8 | 0.03 | s1 | n | y | d2
TN_2019_1296 |  | OP82833916 | 490242X | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 15.04 | 10 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 48.7 | 16.2 | No | 2019-01-04 | B2_s1_d0 | 0.53 | 6.7 | 11.5 | 1203 | 15.9 | B2 | 9.2 | 0.02 | s1 | n | n | d0
|  | OP82833916 | 490242X | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 14.54 | 10 | CEIS | SXLPE+1420FEES+1602SEES | CD | 38 | 19.04 | No | 2019-03-19 | C_s1_d2 | 1.1 | 16.5 | 30.4 | 1065 | 41.7 | C | 6.5 | 0.02 | s1 | n | y | d2
TN_2019_1297 |  |  |  | TOP CABLE HO7Z1-K 1X1.5MM2 | 2.88 | 165 | Vilanova | COMPETITORSAMPLE | CD | 41.3 | 10.6 | No | 2019-01-07 | C_s1_d1 | 1.41 | 18.2 | 36 | 771 | 86.3 | C | 36.9 | 0.11 | s1 | y | n | d1
TN_2019_1298 |  |  |  | MIGUELEZ AFIRENAS H07Z1-K 1X1.5MM2 | 2.94 | 165 | Vilanova | COMPETITORSAMPLE | CD | 40.8 | 12.6 | No | 2019-01-07 | C_s2_d1 | 1.93 | 17.1 | 29.7 | 819 | 70 | C | 56 | 0.11 | s2 | y | n | d1
TN_2019_1299 |  |  |  | MIGUELEZ AFIRENAS HO7Z1-K 1X2.5MM2 | 3.62 | 105 | Vilanova | COMPETITORSAMPLE | CD | 39.5 | 15.9 | No | 2019-01-07 | B2_s1_d0 | 0.82 | 8.2 | 15.7 | 624 | 79.5 | B2 | 21.5 | 0.07 | s1 | n | n | d0
|  | 703436 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.85 | 165 | Manlleu | TPR-52+SKINTPR-53 | -- | 35 | 20.2 | No | 2018-01-08 | D_s1_d1 | 2.1 | 17.5 | 36.9 | 963 | 70.2 | D | 19.9 | 0.06 | s1 | y | n | d1
TN_2019_1301 |  |  |  | CÂBLE 96FO (12X8) TKEST DRY | 18.68 | 8 | Vilanova | TPR-37+TPR-37 | CD | 56.8 | 10.4 | No | 2019-01-09 | C_s2_d1 | 0.47 | 17 | 21.9 | 1086 | 44 | C | 56.6 | 0.11 | s2 | y | n | d1
TN_2019_1302 |  |  |  | 8F TKEST DRY ROLLO 59 | 15.16 | 10 | Vilanova | TPR-37+TPR-37 | CD | 55.7 | 12 | No | 2019-01-09 | B2_s1_d1 | 0.61 | 8.5 | 11.8 | 1092 | 22 | B2 | 22.2 | 0.05 | s1 | y | n | d1
TN_2019_1303 |  |  |  | 512FO KT ROLLO 60 | 20.12 | 8 | Vilanova | TPR-37 | CD | 52.2 | 13.5 | No | 2019-01-09 | E ou F_s2_d2 | 3.3 | 98.8 | 300.5 | 1494 | 251.7 | E ou F | 174.7 | 0.42 | s2 | n | y | d2
TN_2019_1304 |  |  | 505863B | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 41.45 | 5 | Vilanova | HEPR+1420FEES+6000SEES | CD | 27.8 | 11.6 | No | 2019-01-10 | D_s1_d2 | 1.46 | 32.2 | 47.7 | 1500 | 57.3 | D | 6.7 | 0.01 | s1 | n | y | d2
TN_2019_1305 |  |  | T7-F88882 | FG16R16 1X50MM² - 0.6/1 KV | 14.43 | 11 | Vilanova | SXLPE+2000SPIT | CD | 25.8 | 13.5 | No | 2019-01-10 | D_s3_d2 | 3.3 | 55.4 | 208.1 | 1125 | 253 | D | 746.8 | 1.99 | s3 | n | y | d2
TN_2019_1306 |  |  |  | 512FO KT ROLLO 61 | 20.59 | 7 | Vilanova | TPR-37 | CD | 24.6 | 14.9 | No | 2019-01-10 | D_s2_d2 | 3.3 | 69.4 | 220.8 | 1500 | 184 | D | 153 | 0.32 | s2 | n | y | d2
|  | 996978 |  | FG17 1X1.5 CU5 | 2.85 | 165 | Manlleu | FPS166 |  | 20 | 35 | No | 2019-01-08 | D_s1_d1 | 3 | 27 | 52.7 | 786 | 111.9 | D | 29 | 0.05 | s1 | y | n | d1
TN_2019_1307 |  |  | T8-G76246 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 11.21 | 14 | Vilanova | SXLPE+05ABFPIT+2000SPIT | CD | 38.1 | 6.9 | No | 2019-01-11 | C_s2_d0 | 0.75 | 18.7 | 30.7 | 636 | 135.7 | C | 185.6 | 0.55 | s2 | n | n | d0
TN_2019_1308 |  |  | T7-F87016 | FS18OR18 3G1.5 500V | 6.85 | 21 | Vilanova | 2800GPIT+05ABFPIT+2000SPIT | CD | 36.2 | 9.3 | No | 2019-01-11 | B2_s2_d0 | 0.69 | 2.3 | 13.4 | 405 | 127.4 | B2 | 96.7 | 0.66 | s2 | n | n | d0
TN_2019_1309 |  |  | T8-G72180 | FG16OM16 5G1.5 MM² - 0.6/1 KV | 12.87 | 12 | Vilanova | SXLPE+03AEFDIT+5300SEIT | CD | 31.9 | 11.9 | No | 2019-01-11 | B2_s1_d1 | 0.82 | 10.5 | 18.5 | 894 | 31.3 | B2 | 17.1 | 0.03 | s1 | y | n | d1
19010001 |  | 17584 | -- | DRAKA 2017 4 OF G657 A2 | 3.9 | 90 | Paron | ECCOH5970 | -- | 22 | 31 | No | 2019-01-14 | B2_s1_d0 | 1.48 | 12.3 | 28.3 | 750 | 83 | B2 | 45 | 0.11 | s1 | n | n | d0
19010002 |  | 17614 | 256915F | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.6 | 14 | Paron | SXLPE+MB52+1602SEES | -- | 21.6 | 33.5 | No | 2019-01-14 | C_s2_d2 | 1.48 | 18.6 | 57.9 | 729 | 136 | C | 58 | 0.12 | s2 | y | y | d2
TN_2019_1310 |  |  | T8-G72173 | FG16OM16 5G1.5 MM² - 0.6/1 KV | 12.4 | 13 | Vilanova | SXLPE+03AEFDIT+5300SEIT | CD | 59.1 | 12.4 | No | 2019-01-14 | C_s1_d2 | 0.64 | 15.9 | 23.2 | 960 | 41.2 | C | 7.3 | 0.01 | s1 | n | y | d2
TN_2019_1311 |  |  | T7-F87015 | FS18OR18 5G1 500V | 7.66 | 19 | Vilanova | 2800GPIT+0800FPIT+2100SPIT | CD | 57.2 | 13.1 | No | 2019-01-14 | B2_s2_d0 | 1.07 | 5.2 | 15.1 | 429 | 146.7 | B2 | 128.2 | 0.76 | s2 | n | n | d0
TN_2019_1312 |  |  | T8-G76204 | FG16M16 1X10 MM² - 0.6/1 KV | 9.6 | 15 | Vilanova | SXLPE+03AEFDIT+5300SEIT | CD | 54.6 | 14 | No | 2019-01-14 | B2_s1_d0 | 0.37 | 4.9 | 10 | 705 | 37.3 | B2 | 0.5 | 0.01 | s1 | n | n | d0
TN_2019_1313 |  |  | T8-G76153 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12 | 13 | Vilanova | SXLPE+30%ADD.INTUMESCENTINBULK+05ABFPIT+2000SPIT | CD | 54.4 | 14.2 | No | 2019-01-14 | D_s3_d2 | 3.3 | 34.2 | 60.6 | 801 | 122.5 | D | 750.2 | 1.03 | s3 | n | y | d2
19010003 |  | 17614 | 506305G | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10 | 15 | Paron | SXLPE+MB52+1602SEES | -- | 21.4 | 33.2 | No | 2019-01-14 | D_s2_d2 | 2.15 | 29.8 | 68.7 | 723 | 177 | D | 76 | 0.18 | s2 | y | y | d2
TN_2019_1314 |  |  |  | CÂBLE 96FO (12X8) TKEST DRY | 19.1 | 8 | Vilanova | TPR-37+TPR-37 | CD | 63.6 | 10.7 | No | 2019-01-15 | C_s2_d2 | 0.95 | 20.5 | 26.3 | 1212 | 43.2 | C | 52.1 | 0.13 | s2 | n | y | d2
TN_2019_1315 |  |  | T8-G76148 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.96 | 13 | Vilanova | SXLPE+SKINHDPE+INTUMESCENTMBC40%]+05ABFPIT+2000SPIT | CD | 62.1 | 11.3 | No | 2019-01-15 | B2_s2_d1 | 1.48 | 11.4 | 26 | 774 | 59.5 | B2 | 276.4 | 0.6 | s2 | y | n | d1
TN_2019_1316 |  |  | T7-F88891 | FG16R16 1X6 MM² - 0.6/1 KV | 7.31 | 21 | Vilanova | S-XLPE+SKINHDPE+INTUMESCENTMBC40%]+2000SPIT | CD | 59.4 | 12.7 | No | 2019-01-15 | B2_s2_d2 | 1.2 | 4.9 | 16.2 | 504 | 80.6 | B2 | 143.6 | 0.47 | s2 | n | y | d2
TN_2019_1317 |  |  | T7-F86999 | FG16R16 1X6 MM² - 0.6/1 KV | 7.35 | 21 | Vilanova | S-XLPE+30%INTUMESCENTMBC]+2000SPIT | CD | 57.8 | 13.7 | No | 2019-01-15 | C_s2_d2 | 1.79 | 10.3 | 24.6 | 477 | 139.9 | C | 268.2 | 0.59 | s2 | n | y | d2
TN_2019_1318 |  |  | T7-F88895 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.29 | 14 | Vilanova | SXLPE+11AAFPIT+2000SPIT | CD | 54.1 | 14.9 | No | 2019-01-15 | D_s3_d1 | 2.25 | 21.8 | 34.7 | 870 | 79.4 | D | 435.6 | 0.65 | s3 | y | n | d1
19010004 |  | 17614 | 495585E | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 26 | 6 | Paron | SXLPE+TPR54 | -- | 25.6 | 22.2 | No | 2019-01-16 | B2_s1_d2 | 1.1 | 12.9 | 29.6 | 1494 | 25 | B2 | 7 | 0.02 | s1 | y | y | d2
19010005 |  | 17614 | 496640B | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 15 | 10 | Paron | SXLPE+TPR54 | -- | 28.5 | 20.8 | No | 2019-01-16 | B2_s1_d2 | 1.1 | 14.8 | 24.4 | 1107 | 32 | B2 | 18 | 0.05 | s1 | y | y | d2
19010006 |  | 17614 | 495564G | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 26.5 | 6 | Paron | SXLPE+50%1602SEES+50%TPR54 | -- | 27.5 | 22.4 | No | 2019-01-16 | D_s1_d2 | 1.53 | 34 | 82.3 | 1434 | 79 | D | 29 | 0.1 | s1 | y | y | d2
|  | 82493723 | 450947K | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12 | 13 | CEIS | SXLPE+1420FEES+1602SEES | -- | 54 | 8.1 | No | 2019-01-16 | C_s2_d1 | 1.2 | 23.1 | 39 | 870 | 68.5 | C | 53.8 | 0.15 | s2 | y | n | d1
|  | 82416349 | 437569U | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.2 | 13 | CEIS | SXLPE+1420FEES+1602SEES | -- | 58 | 4.12 | No | 2019-01-16 | B2_s1_d0 | 0.8 | 14.2 | 24.6 | 831 | 46.7 | B2 | 46.9 | 0.07 | s1 | n | n | d0
TN_2019_1319 |  |  | T6-F80903 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.37 | 14 | Vilanova | SXLPE+11AAFPIT+2000SPIT | CD | 72.7 | 13.1 | No | 2019-01-16 | D_s3_d1 | 2.5 | 30.7 | 44.4 | 849 | 108.4 | D | 584.6 | 0.86 | s3 | y | n | d1
TN_2019_1320 |  |  | 450650M | PRYSMIAN DMA C33-251 XH10Z1 (CBE FRT) 1X500/16 8.7/15 | 49.55 | 4 | Vilanova | XLPE+1420FEES+6000SEES | CD | 65.7 | 14.7 | No | 2019-01-16 | D_s1_d2 | 1.54 | 36.3 | 55.4 | 1494 | 59.7 | D | 7.5 | 0.02 | s1 | n | y | d2
TN_2019_1321 |  | 20270395 OP69039 | 505544E | RHOZ1MZ1 500V 2X2X1.5 | 17.53 | 8 | Vilanova | XLPEVISICO+GFR380+GFR380 | CD | 65.2 | 14.7 | No | 2019-01-16 | B2_s1_d2 | 0.88 | 14.4 | 20.2 | 1338 | 51.3 | B2 | 32.1 | 0.05 | s1 | n | y | d2
TN_2019_1322 |  | 81849766 | 507974W | XHIOZ1 1X120 17.5KV | 34.18 | 5 | Vilanova | PENDINGTOCONFIRM | CD | 62.9 | 15.5 | No | 2019-01-16 | D_s1_d2 | 1.71 | 40 | 58.5 | 1236 | 66.9 | D | 8.1 | 0.06 | s1 | n | y | d2
19010007 |  | 17628 | -- | 1000-1X6MM²-SH-NF F55-625-255 | 8.44 | 19 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 25.2 | 21 | No | 2019-01-18 | B2_s1_d1 | 0.68 | 4.7 | 8.1 | 732 | 41 | B2 | 5 | 0.02 | s1 | y | n | d1
19010008 |  | 17614 | 503308Y | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 14 | 11 | Paron | SXLPE+1420FEES+1602SEES | -- | 26.3 | 20.3 | No | 2019-01-18 | C_s1_d2 | 1.55 | 22.3 | 40.8 | 1338 | 40 | C | 21 | 0.06 | s1 | y | y | d2
19010009 |  | 17614 | 495588H | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 14.3 | 11 | Paron | SXLPE+50%1602SEES+50%TPR54 | -- | 27.8 | 20 | No | 2019-01-18 | D_s1_d2 | 2.25 | 32.8 | 72.5 | 1500 | 61 | D | 32 | 0.09 | s1 | y | y | d2
19010010 |  | 17614 | 495565H | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 16.5 | 9 | Paron | TPR-54 | -- | 27.9 | 21.8 | No | 2019-01-18 | E ou F_s3_d2 | 3.3 | 98.6 | 344 | 1356 | 326 | E ou F | 334 | 6.28 | s3 | y | y | d2
|  |  | 890671 | EATST 10X4X1.4 | 37.2 | 5 | Manlleu | TPR-55 | -- | 33 | 20 | No | 2019-01-18 | B2_s1_d1 | 0.71 | 5.4 | 6.7 | 1176 | 15.2 | B2 | 4.1 | 0.01 | s1 | y | n | d1
|  |  | 890668 | EATST 14X4X1.4 | 32 | 6 | Manlleu | TPR-55 | -- | 34 | 20 | No | 2019-01-18 | B2_s1_d1 | 0.55 | 6.6 | 8.3 | 1491 | 17 | B2 | 5.3 | 0.02 | s1 | y | n | d1
|  |  |  | CCTSST FR03 10X4X1.4 | 34.3 | 5 | Manlleu | TPR-55 | -- | 33 | 20 | No | 2019-01-18 | B2_s1_d1 | 0.67 | 3.6 | 8.9 | 639 | 29.6 | B2 | 5.5 | 0.01 | s1 | y | n | d1
|  |  |  | CCTSST FR03 48X1.4 | 29.1 | 6 | Manlleu | TPR-55 | -- | 33 | 20 | No | 2019-01-18 | B2_s1_d1 | 0.52 | 2.4 | 5.4 | 597 | 18.1 | B2 | 2.4 | 0 | s1 | y | n | d1
TN_2019_1323 |  |  |  | HO7Z1-K (AS) 750V 1X1.5 EXZHELLENT | 2.95 | 165 | Vilanova | 1602SEES+TPR-53+CALOXOL | CD | 68.7 | 9.7 | No | 2019-01-18 | D_s2_d1 | 3.3 | 45 | 58.9 | 813 | 120.5 | D | 62.1 | 0.12 | s2 | y | n | d1
TN_2019_1324 |  |  |  | HO7Z1-K (AS) 750V 1X2.5 EXZHELLENT | 3.56 | 105 | Vilanova | 1602SEES+TPR-53+CALOXOL | CD | 64.7 | 10.2 | No | 2019-01-18 | D_s1_d0 | 3.3 | 38.2 | 49.1 | 840 | 108.9 | D | 42.9 | 0.09 | s1 | n | n | d0
TN_2019_1325 |  |  |  | HO7Z1-K (AS) 750V 1X4 EXZHELLENT | 4.11 | 75 | Vilanova | 1602SEES+TPR-53+CALOXOL | CD | 61.4 | 11.6 | No | 2019-01-18 | C_s1_d1 | 1.65 | 14.6 | 30.6 | 798 | 84.1 | C | 36.6 | 0.11 | s1 | y | n | d1
TN_2019_1326 |  |  |  | HO7Z1-K (AS) 750V 1X6 EXZHELLENT | 4.63 | 60 | Vilanova | 1602SEES+TPR-53+CALOXOL | CD | 56.6 | 13.1 | No | 2019-01-18 | B2_s1_d0 | 0.98 | 7.2 | 17.1 | 684 | 56.2 | B2 | 28.4 | 0.11 | s1 | n | n | d0
|  | 82090338 | TO-F54769 | ASZ 300/500 1X170 | 19.9 | 8 | Manlleu |  | -- | 30 | 19 | No | 2019-01-16 | B2_s1_d0 | 0.22 | 0.4 | 1.5 | 1434 | 0 | B2 | 11.4 | 0.02 | s1 | n | n | d0
TN_2019_1327 |  |  |  | HO7Z1-K (AS) 750V 1X10 EXZHELLENT | 6.01 | 25 | Vilanova | 1602SEES | CD | 63.6 | 8.3 | No | 2019-01-23 | B2_s1_d0 | 1.39 | 3.3 | 8 | 486 | 43.6 | B2 | 1.4 | 0 | s1 | n | n | d0
TN_2019_1328 |  |  |  | TOP CABLE HO7Z1-K 1X2.5MM2 | 3.53 | 120 | Vilanova | COMPETITORSAMPLE | CD | 62.2 | 9.3 | No | 2019-01-23 | B2_s1_d1 | 1.26 | 12.2 | 27.4 | 657 | 79.1 | B2 | 23.1 | 0.05 | s1 | y | n | d1
TN_2019_1329 |  | OP69476 20280739 | 507674V | RZ1MZ1-K 1KV 19X1.5MM² 2RH | 23.19 | 7 | Vilanova | XLPE+6010SEES+GFR380 | CD | 59.4 | 11.5 | No | 2019-01-23 | B2_s1_d1 | 0.62 | 11.2 | 19 | 1476 | 32.4 | B2 | 6.8 | 0.03 | s1 | y | n | d1
TN_2019_1330 |  |  | T7-F88891 | FG16R16 1X6 MM² - 0.6/1 KV | 7.31 | 21 | Vilanova | S-XLPE+SKINHDPE+INTUMESCENTMBC40%]+2000SPIT | CD | 58.9 | 12.2 | No | 2019-01-23 | C_s2_d1 | 1.09 | 8.7 | 30.9 | 477 | 174.4 | C | 166.3 | 0.63 | s2 | y | n | d1
TN_2019_1331 |  |  | T7-F88891 | FG16R16 1X6 MM² - 0.6/1 KV | 7.31 | 21 | Vilanova | S-XLPE+SKINHDPE+INTUMESCENTMBC40%]+2000SPIT | CD | 58.6 | 12.6 | No | 2019-01-23 | B2_s2_d2 | 0.8 | 6.2 | 25.4 | 474 | 148.1 | B2 | 95.6 | 0.39 | s2 | n | y | d2
19010012 |  | 17623 | -- | HO7Z1-U AFUMEX PLUS FRANCE 1X1 | 3.02 | 165 | Paron | 1602SEESAVECPOLYSILOXANE2%ETRUBANENHÉLICE.IRRADIÈ20MRADS | -- | 37 | 25 | No | 2019-01-26 | B2_s1_d1 | 1.1 | 11.4 | 29.8 | 594 | 125 | B2 | 30 | 0.07 | s1 | y | n | d1
19010011 |  | 17623 | -- | HO7Z1-U AFUMEX PLUS FRANCE 1X1 | 2.92 | 165 | Paron | 1602SEESAVECPOLYSILOXANE2%IRRADIÈ20MRADS | -- | 36.2 | 20.9 | No | 2019-01-26 | B2_s1_d1 | 1.1 | 8.9 | 24.9 | 534 | 119 | B2 | 31 | 0.12 | s1 | y | n | d1
19010013 |  | 17648 | -- | CÂBLE L1082-1 (FO) | 4.08 | 75 | Paron | 5200SMIT+1700SEES | -- | 37.5 | 20.5 | No | 2019-01-26 | C_s1_d1 | 1.7 | 14.9 | 38.5 | 642 | 121 | C | 37 | 0.14 | s1 | y | n | d1
19010014 |  | 17648 | 2018-028 | CÂBLE L1082-1 (FO) | 4 | 80 | Paron | 5200SMIT+1700SEES | -- | 21 | 26.2 | No | 2019-01-29 | C_s1_d2 | 1.14 | 12.2 | 30.5 | 585 | 124 | C | 15 | 0.03 | s1 | y | y | d2
19010015 |  | 17648 | -- | CÂBLE L1082-1 (FO) | 4.2 | 75 | Paron | 5200SMIT+1700SEES | -- | 21.8 | 26.7 | No | 2019-01-29 | D_s1_d1 | 3.3 | 34.1 | 51.6 | 741 | 125 | D | 27 | 0.04 | s1 | y | n | d1
|  | 703436 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.85 | 165 | Manlleu | TPR-52+SKINTPR-53 | -- | 35 | 20 | No | 2019-01-22 | D_s1_d1 | 2.57 | 22.3 | 39.4 | 753 | 86.9 | D | 36.3 | 0.06 | s1 | y | n | d1
|  | 703436 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.85 | 180 | Manlleu | TPR-52+SKINTPR-53 | -- | 35 | 20 | No | 2019-01-22 | D_s1_d1 | 2.84 | 30 | 47.5 | 789 | 116.5 | D | 38.9 | 0.06 | s1 | y | n | d1
|  | 996736 | 12T2954 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 9.7 | 15 | Manlleu | PRS-03/TPR-45+FPT546 | -- | 33 | 20 | No | 2019-01-14 | B2_s1_d1 | 0.46 | 5.7 | 13.4 | 792 | 35 | B2 | 10.6 | 0.02 | s1 | y | n | d1
|  | 996866 | 06F8312 | FG17 1X1.5 CU5 | 2.9 | 165 | Manlleu | FPS152 | -- | 26 | 20 | No | 2019-01-29 | D_s1_d1 | 3.3 | 55.4 | 85.2 | 1122 | 155.2 | D | 44.5 | 0.09 | s1 | y | n | d1
|  | 996868 | 07N5708 | FG17 1X4 CU5 | 4.15 | 75 | Manlleu | FPS152 | -- | 29 | 20 | No | 2019-01-25 | B2_s1_d1 | 0.55 | 3.1 | 10 | 630 | 31.7 | B2 | 0.5 | 0.01 | s1 | Y | n | d1
|  | 703456 | 07N3725 | EXZHELLENT RZ1-K (AS) 1KV 1X35 | 13.1 | 12 | Manlleu |  | -- | 28 | 20 | No | 2019-01-29 | C_s1_d2 | 1.68 | 27.5 | 41.8 | 1344 | 52.8 | C | 15.5 | 0.04 | s1 | y | y | d2
|  | 703175 | roll | ES05Z1-K (AS) 300/500 1X1 EXZHELLENT | 2.46 | 240 | Manlleu |  | -- | 27 | 20 | No | 2019-01-29 | D_s1_d1 | 2.62 | 36.4 | 24.4 | 1236 | 75.3 | D | 35.8 | 0.09 | s1 | y | n | d1
|  | 559381 | roll | F/UTP6 4P 350MHZ LSZH | 7.4 | 21 | Manlleu |  | -- | 27 | 20 | No | 2019-01-29 | E ou F_s2_d1 | 3.3 | 238.5 | 48 | 531.1 | 750 | E ou F | 148.7 | 0.69 | s2 | y | n | d1
19010016 |  | 17657 | roll | FTG18OM16 3X120+70MM² | 48.9 | 4 | Paron | MICA+SD3500IT+TALCUM+0400FPIT+5300SEIT | -- | 28.1 | 20.6 | No | 2019-01-31 | B2_s1_d0 | 0.69 | 4.5 | 5.8 | 1491 | 11 | B2 | 2 | 0 | s1 | n | n | d0
19010017 |  | 17657 | roll | FTG18OM16 0.6/1KV 1X10MM² | 11.6 | 8 | Paron | MICA+SD3500IT+TALCUM+0400FPIT+5300SEIT | -- | 28.8 | 21.2 | No | 2019-01-31 | B2_s1_d0 | 0.49 | 4.6 | 6.3 | 501 | 32 | B2 | 3 | 0 | s1 | n | n | d0
19010018 |  | 17657 | roll | FTG18OM16 0.6/1KV 1X185MM² | 27.8 | 6 | Paron | MICA+SD3500IT+TALCUM+0400FPIT+5300SEIT | -- | 28 | 20 | No | 2019-01-31 | B2_s1_d0 | 0.6 | 5.8 | 7.2 | 957 | 17 | B2 | 1 | 0 | s1 | n | n | d0
19010019 |  | 17657 | roll | FTG18OM16 0.6/1KV 5X1.5MM² | 18 | 8 | Paron | MICA+SD3500IT+SCAPA+0400FPIT+5300SEIT | -- | 28.8 | 21.1 | No | 2019-01-31 | B2_s1_d2 | 0.49 | 3.4 | 5 | 1422 | 17 | B2 | 3 | 0.01 | s1 | y | y | d2
19010020 |  |  | roll | K22 36-1.6-SH-NF F 55-622-PRYSMIAN 255 | 33 | 6 | Paron |  | -- | 28.9 | 20 | No | 2019-01-31 | B2_s1_d2 | 0.57 | 6.1 | 8 | 1098 | 16 | B2 | 4 | 0.01 | s1 | y | y | d2
|  | 69474 | 510284G | RZ1MZ1-K 3X70 | 37.6 | 5 | Manlleu | XLPE/6010/GFR380/ | -- | 28 | 20 | No | 2019-01-31 | B2_s1_d2 | 0.56 | 6.1 | 8.7 | 585 | 40.1 | B2 | 8.1 | 0.01 | s1 | y | y | d2
|  | 69475 | 510064T | RZ1MZ1-K 19X1.5 | 23.1 | 7 | Manlleu | XLPE/GFR380/GFR380 | -- | 32 | 20 | No | 2019-01-31 | B2_s1_d1 | 0.73 | 10.6 | 19 | 1497 | 42.2 | B2 | 22.2 | 0.08 | s1 | y | n | d1
|  | 69473 | 506951J | RZ1MZ1-K 3X70 | 39.1 | 5 | Manlleu | XLPE/GFR380/GFR380 | -- | 29 | 20 | No | 2019-01-31 | B2_s1_d2 | 0.66 | 5 | 8.2 | 1440 | 31.5 | B2 | 7.9 | 0.02 | s1 | y | y | d2
TN_2019_1332 |  | 509729 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.91 | 165 | Vilanova | 1602SEES+SKINTPR-53 | CD | 47.8 | 10.6 | No | 2019-01-30 | D_s2_d2 | 2.28 | 26.6 | 47 | 678 | 132.1 | D | 79.9 | 0.12 | s2 | n | y | d2
TN_2019_1333 |  | 81849766 | 507974W | XHIOZ1 1X120 17.5KV | 34.18 | 5 | Vilanova | 1420+6000 | CD | 44.7 | 12.1 | No | 2019-01-30 | C_s2_d2 | 1.55 | 24.4 | 51.9 | 1290 | 57.5 | C | 52.9 | 0.16 | s2 | n | y | d2
TN_2019_1334 |  |  |  | HO7Z1-K (AS) 750V 1X240 EXZHELLENT | 24.76 | 7 | Vilanova |  | CD | 39.8 | 14.3 | No | 2019-01-30 | B2_s1_d2 | 0.51 | 5 | 6.7 | 882 | 21 | B2 | 10.9 | 0.02 | s1 | n | y | d2
|  | 274663 | 09T3437 | EXZHELLENT RZ1-K (AS) 1KV 3G2.5 | 11.1 | 14 | Manlleu | PRS-03/VPE-08+TPR-49+TPR-54 | -- | 30 | 20 | No | 2018-01-31 | C_s1_d0 | 1.5 | 20 | 27 | 1311 | 43.5 | C | 12.3 | 0.03 | s1 | n | n | d0
|  | 703446 | roll | HO7Z1-K TYPE2 (AS) 1X10MM2 GGC | 6.1 | 25 | Manlleu |  | -- | 28 | 20 | No | 2018-01-31 | B2_s1_d1 | 0.48 | 2.5 | 9.3 | 495 | 52.4 | B2 | 1.2 | 0.01 | s1 | y | n | d1
TN_2019_1335 |  | 81849766 | 507974W | XHIOZ1 1X120 17.5KV | 34.18 | 5 | Vilanova | 1420+6000 | -- | 35.8 | 11.3 | No | 2019-02-04 | D_s1_d2 | 1.22 | 35.6 | 63.8 | 1500 | 54.1 | D | 10.6 | 0.02 | s1 | y | y | d2
19020001 |  | 17647 | -- | TERNA 1X2500 AL-XLPE-20-AL-320/340 KV DC | 127 | 2 | Paron | XLPE+TUBEAL+6000SEES+SKINSC | -- | 25.9 | 21.1 | No | 2019-02-05 | B2_s1_d2 | 0.86 | 8.3 | 13 | 1500 | 26 | B2 | 4 | 0.01 | s1 | y | y | d2
19020002 |  | 17647 | -- | TERNA 1X2500 AL-XLPE-20-AL-320/340 KV DC | 127 | 2 | Paron | XLPE+TUBEAL+6000SEES+SKINSC | -- | 28.9 | 20 | No | 2019-02-05 | B2_s1_d2 | 0.89 | 8.5 | 11.6 | 1500 | 24 | B2 | 5 | 0.01 | s1 | y | y | d2
|  | 996978 |  | FG17 1X1.5 CU5 | 2.85 | 165 | Manlleu | FPS166 | -- | 29 | 20 | No | 2019-02-05 | D_s1_d1 | 2.58 | 21.1 | 42.7 | 774 | 97.6 | D | 26.9 | 0.06 | s1 | y | n | d1
TN_2019_1336 |  |  |  | CÂBLE 96FO (12X8) TKEST DRY | 18.68 | 8 | Vilanova | TPR-37+TPR-37 | OD | 67.4 | 13.5 | No | 2019-02-06 | B2_s1_d0 | 0.69 | 13.1 | 19.2 | 1191 | 29.7 | B2 | 38.7 | 0.1 | s1 | n | n | d0
TN_2019_1337 |  |  |  | 8F TKEST DRY ROLLO 59 | 15.56 | 9 | Vilanova | TPR-37+TPR-37 | OD | 63.6 | 14.8 | No | 2019-02-06 | B2_s1_d0 | 0.58 | 9.4 | 14.5 | 942 | 24.3 | B2 | 17.5 | 0.04 | s1 | n | n | d0
TN_2019_1338 |  | 81849766 | 507974W | XHIOZ1 1X120 17.5KV | 34.19 | 5 | Vilanova | 1420+6000 | OD | 58.3 | 17 | No | 2019-02-06 | C_s1_d2 | 1.18 | 21.4 | 29.8 | 1098 | 55.5 | C | 17.4 | 0.04 | s1 | n | y | d2
TN_2019_1339 |  | 20270395 OP69039 | 505544E | RHOZ1MZ1 500V 2X2X1.5 | 17.53 | 8 | Vilanova | XLPEVISICO+GFR380+GFR380 | OD | 31.2 | 27 | No | 2019-02-06 | B2_s1_d1 | 0.64 | 8.9 | 12.7 | 1056 | 37.5 | B2 | 38.1 | 0.06 | s1 | y | n | d1
19020004 |  | 17647 | -- | TERNA 1X2500 AL-XLPE-20-AL-320/340 KV DC | 123 | 2 | Paron | XLPE+TUBEAL+6000SEES+SKINSC | -- | 30.8 | 20.1 | No | 2019-02-06 | B2_s1_d2 | 0.8 | 7.8 | 9.8 | 741 | 23 | B2 | 7 | 0.01 | s1 | y | y | d2
19020003 |  | 17647 | -- | TERNA 1X2500 AL-XLPE-20-AL-320/340 KV DC | 123 | 2 | Paron | XLPE+TUBEAL+6000SEES+SKINSC | -- | 27.5 | 21 | No | 2019-02-06 | B2_s1_d2 | 0.8 | 5.4 | 7.2 | 702 | 18 | B2 | 4 | 0.01 | s1 | y | y | d2
|  | 70233 | 514232Y | RHZ1 (AS) 5KV 1X6 | 18.4 | 8 | Manlleu | TRIPLEEXTRUSIÓNXLPE/CINTASCFR/CINTACOBRE/CPR | -- | 31 | 20 | No | 2019-02-06 | D_s2_d2 | 3 | 55.8 | 175.5 | 1500 | 146.2 | D | 54.3 | 0.25 | s2 | y | y | d2
TN_2019_1340 |  |  |  | LT-TVT 80F | 14.54 | 10 | Vilanova | PENDINGTOCONFIRM | OD | 66.1 | 15.4 | No | 2019-02-07 | C_s1_d0 | 0.93 | 19.4 | 32.5 | 930 | 51.8 | C | 32.2 | 0.15 | s1 | n | n | d0
TN_2019_1341 |  | 20291473 | 07-D36034 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.3 | 14 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 62.7 | 13.9 | No | 2019-02-07 | C_s2_d1 | 1.64 | 24.2 | 47.5 | 651 | 139 | C | 385.1 | 0.93 | s2 | y | n | d1
TN_2019_1342 |  | 20291472 | 07-F88981 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.3 | 14 | Vilanova | SXLPE+05AFFPIT+20AESPIT | CD | 67 | 14.9 | No | 2019-02-07 | D_s3_d2 | 3.3 | 58.2 | 116.5 | 1290 | 134.4 | D | 1213.4 | 2.03 | s3 | y | y | d2
TN_2019_1343 |  | 20291471 | 07-F88921 | FG16R16 1X6 MM² - 0.6/1 KV | 7.94 | 19 | Vilanova | SXLPE+20AFSPIT | CD | 63.5 | 15.9 | No | 2019-02-07 | C_s2_d2 | 1.35 | 10.4 | 34.6 | 579 | 177.2 | C | 241.2 | 0.9 | s2 | y | y | d2
TN_2019_1344 |  | 20291470 | Roll | FG16R16 1X6 MM² - 0.6/1 KV | 6.99 | 19 | Vilanova | SXLPE+20AESPIT | CD | 63.8 | 16.5 | No | 2019-02-07 | B2_s2_d2 | 1.06 | 8 | 27.3 | 525 | 127.1 | B2 | 165.8 | 0.74 | s2 | y | y | d2
|  | 703998 | ROLL | HO7Z1-K TYPE2 (AS) 1X2.5MM2 GGC | 3.53 | 120 | Manlleu | TPR-52+TPR-53 | -- | 32 | 20 | No | 2019-02-07 | D_s1_d2 | 2.04 | 22.5 | 39 | 807 | 79.5 | D | 34.6 | 0.07 | s1 | Y | Y | d2
|  | 996996 | 10j2125 | EXZHELLENT RZ1-K (AS) 1KV 1X240 | 26.4 | 6 | Manlleu | PRS-03+TPR-54 | -- | 33 | 20 | No | 2019-02-07 | C_s1_d2 | 1.12 | 10 | 31 | 1500 | 25.8 | C | 3.1 | 0.02 | s1 | y | y | d2
|  | 69478 | 508223S | RZ1MZ1-K 5X120 | 60.4 | 4 | Manlleu | XLPE+6010+GFR380 | -- | 31 | 20 | No | 2019-02-07 | B2_s1_d0 | 0.53 | 5.1 | 6.1 | 612 | 23.4 | B2 | 4.4 | 0.01 | s1 | N | N | d0
|  | 69477 | 508230Z | RZ1MZ1-K 5X120 | 60.4 | 4 | Manlleu | XLPE+GFR380+GFR380 | -- | 30 | 20 | No | 2019-02-07 | B2_s1_d1 | 0.47 | 3.1 | 4.8 | 633 | 16.5 | B2 | 2.1 | 0 | s1 | Y | N | d1
|  | 996025 | 12T1978 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.2 | 15 | Manlleu | PRS-03SKINFPE144+TPR-49+TPR-54 | -- | 31 | 20 | No | 2019-02-08 | D_s2_d2 | 3.3 | 69.7 | 143.3 | 1419 | 128.3 | D | 72.6 | 0.35 | s2 | y | y | d2
|  | 997026 | 12T1978 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.3 | 15 | Manlleu | PRS-03SKINFPE150+TPR-49+TPR-54 | -- | 33 | 20 | No | 2019-02-08 | E ou F_s2_d2 | 3.3 | 77.8 | 152.3 | 1449 | 147.1 | E ou F | 99.9 | 0.34 | s2 | y | Y | d2
|  | 997027 | 12T1978 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.3 | 15 | Manlleu | PRS-03SKINFPE151+TPR-49+TPR-54 | -- | 33 | 20 | No | 2019-02-08 | C_s1_d0 | 1.89 | 26.6 | 40 | 1329 | 49.1 | C | 20.1 | 0.05 | s1 | n | n | d0
TN_2019_1346 |  | 20291472 | 07-F88981 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.3 | 14 | Vilanova | SXLPE+05AFFPIT+20AESPIT | CD | 67.2 | 11.5 | No | 2019-02-08 | D_s3_d2 | 2.7 | 33.7 | 56.7 | 846 | 140.5 | D | 719.7 | 1.13 | s3 | n | y | d2
TN_2019_1347 |  | 20291473 | 07-D36034 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.3 | 14 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 64.2 | 13.6 | No | 2019-02-08 | C_s3_d2 | 1.99 | 26 | 48.1 | 840 | 113.2 | C | 417.8 | 0.74 | s3 | n | y | d2
TN_2019_1348 |  | 20291471 | 07-F88921 | FG16R16 1X6 MM² - 0.6/1 KV | 7.94 | 19 | Vilanova | SXLPE+20AFSPIT | CD | 57.4 | 17.2 | No | 2019-02-08 | B2_s2_d2 | 1.11 | 9 | 29.5 | 501 | 148.8 | B2 | 191.7 | 0.73 | s2 | n | y | d2
19020005 |  | 17672 | -- | FO DROP 4MM 43 D01 | 4.3 | 75 | Paron | 1700SEES | -- | 31.4 | 20.3 | No | 2019-02-11 | D_s1_d1 | 2.6 | 20.1 | 45.5 | 672 | 149 | D | 14 | 0.03 | s1 | y | n | d1
19020006 |  | 17672 | -- | FO DROP 1MM 41 D01 | 4 | 90 | Paron | 1700SEES+LUBKO1105A | -- | 32.6 | 20.3 | No | 2019-02-11 | B2_s1_d1 | 1.13 | 11.4 | 27.8 | 624 | 105 | B2 | 12 | 0.03 | s1 | y | n | d1
TN_2019_1349 |  |  | 07-F88915 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.66 | 14 | Vilanova | SXLPE+05AFFPIT+20AESPIT | CD | 51.3 | 11.1 | No | 2019-02-11 | C_s2_d1 | 1.56 | 17.9 | 39.2 | 678 | 125.5 | C | 397.1 | 0.95 | s2 | y | n | d1
TN_2019_1350 |  |  | 07-F88917 | FG16R16 1X6 MM² - 0.6/1 KV | 7.88 | 19 | Vilanova | SXLPE+20AESPIT | CD | 53.4 | 11 | No | 2019-02-11 | C_s2_d2 | 1.38 | 11.6 | 35.8 | 531 | 185.2 | C | 292.9 | 1 | s2 | n | y | d2
TN_2019_1351 |  |  | 07-F88906 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.27 | 15 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 48.4 | 13.5 | No | 2019-02-11 | C_s2_d1 | 1.4 | 15.3 | 32.7 | 759 | 83 | C | 290 | 0.66 | s2 | y | n | d1
TN_2019_1352 |  |  | Roll | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.54 | 14 | Vilanova | SXLPE+05AFFPIT+20AESPIT | CD | 45.5 | 14.2 | No | 2019-02-11 | C_s3_d2 | 1.62 | 18.1 | 33.4 | 834 | 95.3 | C | 406.1 | 0.78 | s3 | n | y | d2
TN_2019_1353 |  |  | Roll | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.32 | 15 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 43.8 | 15.9 | No | 2019-02-11 | C_s2_d1 | 1.3 | 13.5 | 32.7 | 609 | 117.6 | C | 249.3 | 0.74 | s2 | y | n | d1
19020007 |  | 17672 | -- | FO DROP 1MM 41 D 02 | 4 | 90 | Paron | 1700SEES+LUBKO1105A | -- | 33.5 | 21.4 | No | 2019-02-11 | B2_s1_d1 | 1.17 | 13.4 | 29.1 | 600 | 108 | B2 | 12 | 0.03 | s1 | y | n | d1
19020009 |  | 17672 | -- | FO DROP 2MM 41 D 01 | 4.3 | 75 | Paron | 1700SEES+LUBKO1105A | -- | 35.3 | 20.3 | No | 2019-02-11 | D_s1_d1 | 3 | 31.7 | 61.3 | 711 | 162 | D | 21 | 0.03 | s1 | y | n | d1
19020010 |  | 17671 | -- | K25 5G1.50-SH-NF F 55-625-255 | 12.4 | 13 | Paron | ID3100/SV3300FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 34.5 | 21 | No | 2019-02-11 | C_s1_d2 | 1.2 | 17.7 | 30.3 | 867 | 54 | C | 26 | 0.08 | s1 | y | y | d2
TN_2019_1354 |  |  | 07-F88915 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.66 | 14 | Vilanova | SXLPE+05AFFPIT+20AESPIT | CD | 61.7 | 9.1 | No | 2019-02-12 | C_s2_d1 | 1.24 | 15.7 | 33.5 | 651 | 106 | C | 372.5 | 0.89 | s2 | y | n | d1
TN_2019_1355 |  |  | 07-F88917 | FG16R16 1X6 MM² - 0.6/1 KV | 7.88 | 19 | Vilanova | SXLPE+20AESPIT | CD | 60 | 9.6 | No | 2019-02-12 | B2_s2_d2 | 0.86 | 7.8 | 23.6 | 528 | 106.9 | B2 | 183.4 | 0.61 | s2 | n | y | d2
TN_2019_1356 |  |  | 07-F88906 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.27 | 15 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 55 | 12 | No | 2019-02-12 | C_s2_d1 | 1.45 | 15.2 | 45.2 | 699 | 115.1 | C | 312.8 | 0.99 | s2 | y | n | d1
TN_2019_1357 |  |  | Roll | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.54 | 14 | Vilanova | SXLPE+05AFFPIT+20AESPIT | CD | 48 | 14.4 | No | 2019-02-12 | C_s2_d1 | 1.29 | 13.3 | 33 | 687 | 93.2 | C | 282.5 | 0.68 | s2 | y | n | d1
TN_2019_1358 |  |  | Roll | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.32 | 15 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 33 | 17.5 | No | 2019-02-12 | C_s2_d1 | 1.57 | 17.3 | 40.3 | 687 | 114.5 | C | 337.7 | 0.81 | s2 | y | n | d1
19020011 |  | 17671 | -- | K25 5G1.50-SH-NF F 55-625-255 | 13 | 12 | Paron | ID3100/SV3300FR+RUBANSCAPALONGITUDINAL+0400FEIT+5300SEIT | -- | 27 | 20.5 | No | 2019-02-13 | C_s2_d2 | 1.36 | 13.8 | 30.8 | 849 | 59 | C | 61 | 0.21 | s2 | y | y | d2
19020012 |  | 17671 | -- | K25 5G1.50-SH-NF F 55-625-255 | 12.4 | 13 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 26.2 | 21.2 | No | 2019-02-13 | C_s1_d2 | 1.29 | 19 | 36.8 | 981 | 55 | C | 50 | 0.16 | s1 | y | y | d2
|  | 997006 | 09T5491 | RZ1 300/500 3G4 | 10.4 | 15 | Manlleu | TPR-551.10MM | -- | 35 | 20 | No | 2019-02-12 | D_s1_d2 | 2.81 | 35.1 | 72.5 | 1479 | 61.5 | D | 34 | 0.12 | s1 | Y | Y | d2
|  | 997007 | 09T5491 | RZ1 300/500 3G4 | 11.1 | 14 | Manlleu | TPR-551.22MM | -- | 35 | 20 | No | 2019-02-12 | C_s1_d2 | 1.98 | 27.5 | 40.8 | 1308 | 55.7 | C | 25.8 | 0.05 | s1 | Y | Y | d2
|  | 997008 | 09T5498 | RZ1 300/500 3G4 | 10.4 | 15 | Manlleu | FPT5621.10MM | -- | 27 | 20 | No | 2019-02-12 | D_s2_d2 | 3.3 | 69.3 | 127.2 | 1449 | 145.6 | D | 80.6 | 0.21 | s2 | y | y | d2
|  | 997009 | 09T5498 | RZ1 300/500 3G4 | 11.25 | 14 | Manlleu | FPT5621.22MM | -- | 35 | 20 | No | 2019-02-12 | E ou F_s2_d2 | 3.3 | 76.9 | 176 | 1293 | 177.7 | E ou F | 95.8 | 0.32 | s2 | Y | Y | d2
|  | 997010 | 09T0775 | RZ1 300/500 3G4 | 10.6 | 14 | Manlleu | TPR-551.00 | -- | 29 | 20 | No | 2019-02-13 | E ou F_s2_d2 | 3.3 | 79.2 | 243 | 1314 | 239.6 | E ou F | 219.2 | 0.03 | s2 | y | y | d2
|  | 997011 | 09T0775 | RZ1 300/500 3G4 | 11 | 14 | Manlleu | TPR-551.22 | -- | 35 | 20 | No | 2019-02-13 | D_s2_d2 | 3.3 | 48.7 | 145.3 | 1497 | 121.4 | D | 93.9 | 0.51 | s2 | y | y | d2
|  | 997013 | 1093773 | RZ1 300/500 3G4 | 10.8 | 14 | Manlleu | FPT1521.22MM | -- | 35 | 20 | No | 2019-02-13 | E ou F_s2_d2 | 3.3 | 80.2 | 214.6 | 1179 | 244.7 | E ou F | 143 | 0.53 | s2 | y | y | d2
19020013 |  | 17672 | -- | FO DROP 2MM 41 D 02 | 4.1 | 75 | Paron | 1700SEES+LUBKO1105A | -- | 27.5 | 22 | No | 2019-02-13 | C_s1_d1 | 1.35 | 13.7 | 34.1 | 687 | 107 | C | 11 | 0.04 | s1 | y | n | d1
|  | 996941 | 13N1452 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 9.8 | 15 | Manlleu | COBERTAFPT562 | '-- | 30 | 20 | No | 2019-02-14 | E ou F_s2_d2 | 3.3 | 75.7 | 122.6 | 1230 | 166.6 | E ou F | 66.2 | 0.22 | s2 | y | y | d2
|  | 996941 | 09J6216 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 9.9 | 15 | Manlleu | COBERTATPR-49/TPR-54 | -- | 30 | 20 | No | 2019-02-14 | B2_s1_d1 | 1.02 | 12 | 24.9 | 768 | 58.8 | B2 | 17 | 0.05 | s1 | y | n | d1
|  | 274108 | 12T4929 | EXZHELLENT RZ1-K (AS) 1KV 1X240 | 29.6 | 6 | Manlleu | PRS-03+TPR-49+TPR-37 | '-- | 26 | 20 | No | 2019-02-15 | B2_s1_d0 | 0.57 | 6.7 | 8.6 | 732 | 25.3 | B2 | 13 | 0.03 | s1 | n | n | d0
|  | 703455 | roll | HO7Z1-K TYPE2 (AS) 1X35MM2 | 10.3 | 15 | Manlleu | TPR-27 | -- | 25 | 20 | No | 2019-02-15 | B2_s1_d0 | 0.55 | 2.6 | 8.1 | 534 | 38 | B2 | 1.4 | 0 | s1 | n | n | d0
19020014 |  | 17685 | -- | NEXANS ALSECURE RZ1-K (AS) 1KV 3G1.5 | 10.3 | 15 | Paron | COMPETITORSAMPLE | -- | 27 | 20.8 | No | 2019-02-15 | D_s2_d2 | 3.3 | 69.6 | 167.7 | 1299 | 168 | D | 78 | 0.36 | s2 | y | y | d2
19020015 |  | 17685 | -- | NEXANS ALSECURE RZ1-K (AS) 1KV 5G2.5 | 12.8 | 12 | Paron | COMPETITORSAMPLE | -- | 28.3 | 20.3 | No | 2019-02-15 | D_s1_d2 | 2.44 | 28.7 | 42.5 | 897 | 73 | D | 48 | 0.1 | s1 | y | y | d2
19020014 |  | 17685 | -- | NEXANS ALSECURE RZ1-K (AS) 1KV 3G2.5 | 10.9 | 14 | Paron | COMPETITORSAMPLE | -- | 28.2 | 22.3 | No | 2019-02-15 | C_s1_d1 | 1.9 | 20.6 | 31.8 | 885 | 54 | C | 32 | 0.07 | s1 | y | n | d1
19020017 |  | 17685 | -- | ALCOBRE RZ1-K (AS) 1KV 3G2.5 | 9.75 | 15 | Paron | COMPETITORSAMPLE | -- | 27.1 | 20.3 | No | 2019-02-18 | D_s2_d2 | 2.25 | 25.4 | 52.8 | 717 | 141 | D | 61 | 0.13 | s2 | y | y | d2
19020018 |  | 17685 | -- | ALCOBRE RZ1-K (AS) 1KV 3G1.5 | 10.48 | 15 | Paron | COMPETITORSAMPLE | -- | 28.9 | 19.9 | No | 2019-02-18 | D_s2_d2 | 3.3 | 69.7 | 165.3 | 1302 | 166 | D | 185 | 0.65 | s2 | y | y | d2
|  | 274766 | 699517 | EXZHELLENT RZ1-K (AS) 1KV 3G2.5 | 11.3 | 14 | Manlleu | PRS-03SKINVPE-08+TPR-49+TPR-54 | -- | 25 | 20 | No | 2019-02-15 | C_s1_d0 | 1.12 | 16.5 | 23.6 | 1473 | 43.9 | C | 25.1 | 0.11 | s1 | n | n | d0
19020019 |  | 17685 | -- | ALCOBRE RZ1-K (AS) 1KV 5G2.5 | 12.7 | 12 | Paron | COMPETITORSAMPLE | -- | 30.5 | 21.8 | No | 2019-02-20 | E ou F_s2_d2 | 3.3 | 97.1 | 265.7 | 1305 | 264 | E ou F | 251 | 1.02 | s2 | y | y | d2
19020020 |  | 17685 | -- | CABELTE RZ1-K (AS) 1KV 5G1.5 | 12 | 13 | Paron | COMPETITORSAMPLE | -- | 33.6 | 21.5 | No | 2019-02-20 | D_s1_d1 | 2.24 | 32.7 | 47.2 | 1053 | 70 | D | 46 | 0.08 | s1 | y | n | d1
TN_2019_1359 |  |  | 454416F | PRYSMIAN EPROTENAX DHVMV 2RH 6/10 KV 3X120 | 66.98 | 3 | Vilanova | PVC2400 | OD | 53.8 | 8.6 | No | 2019-02-13 | B2_s3_d2 | 0.61 | 10.5 | 12.1 | 756 | 34.7 | B2 | 1102.7 | 1.27 | s3 | n | y | d2
TN_2019_1360 |  | 69812 | 475782E | AL-AFUMEX DZ1F3Z1 2X150 | 48.68 | 4 | Vilanova | FLEJEDEACERO+COLA+LANTOR+CPRDMZ-E | CD | 53.3 | 15.6 | No | 2019-02-19 | B2_s1_d2 | 0.69 | 5.9 | 10.4 | 798 | 22.9 | B2 | 5.9 | 0.01 | s1 | n | y | d2
TN_2019_1361 |  | 69810 | 514545N | AL-AFUMEX DZ1F3Z1 3X16 | 29.03 | 6 | Vilanova | FLEJEDEACERO+COLA+LANTOR+CPRDMZ-E | CD | 61.5 | 15.9 | No | 2019-02-19 | B2_s1_d2 | 0.72 | 8.8 | 15.2 | 1500 | 30.1 | B2 | 9.9 | 0.04 | s1 | n | y | d2
TN_2019_1362 |  | 69811 | 506981S | AL-AFUMEX DZ1F3Z1 3X25 | 32.05 | 6 | Vilanova | FLEJEDEACERO+COLA+LANTOR+CPRDMZ-E | CD | 72.3 | 11.2 | No | 2019-02-20 | B2_s1_d2 | 0.57 | 8 | 10.4 | 1473 | 29.3 | B2 | 4.5 | 0.01 | s1 | n | y | d2
19020021 |  | 17685 | -- | CABELTE RZ1-K (AS) 1KV 5G2.5 | 14 | 11 | Paron | COMPETITORSAMPLE | -- | 33.2 | 23.3 | No | 2019-02-20 | C_s1_d0 | 1.4 | 21.5 | 36.6 | 1125 | 58 | C | 40 | 0.12 | s1 | n | n | d0
|  | 274511 | 697305 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.4 | 15 | Manlleu | PRS-03SKINVPE-08+TPR-49+TPR-54 | '-- | 30 | 20 | No | 2019-02-19 | D_s1_d0 | 2.38 | 29.6 | 42.6 | 1125 | 52.3 | D | 20.6 | 0.05 | s1 | n | n | d0
|  | 274850 | 08S9202 | EXZHELLENT RZ1-K-M (AS) 1KV 1X185 | 26.7 | 6 | Manlleu | PRS-03+TPR-49+TPR-37 | '-- | 30 | 20 | No | 2019-02-19 | B2_s1_d0 | 0.43 | 4.1 | 7.3 | 708 | 20.7 | B2 | 2 | 0.01 | s1 | n | n | d0
|  | 703765 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.9 | 165 | Manlleu | TPR-52+SKINTPR-53 | '-- | 25 | 30 | No | 2019-02-19 | D_s1_d2 | 2.07 | 20.3 | 40.4 | 879 | 92.7 | D | 34.7 | 0.06 | s1 | n | s | d2
TN_2019_1363 |  |  | 419862X | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.32 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 71.9 | 11.8 | No | 2019-02-20 | C_s1_d2 | 1.72 | 24.9 | 35.3 | 945 | 56.7 | C | 32.7 | 0.09 | s1 | n | y | d2
TN_2019_1364 |  |  | 419862X | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.32 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 65.3 | 14.2 | No | 2019-02-20 | C_s1_d2 | 1.32 | 22.2 | 30.3 | 1116 | 48.9 | C | 26.7 | 0.06 | s1 | n | y | d2
TN_2019_1366 |  |  | T7-F88898 | FG16R16 1X6 MM² - 0.6/1 KV | 8.14 | 19 | Vilanova | SXLPE+20AGSPIT | CD | 68.1 | 9.9 | No | 2019-02-21 | B2_s2_d2 | 1.41 | 11.4 | 26.5 | 576 | 101.5 | B2 | 380.3 | 0.89 | s2 | n | y | d2
TN_2019_1367 |  |  | T7-D36068 | FG16R16 1X6 MM² - 0.6/1 KV | 7.17 | 21 | Vilanova | SXLPE+20AGSPIT | CD | 64.7 | 13.1 | No | 2019-02-21 | B2_s2_d2 | 0.66 | 4.7 | 18.4 | 522 | 83.9 | B2 | 87.1 | 0.34 | s2 | n | y | d2
TN_2019_1368 |  |  | TE-H85998 | FG16OR16 2X70MM² - 0.6/1 KV | 30.81 | 6 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 58.3 | 17 | No | 2019-02-21 | C_s3_d2 | 1.32 | 21.2 | 54.4 | 1365 | 51.5 | C | 406.7 | 0.91 | s3 | n | y | d2
TN_2019_1369 |  |  | T8-G76105 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.05 | 13 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 68.6 | 11.1 | No | 2019-02-22 | C_s3_d1 | 1.96 | 29.1 | 52.8 | 765 | 115.3 | C | 557.3 | 0.9 | s3 | y | n | d1
TN_2019_1370 |  |  | T8-G76050 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.45 | 14 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 61 | 15 | No | 2019-02-22 | D_s3_d2 | 3.3 | 63.3 | 100 | 1353 | 141.1 | D | 1049.3 | 1.6 | s3 | n | y | d2
TN_2019_1371 |  |  | T9-F94954 | FG16R16 1X10MM² - 0.6/1 KV | 8.47 | 19 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 53.3 | 17.5 | No | 2019-02-22 | B2_s2_d2 | 0.99 | 7.2 | 18 | 723 | 59.8 | B2 | 125.6 | 0.36 | s2 | n | y | d2
TN_2019_1372 |  |  | TF-H11467 | FG16R16 1X240MM² - 0.6/1 KV | 27.94 | 6 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 47.1 | 19.8 | No | 2019-02-22 | C_s2_d2 | 1.43 | 17.4 | 44.4 | 1497 | 37.7 | C | 214.5 | 0.56 | s2 | n | y | d2
19020022 |  | 17685 | -- | EXZHELLENT RZ1-K (AS) 1KV 2X2.5 | 10.85 | 14 | Paron | ??? | -- | 28.3 | 22.6 |  | 2019-02-22 | C_s1_d0 | 1.7 | 20.7 | 31.5 | 1074 | 43 | C | 41 | 0.1 | s1 | n | n | d0
19010023 |  | 17657 | roll | FTG18OM16 0.6/1KV 5X1.5MM² | 18 | 8 | Paron | MICA+SD3500IT+SCAPA+0400FPIT+5300SEIT | -- | 30.4 | 21.6 | No | 2019-02-22 | B2_s1_d0 | 0.57 | 4 | 6.3 | 618 | 24 | B2 | 4 | 0.01 | s1 | n | n | d0
19020024 |  | 17685 | -- | CABELTE RZ1-K (AS) 1KV 3G2.5 | 11 | 14 | Paron | COMPETITORSAMPLE | -- | 32.8 | 20.9 | No | 2019-02-22 | C_s1_d1 | 1.7 | 21.2 | 30.3 | 1110 | 43 | C | 34 | 0.07 | s1 | y | n | d1
19020025 |  | 17685 | -- | CABELTE RZ1-K (AS) 1KV 3G1.5 | 8.4 | 19 | Paron | COMPETITORSAMPLE | -- | 33.6 | 22.5 | No | 2019-02-22 | D_s2_d2 | 3.3 | 66 | 399 | 954 | 610 | D | 131 | 1.19 | s2 | y | y | d2
TN_2019_1373 |  |  | T8-G76103 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.45 | 15 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 65.5 | 11.3 | No | 2019-02-24 | C_s3_d2 | 1.99 | 25.6 | 52.4 | 654 | 154.1 | C | 576.9 | 1.21 | s3 | n | y | d2
TN_2019_1374 |  |  | T9-F96483 | FG16R16 1X50MM² - 0.6/1 KV | 14.75 | 10 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 57.6 | 14 | No | 2019-02-24 | D_s3_d2 | 2.95 | 37.7 | 69.6 | 1059 | 118.3 | D | 633.8 | 1.12 | s3 | n | y | d2
TN_2019_1375 |  |  | T8-G71608 | FG16R16 1X16MM² - 0.6/1 KV | 9.51 | 15 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 49 | 16.7 | No | 2019-02-24 | B2_s2_d1 | 1.19 | 11.3 | 29.1 | 621 | 91.1 | B2 | 188.2 | 0.5 | s2 | y | n | d1
TN_2019_1376 |  |  | T8-G71614 | FG16R16 1X25MM² - 0.6/1 KV | 11.4 | 14 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 47.4 | 18.3 | No | 2019-02-24 | D_s3_d2 | 3.3 | 36 | 62.6 | 843 | 115.2 | D | 683.7 | 1.14 | s3 | n | y | d2
TN_2019_1377 |  |  | T8-G76020 | FG16R16 1X35MM² - 0.6/1 KV | 12.8 | 12 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 71.5 | 10 | No | 2019-02-25 | C_s2_d2 | 1.55 | 21.2 | 43.2 | 807 | 85.8 | C | 282.9 | 0.72 | s2 | n | y | d2
TN_2019_1378 |  |  | T7-D36066 | FG16R16 1X16MM² - 0.6/1 KV | 8.04 | 19 | Vilanova | SXLPE+05AHFPIT+20AGSPIT | CD | 64.3 | 12.6 | No | 2019-02-25 | C_s2_d2 | 1.5 | 11.8 | 35.9 | 600 | 129.5 | C | 312.8 | 0.93 | s2 | n | y | d2
TN_2019_1379 |  |  | TF-H11467 | FG16R16 1X240MM² - 0.6/1 KV | 27.94 | 6 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 61.7 | 14.8 | No | 2019-02-25 | D_s2_d2 | 1.64 | 21.8 | 70.2 | 1482 | 59.4 | D | 261.2 | 0.87 | s2 | n | y | d2
TN_2019_1380 |  |  | T8-G76105 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.05 | 13 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 58.6 | 16.9 | No | 2019-02-25 | D_s3_d2 | 2.25 | 31 | 53 | 846 | 117.6 | D | 584.1 | 0.86 | s3 | n | y | d2
TN_2019_1381 |  |  | T9-F94954 | FG16R16 1X10MM² - 0.6/1 KV | 8.47 | 19 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 59 | 13.7 | No | 2019-02-26 | B2_s2_d1 | 0.62 | 10.3 | 20.2 | 591 | 74.6 | B2 | 102 | 0.32 | s2 | y | n | d1
19020026 |  | 17672 | -- | FO DROP 1MM 29 D 01 | 3 | 165 | Paron | 1700SEES | -- | 27.3 | 21.9 | No | 2019-02-27 | B2_s1_d1 | 1.2 | 11.9 | 29 | 588 | 125 | B2 | 27 | 0.05 | s1 | y | n | d1
TN_2019_1382 |  |  | T8-G76103 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.45 | 15 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 67.3 | 10 | No | 2019-02-27 | C_s3_d2 | 1.88 | 26.8 | 51.2 | 672 | 152.1 | C | 494.6 | 1.09 | s3 | n | y | d2
TN_2019_1383 |  |  | TE-H85998 | FG16OR16 2X70MM² - 0.6/1 KV | 30.81 | 6 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 67 | 10.4 | No | 2019-02-27 | C_s3_d2 | 1.23 | 22.6 | 47.3 | 1245 | 50 | C | 731.5 | 1.34 | s3 | n | y | d2
TN_2019_1384 |  |  | TF-H11467 | FG16R16 1X240MM² - 0.6/1 KV | 27.94 | 6 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 63.9 | 13.7 | No | 2019-02-27 | C_s2_d2 | 1.32 | 16.7 | 39.9 | 1365 | 47.1 | C | 178.9 | 0.42 | s2 | n | y | d2
TN_2019_1385 |  |  | T9-F96483 | FG16R16 1X50MM² - 0.6/1 KV | 14.75 | 10 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 56.8 | 16.1 | No | 2019-02-27 | D_s3_d2 | 3.3 | 42.6 | 84.9 | 1041 | 114.5 | D | 763.1 | 1.31 | s3 | n | y | d2
TN_2019_1386 |  |  | T8-G71608 | FG16R16 1X16MM² - 0.6/1 KV | 9.51 | 15 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 54.2 | 19.7 | No | 2019-02-27 | B2_s2_d1 | 1.07 | 13.1 | 24.5 | 735 | 74 | B2 | 151.3 | 0.37 | s2 | y | n | d1
|  |  | A11082789 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 1X150 | 21.6 | 7 | Manlleu | COMPETITORSAMPLE | '-- | 34 | 20 | No | 2019-02-22 | B2_s1_d0 | 0.29 | 2 | 2.9 | 303 | 0 | B2 | 0.9 | 0 | s1 | n | n | d0
|  |  | 31112110 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 3G2.5 | 11.4 | 14 | Manlleu | COMPETITORSAMPLE | '-- | 34 | 20 | No | 2019-02-22 | B2_s1_d0 | 0.71 | 11.5 | 23.9 | 771 | 45 | B2 | 8.3 | 0.02 | s1 | n | n | d0
|  |  | 2986992 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 3G1.5 | 14.4 | 11 | Manlleu | COMPETITORSAMPLE | '-- | 32 | 20 | No | 2019-02-22 | C_s1_d0 | 1.11 | 15.9 | 27.3 | 999 | 41.8 | C | 15.9 | 0.03 | s1 | n | n | d0
|  |  | A12090582 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 1X240 | 26.6 | 6 | Manlleu | COMPETITORSAMPLE | '-- | 33 | 20 | No | 2019-02-22 | B2_s1_d0 | 0.43 | 0.9 | 2.5 | 1500 | 0 | B2 | 0.8 | 0 | s1 | n | n | d0
|  |  | 080P07249 | NEXANS ALSECURE RZ1-K (AS) 1KV 1X150 | 22.3 | 7 | Manlleu | COMPETITORSAMPLE | '-- | 35 | 20 | No | 2019-02-22 | B2_s1_d2 | 0.51 | 4.1 | 7 | 1452 | 12.2 | B2 | 2.3 | 0.01 | s1 | s | n | d2
|  |  | 083750J | MIGUELEZ AFIRENAS-X RZ1-K (AS) 1X150 | 22.4 | 7 | Manlleu | COMPETITORSAMPLE | '-- | 33 | 20 | No | 2019-02-22 | C_s1_d2 | 0.93 | 12 | 35.3 | 1443 | 30.9 | C | 7.7 | 0.04 | s1 | s | s | d2
|  |  | 062971G | MIGUELEZ AFIRENAS-X RZ1-K (AS) 1X150 | 11.6 | 13 | Manlleu | COMPETITORSAMPLE | '-- | 33 | 20 | No | 2019-02-26 | B2_s1_d0 | 0.73 | 9.2 | 19 | 885 | 33.2 | B2 | 19.9 | 0.04 | s1 | n | n | d0
|  |  | 996997 | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.3 | 3 | Manlleu | SMC-21+PRC-07+SMC-01+FPO162+SMC-17SOLAPEDARRERA | '-- | 29 | 20 | No | 2019-02-26 | C_s1_d2 | 1.24 | 16.7 | 21.9 | 1197 | 31.2 | C | 1 | 0.01 | s1 | s | n | d2
|  |  | 409497 | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 77.2 | 3 | Manlleu | SMC-21+PRC-07+SMC-01+TPO-03+SMC-17SOLAPEDAVANT | '-- | 32 | 20 | No | 2019-02-26 | B2_s1_d0 | 0.78 | 6.4 | 9.2 | 915 | 17.5 | B2 | 8.3 | 0.02 | s1 | n | n | d0
|  |  | 409497 | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 77.2 | 3 | Manlleu | SMC-21+PRC-07+SMC-01+TPO-03+SMC-17SOLAPEDARRERA | '-- | 32 | 20 | No | 2019-02-26 | B2_s1_d0 | 0.88 | 9.1 | 11.9 | 915 | 21.2 | B2 | 9.8 | 0.03 | s1 | n | n | d0
|  | 12T1978 | 997025 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.2 | 15 | Manlleu | PRS-03SKINFPE144+TPR-49+TPR-54 | '-- | 30 | 20 | No | 2019-02-27 | E ou F_s2_d2 | 3.3 | 74.5 | 142.8 | 1407 | 129.9 | E ou F | 91.7 | 0.3 | s2 | s | s | d2
|  | 12T1978 | 997027 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.3 | 15 | Manlleu | PRS-03SKINFPE144+TPR-49+TPR-54 | '-- | 30 | 20 | No | 2019-02-27 | D_s1_d0 | 2.53 | 38.2 | 52.1 | 1389 | 76.6 | D | 38.4 | 0.08 | s1 | n | n | d0
|  |  | 063P005105 | NEXANS ALSECURE RZ1-K (AS) 1KV 3G2.5 | 11.1 | 14 | Manlleu | COMPETITORSAMPLE | '-- | 31 | 20 | No | 2019-02-27 | E ou F_s2_d2 | 3.3 | 84.2 | 196.8 | 1095 | 259.2 | E ou F | 79.5 | 0.24 | s2 | s | s | d2
|  |  | 080P06085 | NEXANS ALSECURE RZ1-K (AS) 1KV 1X240 | 28.3 | 6 | Manlleu | COMPETITORSAMPLE | '-- | 30 | 20 | No | 2019-02-27 | C_s1_d2 | 0.97 | 15.8 | 42.9 | 1500 | 35.8 | C | 5.8 | 0.04 | s1 | s | s | d2
|  |  | 409705 | HEPRZ1(AS) 1X630MM2 18/30KV | 58.2 | 4 | Manlleu | SMC-01+GOM-14+SMC-05+TPR-49+TPO-03 | '-- | 30 | 20 | No | 2019-03-04 | B2_s1_d0 | 1.43 | 14.2 | 19.9 | 921 | 37 | B2 | 32.8 | 0.15 | s1 | n | n | d0
|  | 08S7839 | 996995 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 9.8 | 15 | Manlleu | PRS-03SKINTPR-45+TPR-49+TPR-45 | '-- | 31 | 20 | No | 2019-03-04 | D_s2_d2 | 3.3 | 67.3 | 121.9 | 1485 | 115.8 | D | 82.6 | 0.37 | s2 | S | S | d2
|  |  | 104162F | MIGUELEZ AFIRENAS-X RZ1-K (AS) 1X240 | 27.2 | 6 | Manlleu | COMPETITORSAMPLE | '-- | 30 | 20 | No | 2019-03-04 | C_s1_d2 | 1.12 | 16.7 | 39.5 | 1500 | 33 | C | 9.6 | 0.04 | s1 | S | S | d2
19030001 |  | 17712 | -- | K25 5G1.50-SH-NF F 55-625-255 | 12.7 | 12 | Paron | ID3100/SV3300FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 33.6 | 23 | No | 2019-03-05 | B2_s1_d2 | 0.89 | 13.1 | 26.5 | 867 | 47 | B2 | 21 | 0.05 | s1 | y | y | d2
19030002 |  | 17719 | roll | HO7Z1-U AFUMEX PLUS FRANCE 1X1.5 | 2.84 | 180 | Paron | 1602SEES | -- | 33.3 | 24.1 | No | 2019-03-05 | B2_s1_d0 | 0.69 | 5.2 | 12.9 | 603 | 44 | B2 | 11 | 0.03 | s1 | n | n | d0
TN_2019_1387 |  |  | T8-G71614 | FG16R16 1X25MM² - 0.6/1 KV | 11.4 | 14 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 53.8 | 13 | No | 2019-02-28 | D_s3_d2 | 3.3 | 44.4 | 75.9 | 864 | 182.2 | D | 807 | 1.47 | s3 | n | y | d2
TN_2019_1388 |  |  | T8-G76020 | FG16R16 1X35MM² - 0.6/1 KV | 12.8 | 12 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 50.5 | 14 | No | 2019-02-28 | D_s3_d2 | 3.3 | 34.7 | 52.9 | 783 | 109.8 | D | 800.4 | 1.3 | s3 | n | y | d2
TN_2019_1389 |  |  | T8-G76050 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.45 | 14 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 42.8 | 16.9 | No | 2019-02-28 | D_s3_d2 | 33 | 64.2 | 148.1 | 1209 | 162.9 | D | 1117.1 | 2.23 | s3 | n | y | d2
TN_2019_1390 |  |  | T7-D36067 | FG16R16 1X6 MM² - 0.6/1 KV | 7.47 | 21 | Vilanova | SXLPE+05AHFPIT+20AGSPIT | CD | 37.6 | 19.9 | No | 2019-02-28 | D_s3_d2 | 3.3 | 30.7 | 52.6 | 1041 | 152.3 | D | 771.2 | 1.41 | s3 | n | y | d2
TN_2019_1391 |  |  | T7-D36213 | FG16OR16 5G1.5 MM² - 0.6/1 KV | 11.44 | 14 | Vilanova | SXLPE+05AHFPIT+20AGSPIT | CD | 45.7 | 21.1 | No | 2019-02-28 | D_s3_d2 | 2.42 | 25.4 | 38.2 | 852 | 95.3 | D | 508.7 | 0.65 | s3 | n | y | d2
TN_2019_1392 |  |  | T7-D36065 | FG16OR16 5G1.5 MM² - 0.6/1 KV | 11.43 | 14 | Vilanova | SXLPE+05AHFPIT+20AGSPIT | CD | 66.6 | 12.9 | No | 2019-03-05 | D_s3_d1 | 2.65 | 36.9 | 56.1 | 699 | 147.6 | D | 624.9 | 1.02 | s3 | y | n | d1
TN_2019_1393 |  |  | T7-F88903 | FG16OR16 5G1.5 MM² - 0.6/1 KV | 11.49 | 14 | Vilanova | SXLPE+05AHFPIT+20AGSPIT | CD | 65.5 | 13.4 | No | 2019-03-05 | D_s3_d2 | 3.3 | 41.1 | 105.6 | 1422 | 94.1 | D | 1270.6 | 2.22 | s3 | n | y | d2
TN_2019_1394 |  |  | TF-K14001 | AFUMEX CLASS RZ1-K (AS) 1KV 5G10 | 18.78 | 8 | Vilanova | 1602N–LOTTO82742021 | CD | 53.5 | 16.5 | No | 2019-03-05 | C_s1_d2 | 0.86 | 11.9 | 30.7 | 1497 | 25.6 | C | 15.4 | 0.03 | s1 | n | y | d2
TN_2019_1395 |  |  | TG-H43303 | AFUMEX CLASS RZ1-K (AS) 1KV 5G10 | 18.51 | 8 | Vilanova | 1602N–LOTTO82742021 | CD | 41.7 | 17.9 | No | 2019-03-05 | C_s1_d2 | 1 | 14.5 | 35.5 | 1365 | 33.4 | C | 13.5 | 0.03 | s1 | n | y | d2
TN_2019_1396 |  |  | TF-H34238 | AFUMEX CLASS RZ1-K (AS) 1KV 5G10 | 18.95 | 8 | Vilanova | 1602N–LOTTO82742021 | CD | 70.5 | 14.4 | No | 2019-03-06 | B2_s1_d2 | 1.03 | 11.4 | 28.2 | 1500 | 23.6 | B2 | 7.9 | 0.03 | s1 | n | y | d2
TN_2019_1397 |  |  | TE-H13615 | AFUMEX CLASS RZ1-K (AS) 1KV 5G10 | 18.92 | 8 | Vilanova | 1602N–LOTTO82742021 | CD | 69.9 | 14.9 | No | 2019-03-06 | C_s1_d2 | 0.97 | 14.8 | 35.1 | 1413 | 31.6 | C | 8.2 | 0.03 | s1 | n | y | d2
TN_2019_1398 |  | OP70755 20289847 | 523093E | AL-VOLTALENE XZ1(AS)1X50K 0.6/1.0KV | 16.86 | 9 | Vilanova | XLPE+1420+6000 | CD | 69.3 | 16 | No | 2019-03-06 | D_s1_d2 | 2.53 | 43.4 | 81.5 | 1335 | 81.9 | D | 39.5 | 0.07 | s1 | n | y | d2
TN_2019_1399 |  | OP70733 20215693 | 523236K | AL-VOLTALENE XZ1(AS)1X240K 0.6/1.0KV | 27.89 | 6 | Vilanova | XLPE+1420+6000 | CD | 68.2 | 16.7 | No | 2019-03-06 | B2_s1_d2 | 0.9 | 13.4 | 25.1 | 1497 | 35.9 | B2 | 21.3 | 0.05 | s1 | n | y | d2
TN_2019_1400 |  |  | TE-H85998 | FG16OR16 2X70MM² - 0.6/1 KV | 30.81 | 6 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 70.8 | 17 | No | 2019-03-06 | C_s3_d2 | 0.98 | 17.4 | 34.6 | 1173 | 39.7 | C | 453.2 | 0.66 | s3 | n | y | d2
19030003 |  | 17720 | BBT 908292 | 1800-S-1X240MM²-SH-NF F 55-625-255 | 31.5 | 6 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 33.6 | 23.5 | No | 2019-03-07 | B2_s1_d1 | 0.49 | 4.5 | 5.8 | 678 | 20 | B2 | 3 | 0 | s1 | y | n | d1
19030004 |  | 17720 | ACP 01518391 | 750-3G6-SH-NF F 55-625-255 | 14.8 | 10 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 32.6 | 23.1 | No | 2019-03-07 | B2_s1_d2 | 0.69 | 6.7 | 9.8 | 1158 | 24 | B2 | 7 | 0.01 | s1 | y | y | d2
19030005 |  | 17720 | BBT 908292 | 750-3G1.5-SH-NF F 55-625-255 | 10.4 | 15 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 31.2 | 24 | No | 2019-03-07 | C_s1_d2 | 1.39 | 17.8 | 43.7 | 810 | 86 | C | 41 | 0.12 | s1 | y | y | d2
|  |  | 062972G | MIGUELEZ AFIRENAS-X RZ1-K 3G1.5 | 11.1 | 14 | Manlleu | COMPETITORSAMPLE | '-- | 30 | 20 | No | 2019-03-04 | C_s1_d2 | 1.46 | 16.3 | 24.4 | 891 | 41.6 | C | 5.7 | 0.02 | s1 | Y | Y | d2
|  |  | 063P05107 | NEXANS ALSECURE RZ1-K 3G1.5 | 9.9 | 15 | Manlleu | COMPETITORSAMPLE | '-- | 30 | 20 | No | 2019-03-04 | C_s1_d0 | 1.86 | 22.5 | 31.5 | 1482 | 58.5 | C | 36.1 | 0.06 | s1 | n | n | d0
|  | 69812 | 475782E | AL-AFUMEX DZ1F3Z1 2X150 | 49.5 | 4 | Manlleu | IRN267+6000SEES | '-- | 30 | 20 | No | 2019-03-06 | B2_s1_d0 | 0.67 | 6.3 | 8.5 | 849 | 22.5 | B2 | 4.7 | 0.01 | s1 | n | n | d0
|  | 69810 | 514545N | AL-AFUMEX DZ1F3Z1 3X16 | 29.9 | 6 | Manlleu | IRN267+6000SEES | '-- | 30 | 20 | No | 2019-03-06 | B2_s1_d2 | 0.6 | 7.8 | 12.2 | 1500 | 25.8 | B2 | 1.9 | 0.01 | s1 | y | y | d2
|  | 69811 | 506981S | AL-AFUMEX DZ1F3Z1 3X25 | 32.8 | 6 | Manlleu | IRN267+6000SEES | '-- | 30 | 20 | No | 2019-03-06 | B2_s1_d2 | 0.72 | 6.6 | 7.8 | 1176 | 21.5 | B2 | 4.6 | 0.02 | s1 | y | y | d2
|  | 69984 | 524389N | DZ1 ADIF DCA 3.6/6KV 1X 95MM² CU | 22.4 | 7 | Manlleu | IRN267+6000SEES | '-- | 35 | 20 | No | 2019-03-07 | E ou F_s2_d2 | 3.3 | 93.8 | 241.7 | 1500 | 201.4 | E ou F | 112.4 | 0.61 | s2 | y | y | d2
|  | 69986 | 524384H | DZ1 ADIF DCA 3.6/6KV 1X 95MM² CU | 22.1 | 7 | Manlleu | IRN267+6000SEES | '-- | 32 | 20 | No | 2019-03-07 | E ou F_s2_d2 | 3.3 | 100.3 | 231.7 | 1494 | 198.4 | E ou F | 127.2 | 0.54 | s2 | y | y | d2
|  | 997032 | 12T5948 | FG17 1X240 | 24.4 | 7 | Manlleu | FPS152 | '-- | 35 | 20 | No | 2019-03-07 | B2_s1_d1 | 0.7 | 5.9 | 7.4 | 1500 | 27.6 | B2 | 1.6 | 0.01 | s1 | y | n | d1
TN_2019_1401 |  |  | TF-H11467 | FG16R16 1X240MM² - 0.6/1 KV | 27.94 | 6 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 52.6 | 13.6 | No | 2019-03-07 | C_s2_d2 | 1.3 | 16.8 | 42.3 | 1413 | 38 | C | 210 | 0.44 | s2 | n | y | d2
TN_2019_1402 |  |  | T8-G76105 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.05 | 13 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 51 | 14.1 | No | 2019-03-07 | D_s3_d2 | 2.08 | 29.3 | 49.2 | 756 | 109.5 | D | 599.7 | 0.98 | s3 | n | y | d2
TN_2019_1403 |  |  | T8-G76103 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.45 | 15 | Vilanova | SXLPE+05AGFPIT+20AFSPIT | CD | 35.3 | 19.2 | No | 2019-03-07 | D_s3_d2 | 2.75 | 32.4 | 52.2 | 696 | 136 | D | 714.5 | 1.07 | s3 | n | y | d2
|  | 69990 | 523057R | AL-DZ1 ADIF B2CA 3.6/6KV FILLER+ DMZ2 95MM2 | 24.3 | 7 | Manlleu | IRN267+1420FEES+6000SEES | '-- | 33 | 20 | No | 2019-03-08 | D_s1_d2 | 1.81 | 26.4 | 62 | 1497 | 51.8 | D | 31.2 | 0.08 | s1 | Y | Y | d2
TN_2019_1404 |  |  | T7-F88926 | FG16OR16 2X1.5MM² - 0.6/1 KV | 9.46 | 17 | Vilanova | PROT_FILLER=0.1MM_LAV | CD | 54.8 | 10.8 | No | 2019-03-08 | B2_s2_d0 | 0.77 | 7.8 | 21.4 | 588 | 74.4 | B2 | 172.1 | 0.59 | s2 | n | n | d0
TN_2019_1405 |  |  | T8-G72118 | FG16OR16 3G1.5 MM² - 0.6/1 KV | 9.97 | 15 | Vilanova | PROT_FILLER=0.1MM_LAV | CD | 57.1 | 10.7 | No | 2019-03-08 | C_s2_d0 | 1.5 | 11.9 | 38.8 | 672 | 104.4 | C | 280 | 0.8 | s2 | n | n | d0
TN_2019_1406 |  |  | T7-F88902 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.12 | 13 | Vilanova | PROT_FILLER=0.72MM_LA | CD | 42.3 | 16.3 | No | 2019-03-08 | C_s2_d1 | 1.23 | 16.8 | 36.4 | 801 | 72.7 | C | 280.4 | 0.62 | s2 | y | n | d1
TN_2019_1407 |  |  | T8-G76246 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 11.21 | 14 | Vilanova | SXLPE+05ABFPIT+2000SPIT | CD | 35.8 | 18.2 | No | 2019-03-08 | C_s2_d0 | 1.51 | 18.9 | 38.3 | 732 | 89.3 | C | 274 | 0.6 | s2 | n | n | d0
TN_2019_1408 |  | OP70755 20289847 | 523093E | AL-VOLTALENE XZ1(AS)1X50K 0.6/1.0KV | 16.86 | 9 | Vilanova | XLPE+1420+6000 | CD | 56.3 | 16.3 | No | 2019-03-11 | C_s1_d2 | 1.58 | 29.1 | 49.7 | 1383 | 61.7 | C | 24.9 | 0.08 | s1 | n | y | d2
|  | 69985 | 508016S | DZ1 ADIF DCA 3.6/6KV 1X 300MM² CU | 31.6 | 6 | Manlleu | IRN267+6000SEES | '-- | 30 | 20 | No | 2019-03-08 | B2_s1_d1 | 1.02 | 10.7 | 20 | 684 | 57.9 | B2 | 26.3 | 0.08 | s1 | y | n | d1
|  | UF723718 OF68833 | 489603C | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44.38 | 5 | Ceis | XLPE+1420FEES+6000SEES | -- | 47 | 7.81 | No | 2019-02-04 | D_s1_d2 | 2.15 | 68 | 89.2 | 1353 | 121.7 | D | 23.2 | 0.06 | s1 | y | y | d2
|  | UF723718 OF68833 | 489603C | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 44 | 5 | Ceis | XLPE+1420FEES+6000SEES | -- | 43 | 14.2 | No | 2019-03-12 | D_s1_d2 | 1.9 | 40.5 | 52.4 | 1494 | 73.8 | D | 12 | 0.02 | s1 | y | y | d2
19030006 |  | 17731 | -- | CÂBLE 32FO (8X4) KT(XS) FILLED | 13.1 | 12 | Paron | TPR-37 | -- | 26.4 | 22.3 | No | 2019-03-12 | E ou F_s2_d2 | 3.3 | 80 | 172.2 | 1428 | 154 | E ou F | 243 | 1.03 | s2 | y | y | d2
19030007 |  | 17731 | -- | CÂBLE 32FO (8X4) KT(XS) FILLED | 13.1 | 12 | Paron | 1602SEES | -- | 26.8 | 21.1 | No | 2019-03-12 | E ou F_s2_d2 | 3.3 | 105.7 | 192.9 | 1188 | 218 | E ou F | 263 | 0.59 | s2 | y | y | d2
19030009 |  | 17731 | -- | CÂBLE 32FO (8X4) KT(XS) FILLED | 13.4 | 12 | Paron | MEGOLONS548 | -- | 23.2 | 23.1 | No | 2019-03-12 | E ou F_s2_d2 | 3.3 | 87.5 | 176.8 | 1395 | 162 | E ou F | 245 | 0.83 | s2 | y | y | d2
TN_2019_1409 |  |  | TF-H14026+D38D3834:V3835 | AFUMEX CLASS RZ1-K (AS) 1KV 5G2.5 | 13.32 | 12 | Vilanova | PENDINGTOCONFIRM | CD | 61.9 | 17.2 | No | 2019-03-11 | D_s1_d2 | 2.9 | 48.9 | 91.2 | 1497 | 91.8 | D | 43.3 | 0.1 | s1 | n | y | d2
TN_2019_1410 |  |  | TG-H43315 | AFUMEX CLASS RZ1-K (AS) 1KV 5G2.5 | 13.18 | 12 | Vilanova | PENDINGTOCONFIRM | CD | 75.7 | 12.7 | No | 2019-03-12 | D_s2_d2 | 3 | 53.2 | 89.7 | 1161 | 104.3 | D | 57.2 | 0.12 | s2 | n | y | d2
TN_2019_1411 |  |  | TG-H43322 | AFUMEX CLASS RZ1-K (AS) 1KV 5G2.5 | 13.15 | 12 | Vilanova | PENDINGTOCONFIRM | CD | 72 | 14.4 | No | 2019-03-12 | D_s1_d2 | 2.04 | 31.9 | 57.9 | 1497 | 54.3 | D | 36.9 | 0.08 | s1 | n | y | d2
TN_2019_1412 |  |  | TL-C05777-1 | RG16H1M16 1X50 MM² - 12/20 KV | 29.83 | 6 | Vilanova | PENDINGTOCONFIRM | CD | 65.5 | 16.8 | No | 2019-03-12 | B2_s1_d0 | 0.52 | 4.4 | 6.6 | 876 | 12.9 | B2 | 0.4 | 0 | s1 | n | n | d0
TN_2019_1413 |  |  | TL-C05777-2 | RG16H1M16 1X150 MM² - 18/30 KV | 40.45 | 5 | Vilanova | PENDINGTOCONFIRM | CD | 59.8 | 18.5 | No | 2019-03-12 | B2_s1_d0 | 0.57 | 4.2 | 14.6 | 864 | 25.8 | B2 | 0.2 | 0 | s1 | n | n | d0
TN_2019_1414 |  |  | S/N 1 | RG16H1M16 1X95 MM² - 12/20 KV | 32.36 | 6 | Vilanova | PENDINGTOCONFIRM | CD | 70.4 | 13.5 | No | 2019-03-13 | B2_s1_d0 | 0.54 | 6.3 | 7.7 | 780 | 20 | B2 | 4.7 | 0.01 | s1 | n | n | d0
19030010 |  | 17736 | -- | 750-5G10-SH-NF F 55-625-255 | 20.7 | 7 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 34.8 | 22.4 | No | 2019-03-14 | B2_s1_d0 | 0.4 | 2.9 | 3.9 | 807 | 11 | B2 | 3 | 0.01 | s1 | n | n | d0
19030009 |  | 17712 | -- | 750-5G25-SH-NF F 55-625-255 | 29 | 6 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 33.5 | 22.8 | No | 2019-03-14 | B2_s1_d0 | 0.24 | 2 | 4.4 | 609 | 14 | B2 | 3 | 0.01 | s1 | n | n | d0
19030010 |  | -- | 524444Y | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.5 | 8 | Paron |  | -- | 35.2 | 23.4 | No | 2019-03-14 | D_s2_d2 | 1.6 | 39.9 | 88.3 | 1452 | 80.1 | D | 61.9 | 0.18 | s2 | y | y | d2
TN_2019_1415 |  | OP 70961 | 525991E | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 39.79 | 5 | Vilanova | HEPR+1420FEES+6000SEES | CD | 49.5 | 13.6 | No | 2019-03-14 | D_s1_d2 | 1.75 | 39.4 | 74.1 | 1494 | 63.1 | D | 9.4 | 0.02 | s1 | n | y | d2
TN_2019_1416 |  | OP 70961 | 525995J | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 39.78 | 5 | Vilanova | HEPR+1420FEES+6000SEES | CD | 41.8 | 16.7 | No | 2019-03-14 | C_s1_d2 | 1.26 | 27.7 | 50.2 | 1497 | 47.6 | C | 7.5 | 0.01 | s1 | n | y | d2
19030012 |  | 17731 | -- | CÂBLE 16FO (4X4) KT(XS) FILLED | 11.6 | 13 | Paron | 1602SEES | -- | 40 | 23.7 | No | 2019-03-15 | D_s1_d2 | 3 | 42.9 | 62.3 | 894 | 128 | D | 45 | 0.08 | s1 | y | y | d2
19030013 |  | 17731 | -- | CÂBLE 16FO (4X4) KT(XS) FILLED | 11.85 | 13 | Paron | MEGOLONS548 | -- | 40.2 | 23.9 | No | 2019-03-15 | D_s2_d2 | 3 | 45.3 | 56.8 | 1437 | 94 | D | 70 | 0.13 | s2 | y | y | d2
TN_2019_1417 |  |  | TG-H43328 | AFUMEX CLASS RZ1-K (AS) 1KV 5G2.5 | 13.54 | 11 | Vilanova | PENDINGTOCONFIRM | CD | 44.1 | 16 | No | 2019-03-15 | D_s1_d2 | 2.9 | 43.6 | 71.1 | 1242 | 82.4 | D | 49.1 | 0.1 | s1 | n | y | d2
TN_2019_1418 |  | 17720 | -- | 750-3G6-SH-NF F 55-625-255 | 14.81 | 10 | Vilanova | ID3100FR/SV3300FR+0400FEIT+5300SEIT | CD | 39.7 | 19.5 | No | 2019-03-15 | B2_s1_d1 | 0.83 | 10.7 | 19.6 | 1143 | 27.9 | B2 | 17.4 | 0.05 | s1 | y | n | d1
TN_2019_1419 |  | 17720 | BBT 908292 | 750-3G1.5-SH-NF F 55-625-255 | 10.83 | 14 | Vilanova | ID3100FR/SV3300FR+0400FEIT+5300SEIT | CD | 40.9 | 20.1 | No | 2019-03-15 | C_s1_d2 | 1.46 | 21 | 41.3 | 888 | 70.2 | C | 30.6 | 0.06 | s1 | y | y | d2
19030014 |  | 17731 | -- | ADIF DRAKA 19 96FO MN-TKEST | 18.6 | 8 | Paron | TPR-37 | -- | 42 | 23 | No | 2019-03-15 | B2_s2_d1 | 0.87 | 13.7 | 18.6 | 1209 | 35 | B2 | 72 | 0.11 | s2 | y | n | d1
|  | 69987 | 514504U | DZ1 ADIF DCA 3.6/6KV 1X400 MM2 AL | 33.8 | 5 | Manlleu | IRN267+6000SEES | '-- | 35 | 20 | No | 2019-03-12 | B2_s1_d2 | 0.86 | 10.2 | 13.6 | 858 | 32.5 | B2 | 12.2 | 0.03 | s1 | y | y | d2
|  | 69998 | 521754Z | AL-DZ1 ADIF B2CA 3.6/6KV FILLER+DMZ2 300MM2 | 33.2 | 6 | Manlleu | IRN267+1420FEES+6000SEES | '-- | 35 | 20 | No | 2019-03-12 | D_s1_d2 | 2.16 | 45.3 | 71 | 1500 | 80.5 | D | 16.5 | 0.04 | s1 | y | y | d2
|  | 69996 | 514506W | AL-DZ1 ADIF B2CA 3.6/6KV 1X300MM2 | 30.8 | 6 | Manlleu | IRN267+6000SEES | '-- | 35 | 20 | No | 2019-03-12 | _ _ | 3.3
|  | 69991 | 52836N | DZ1 ADIF B2CA 3.6/6KV FILLER+DMZ2 1X300MM2 | 34.1 | 5 | Manlleu | IRN267+1420FEES+6000SEES | '-- | 34 | 20 | No | 2019-03-12 | D_s1_d2 | 2.17 | 27.2 | 38.1 | 1236 | 56 | D | 30.2 | 0.1 | s1 | y | y | d2
|  | 69989 | 514502S | DZ1 ADIF B2CA 3.6/6KV 1X300MM2 | 31.8 | 6 | Manlleu | IRN267+6000SEES | '-- | 34 | 20 | No | 2019-03-12 | _ _ | 3.3
|  | 996996 | 1Z91A19 | EXZHELLENT RZ1-K (AS) 1KV 1X240 | 26.3 | 6 | Manlleu | PRS-03+TPR-54 | '-- | 33 | 20 | No | 2019-03-14 | B2_s1_d2 | 0.84 | 11 | 25 | 1467 | 21.4 | B2 | 9.3 | 0.02 | s1 | Y | Y | d2
|  | 70226 | TO-F50181 | 3X2.5 NBTA 0.6/1 | 12.5 | 12 | Manlleu | PROTO1:GFR3650.5MM0400 | '-- | 34 | 20 | No | 2019-03-14 | B2_s1_d2 | 0.98 | 10.7 | 24.8 | 873 | 51.3 | B2 | 21.1 | 0.05 | s1 | y | y | d2
|  | 70231 | TO-H11668 | 3X2.5 NBTA 0.6/1 | 13.3 | 12 | Manlleu | PROTO2:GFR3650.5MMGV3000FR | '-- | 35 | 20 | No | 2019-03-14 | C_s1_d0 | 1.28 | 16.1 | 26.1 | 993 | 39.5 | C | 11 | 0.03 | s1 | N | N | d0
|  | 70227 | TO-F54673 | 3X2.5 NBTA 0.6/1 | 11.2 | 14 | Manlleu | PROTO3:GFR365NOFILLERTESTWASSTOPPEDATMINUT8FORSAFETYREASONS | '-- | 35 | 20 | No | 2019-03-14 | _ _ | 3.3
|  | 70225 | TO-G82166 | 3X2.5 NBTA 0.6/1 | 11.2 | 14 | Manlleu | PROTO1:GFR3650.5MMFILLER | '-- | 33 | 20 | No | 2019-03-14 | E ou F_s2_d2 | 3.3 | 79.1 | 194 | 1434 | 171.3 | E ou F | 86.4 | 0.65 | s2 | y | y | d2
|  | 70232 | T8-G66663 | 3X2.5 NBTA 0.6/1 | 11.4 | 14 | Manlleu | PROTO2:GFR3650.8MMFILLER | '-- | 34 | 20 | No | 2019-03-14 | E ou F_s2_d2 | 3.7 | 93.1 | 274 | 1434 | 231.3 | E ou F | 246.4 | 0.75 | s2 | y | y | d2
|  | 70604 | TO-H11664 | 3X6 NVFD | 15.3 | 10 | Manlleu | PROTO1:GFR365 | '-- | 32 | 20 | No | 2019-03-15 | C_s1_d2 | 0.84 | 15.1 | 26.1 | 1434 | 33.2 | C | 12.9 | 0.07 | s1 | Y | Y | d2
|  | 70228 | TO-G80587 | 1X2X1.5MM² NST | 8.7 | 17 | Manlleu | PROTO1:GFR365TESTWASSTOPPEDATMINUT7FORSAFETYREASONS | '-- | 34 | 20 | No | 2019-03-15 | __ | 3.3
|  | 69823 | TO-H11699 | 2X2X0.75MM² NVD/C 0.6/1 KV | 12.8 | 12 | Manlleu | PROTO1:GFR365 | '-- | 32 | 20 | No | 2019-03-15 | D_s2_d2 | 3 | 40.6 | 60.8 | 1092 | 105.8 | D | 129.9 | 0.21 | s2 | y | y | d2
19030015 |  | 17720 | BBT 908292 | 750-3G1.5-SH-NF F 55-625-255 | 10.6 | 14 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 38.4 | 23 | No | 2019-03-16 | C_s2_d2 | 1.52 | 19.3 | 39.9 | 882 | 69 | C | 56 | 0.13 | s2 | y | y | d2
19030016 |  | 17731 | -- | CÂBLE 16FO (4X4) KT(XS) FILLED | 11.95 | 13 | Paron | TPR-37 | -- | 36.5 | 22.3 | No | 2019-03-16 | D_s2_d2 | 3 | 39.4 | 48.4 | 1269 | 74 | D | 63 | 0.11 | s2 | y | y | d2
19030017 |  | 17731 | -- | CÂBLE 96FO (12X8) TKEST FILLED | 22 | 7 | Paron | 1602SEES+1602SEES | -- | 35.5 | 23.2 | No | 2019-03-16 | D_s2_d2 | 1.6 | 40.3 | 65.7 | 1485 | 66 | D | 66 | 0.11 | s2 | y | y | d2
TN_2019_1420 |  |  | TG-H43316 | AFUMEX CLASS RZ1-K (AS) 1KV 5G2.5 | 13.14 | 12 | Vilanova | PENDINGTOCONFIRM | CD | 69.5 | 12.1 | No | 2019-03-17 | D_s1_d2 | 2.38 | 39.3 | 77.6 | 1449 | 77.6 | D | 37.7 | 0.12 | s1 | n | y | d2
TN_2019_1421 |  |  | TE-H86000 | AFUMEX CLASS RZ1-K (AS) 1KV 5G10 | 18.71 | 8 | Vilanova | PENDINGTOCONFIRM | CD | 68 | 12.9 | No | 2019-03-17 | B2_s1_d2 | 0.7 | 9.1 | 22.3 | 1497 | 23.9 | B2 | 3.2 | 0.01 | s1 | n | y | d2
TN_2019_1422 |  | OP 70961 | 525991E | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 39.79 | 5 | Vilanova | HEPR+1420FEES+6000SEES | CD | 62 | 17.9 | No | 2019-03-17 | D_s1_d2 | 1.61 | 34.7 | 68 | 1494 | 57.5 | D | 0.1 | 0 | s1 | n | y | d2
TN_2019_1423 |  | OP 70961 | 525995J | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 39.78 | 5 | Vilanova | HEPR+1420FEES+6000SEES | CD | 59.9 | 18.5 | No | 2019-03-17 | D_s1_d2 | 1.98 | 40.5 | 79.8 | 1491 | 67.8 | D | 7.8 | 0.02 | s1 | n | y | d2
TN_2019_1424 |  |  |  | FG16OR16 5G1.5 MM² - 0.6/1 KV ( LA TRIVENETA) | 10.96 | 14 | Vilanova | COMPETITORSAMPLE | CD | 70.4 | 9.8 | No | 2019-03-20 | C_s3_d2 | 1.52 | 19.1 | 36.8 | 645 | 108.7 | C | 431.1 | 1 | s3 | n | y | d2
TN_2019_1425 |  |  |  | FG16OR16 5G1.5 MM² - 0.6/1 KV ( LA TRIVENETA) | 10.96 | 14 | Vilanova | COMPETITORSAMPLE | CD | 66.6 | 10.5 | No | 2019-03-20 | C_s3_d2 | 1.76 | 23.5 | 42.9 | 906 | 110.9 | C | 562.7 | 1.04 | s3 | n | y | d2
TN_2019_1426 |  |  |  | FG16OR16 4G1.5 MM² - 0.6/1 KV ( LA TRIVENETA) | 10.11 | 15 | Vilanova | COMPETITORSAMPLE | CD | 54.6 | 15.5 | No | 2019-03-20 | C_s3_d1 | 1.93 | 26.2 | 51.4 | 810 | 127.8 | C | 561.8 | 1.09 | s3 | y | n | d1
TN_2019_1427 |  |  |  | FG16OR16 3G1.5 MM² - 0.6/1 KV ( LA TRIVENETA) | 9.51 | 15 | Vilanova | COMPETITORSAMPLE | CD | 48.6 | 16.6 | No | 2019-03-20 | B2_s2_d0 | 1.2 | 9.7 | 26.2 | 633 | 85.9 | B2 | 240 | 0.69 | s2 | n | n | d0
TN_2019_1428 |  |  |  | FG16OR16 3G1.5 MM² - 0.6/1 KV ( LA TRIVENETA) | 9.51 | 15 | Vilanova | COMPETITORSAMPLE | CD | 49.6 | 16.3 | No | 2019-03-20 | C_s2_d0 | 1.22 | 11.5 | 30.8 | 645 | 98.9 | C | 287.5 | 0.9 | s2 | n | n | d0
19030018 |  | 17745 | -- | 750-3G2.5-SH-NF F 55-625-255 | 12.7 | 12 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 29.4 | 22.5 | No | 2019-03-21 | C_s1_d2 | 1.07 | 12.7 | 31.5 | 1005 | 46 | C | 38 | 0.12 | s1 | y | y | d2
TN_2019_1429 |  |  |  | FG16OR16 4G1.5 MM² - 0.6/1 KV ( LA TRIVENETA) | 10.11 | 15 | Vilanova | COMPETITORSAMPLE | CD | 51.7 | 10.2 | No | 2019-03-21 | C_s2_d1 | 1.48 | 18.9 | 41.8 | 672 | 112.8 | C | 383.7 | 0.99 | s2 | y | n | d1
TN_2019_1430 |  |  |  | AFUMEX CLASS 750V HO7Z1-K (AS) TYPE2 1X4 | 4.01 | 90 | Vilanova | 1602SEES | CD | 32.6 | 17.5 | No | 2019-03-21 | B2_s1_d0 | 1.01 | 8.8 | 25.4 | 609 | 90.9 | B2 | 29.6 | 0.09 | s1 | n | n | d0
TN_2019_1431 |  | 20193654 OP 82979511 | 529197P | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.62 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 42.3 | 13.8 | No | 2019-03-25 | D_s1_d0 | 2.25 | 35.8 | 47.7 | 1101 | 73.8 | D | 24.6 | 0.04 | s1 | n | n | d0
TN_2019_1432 |  | 82938216 | Rollo sin ident | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.14 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 40.8 | 15.2 | No | 2019-03-25 | D_s1_d2 | 3.1 | 42.5 | 82.4 | 1497 | 74.9 | D | 35.5 | 0.06 | s1 | n | y | d2
TN_2019_1433 |  | 82403227 | 439635P | AFUMEX CLASS RZ1-K (AS) 1KV 1X16 | 10.71 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 41.3 | 20 | No | 2019-03-25 | D_s1_d2 | 3.3 | 42.3 | 73.6 | 1500 | 94.6 | D | 39.9 | 0.06 | s1 | n | y | d2
TN_2019_1434 |  | 20193744 | ES1792783 | AFUMEX CLASS 750V HO7Z1-K (AS) TYPE2 1X1.5 | 2.93 | 165 | Vilanova | 1602SEES | CD | 42.8 | 21.6 | No | 2019-03-25 | C_s1_d1 | 1.43 | 14.1 | 35 | 630 | 107.7 | C | 44.1 | 0.11 | s1 | y | n | d1
TN_2019_1435 |  | OP82988675 | 523091C | AL-VOLTALENE XZ1(AS)1X150K 0.6/1.0KV | 24.12 | 7 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 33.7 | 15.6 | No | 2019-03-26 | C_s1_d2 | 1.02 | 15.2 | 35 | 1500 | 36.4 | C | 31.1 | 0.08 | s1 | n | y | d2
TN_2019_1436 |  | OP82988675 | 523091C | AL-VOLTALENE XZ1(AS)1X150K 0.6/1.0KV | 24.12 | 7 | Vilanova | SXLPE+1420FEES+6000SEES | CD | 20.6 | 19.8 | No | 2019-03-26 | C_s1_d2 | 1.1 | 16.3 | 42.3 | 1500 | 43.5 | C | 29.5 | 0.07 | s1 | n | y | d2
19030019 |  | 17754 | -- | RTE- 1X1200MM2 AL PR-11-AL-52/90(100) KV | 83.6 | 3 | Paron | XLPE+ALFOIL+60ACESNOIR+SKINSC | -- | 27 | 2.7 | No | 2019-03-26 | B2_s1_d0 | 0.95 | 13.3 | 18.4 | 882 | 39 | B2 | 11 | 0.02 | s1 | n | n | d0
19030020 |  | 17745 | -- | 750-3G2.5-SH-NF F 55-625-255 | 12.7 | 12 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 31 | 21.4 | No | 2019-03-27 | B2_s1_d2 | 0.9 | 12 | 27 | 972 | 48 | B2 | 31 | 0.09 | s1 | y | y | d2
19030021 |  | 17720 | XCP 06201763 | 750-3G1.5-SH-NF F 55-625-255 | 10.6 | 14 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 27.8 | 22.2 | No | 2019-03-28 | B2_s1_d2 | 1.1 | 12 | 26.2 | 891 | 66 | B2 | 36 | 0.09 | s1 | y | y | d2
19030022 |  | 17720 | XCP 06201744 | 750-3G1.5-SH-NF F 55-625-255 | 10.9 | 14 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 28.2 | 22.1 | No | 2019-03-28 | B2_s1_d2 | 1.2 | 12.5 | 29.8 | 909 | 49 | B2 | 47 | 0.1 | s1 | y | y | d2
19030023 |  | 17720 | XCP 06199986 | 750-3G1.5-SH-NF F 55-625-255 | 10.9 | 14 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 27.6 | 22.5 | No | 2019-03-28 | C_s3_d2 | 1.4 | 16.8 | 34.7 | 909 | 58 | C | 45 | 55 | s3 | y | y | d2
TN_2019_1437 |  | OP82988675 | 523091C | AL-VOLTALENE XZ1(AS)1X150K 0.6/1.0KV | 24.12 | 7 | Vilanova | SXLPE+1420FEES+6000SEES | CD | 47.3 | 16.4 | No | 2019-03-29 | C_s1_d2 | 1 | 15.1 | 40.8 | 1500 | 41.1 | C | 11.8 | 0.03 | s1 | n | y | d2
TN_2019_1438 |  | OP70755 20289847 | 523093E | AL-VOLTALENE XZ1(AS)1X50K 0.6/1.0KV | 16.86 | 9 | Vilanova | SXLPE+1420FEES+6000SEES | CD | 70.5 | 14.4 | No | 2019-03-02 | C_s1_d2 | 1.7 | 29.4 | 56.3 | 1491 | 65.3 | C | 31.4 | 0.09 | s1 | n | y | d2
TN_2019_1439 |  | OP70755 20289847 | 523093E | AL-VOLTALENE XZ1(AS)1X50K 0.6/1.0KV | 16.86 | 9 | Vilanova | SXLPE+1420FEES+6000SEES | CD | 67 | 15.2 | No | 2019-03-02 | D_s1_d2 | 1.98 | 32.6 | 62 | 1500 | 64.6 | D | 33.2 | 0.1 | s1 | n | y | d2
TN_2019_1440 |  | OP69810 20284398 | 520900W | AL-AFUMEX DZ1F3Z1 CL2 ADIF B2CA 3KV 3X16MM² | 29.51 | 6 | Vilanova | CUBIERTAINTERNA1602+ACEROSNCORRUGADO+CUBIERTA1602 | CD | 63.5 | 16.8 | No | 2019-03-02 | B2_s1_d2 | 0.67 | 8.7 | 12.2 | 1497 | 20.5 | B2 | 18.8 | 0.03 | s1 | n | y | d2
TN_2019_1441 |  | OP71402 20296008 | 533602C | EXZHELLENT RZ1-K (AS) 1KV 1X35 | 13.89 | 11 | Vilanova | XLPE+TPR54R00 | CD | 60.3 | 18.2 | No | 2019-03-02 | C_s1_d2 | 1.61 | 20.7 | 31.9 | 1230 | 35 | C | 22.7 | 0.04 | s1 | n | y | d2
TN_2019_1442 |  | OP69810 20284398 | 530376W | AL-AFUMEX DZ1F3Z1 CL2 ADIF B2CA 3KV 3X16MM² | 28.41 | 6 | Vilanova | CUBIERTAINTERNA1602+ACEROSNCORRUGADO+CUBIERTATPR55 | CD | 58.5 | 19.3 | No | 2019-03-02 | B2_s1_d2 | 0.72 | 8.1 | 14.1 | 1491 | 22.5 | B2 | 21.1 | 0.05 | s1 | n | y | d2
TN_2019_1443 |  | OP69811 20284399 | 530722X | AL-AFUMEX DZ1F3Z1 CL2 ADIF B2CA 3KV 3X25MM² | 31.37 | 6 | Vilanova | CUBIERTAINTERNA1602+ACEROSNCORRUGADO+CUBIERTATPR55 | CD | 59.3 | 19.7 | No | 2019-03-02 | B2_s1_d2 | 0.59 | 7.1 | 9.8 | 1170 | 24 | B2 | 0.1 | 0.01 | s1 | n | y | d2
19040001 |  | 17720 | -- | 750-7G2.5-SH-NF F 55-625-255 | 16.5 | 9 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 34.3 | 24.6 | No | 2019-04-02 | B2_s1_d2 | 0.82 | 11.9 | 23.7 | 1119 | 29 | B2 | 18 | 0.05 | s1 | y | y | d2
19040002 |  | 17755 | roll | HO7Z1-K (AS) 750V 1X1.5 EXZHELLENT | 2.9 | 165 | Paron | 1602SEES | -- | 33 | 24.7 | No | 2019-04-02 | D_s2_d0 | 2.1 | 16.7 | 31.6 | 744 | 90 | D | 63 | 0.14 | s2 | n | n | d0
19040003 |  | 17755 | roll | HO7Z1-K (AS) 750V 1X1.5 EXZHELLENT | 2.9 | 165 | Paron | 1602SEES | -- | 32.1 | 25 | No | 2019-04-02 | D_s2_d1 | 2.05 | 16.8 | 36.2 | 654 | 128 | D | 53 | 0.13 | s2 | y | n | d1
|  | 70861 | 514226T | RZ1MAZ1-K 1KV 1X240 | 34.6 | 5 | Manlleu | 6010+GFR380 | '-- | 28 | 20 | No | 2019-04-28 | B2_s1_d2 | 0.74 | 2.2 | 3.7 | 588 | 12.9 | B2 | 8.9 | 0.01 | s1 | y | y | d2
|  | 70861 | 514226T | RZ1MAZ1-K 1KV 1X240 | 34.6 | 5 | Manlleu | 6010+GFR380 | '-- | 28 | 20 | No | 2019-04-28 | B2_s1_d1 | 0.65 | 2.9 | 5.2 | 552 | 23.3 | B2 | 0 | 0.01 | s1 | y | n | d1
|  |  | 208013N | RZ1MAZ1-K 1KV 1X240 | 34.5 | 5 | Manlleu | GFR380+GFR380 | '-- | 27 | 20 | No | 2019-04-28 | B2_s1_d0 | 0.57 | 1.9 | 3.4 | 501 | 13 | B2 | 2 | 0.01 | s1 | n | n | d0
|  | 70912 | 53064H | RHOZ1MZ1 500V 2X2X1.5 2RH | 16.9 | 9 | Manlleu | 6010SEES+GFR380 | '-- | 33 | 20 | No | 2019-04-01 | B2_s1_d2 | 0.98 | 13 | 22.5 | 1125 | 27.5 | B2 | 14.6 | 0.05 | s1 | y | y | d2
|  | 70913 | 524404E | RHOZ1MZ1 500V 6X3X1.5 2RH | 26.15 | 6 | Manlleu | 6010SEES+GFR380 | '-- | 34 | 20 | No | 2019-04-01 | B2_s1_d2 | 0.93 | 8.9 | 20 | 1497 | 20.3 | B2 | 8.8 | 0.03 | s1 | y | y | d2
19040005 |  | 17771 | -- | TENLNET R.I 40 2018 90FO OSGZ1 OF 1800788 | 15.6 | 9 | Paron | COMPETITORSAMPLE | -- | 29.6 | 21.8 | No | 2019-04-04 | D_s2_d1 | 2.5 | 46.5 | 64.9 | 1440 | 85 | D | 76 | 0.15 | s2 | y | n | d1
19040004 |  | 17754 | -- | RTE- 1X1200MM2 AL PR-11-AL-52/90(100) KV | 83.3 | 3 | Paron | XLPE+ALFOIL+60ACESNOIR+SKINSC | -- | 29 | 22.8 | No | 2019-04-04 | B2_s1_d0 | 0.8 | 8.1 | 11.2 | 756 | 27 | B2 | 5 | 0.01 | s1 | n | n | d0
|  | 70799 | 525906M | RZ1MZ1 1KV 24X1.5 2RH | 26.2 | 6 | Manlleu | 6010SEES+GFR380 | '-- | 35 | 20 | No | 2019-04-01 | B2_s1_d2 | 0.64 | 3.2 | 6.6 | 1482 | 11.7 | B2 | 1.5 | 0.01 | s1 | y | y | d2
|  | 70910 | 249732Y | ROZ1MZ1 500V 24X2X0.5 2RH | 28.8 | 6 | Manlleu | 6010SEES+GFR380 | '-- | 36 | 20 | No | 2019-04-02 | B2_s1_d2 | 0.79 | 7 | 11.6 | 1452 | 21.3 | B2 | 2.9 | 0.01 | s1 | y | y | d2
|  | 70909 | 525909R | ROZ1MZ1 500V 12X2X1.5 2RH | 28.2 | 6 | Manlleu | 6010SEES+GFR380 | '-- | 35 | 20 | No | 2019-04-02 | B2_s1_d2 | 0.68 | 6.1 | 8.8 | 1197 | 30.6 | B2 | 2.9 | 0.01 | s1 | y | y | d2
|  | 70772 | 530641J | ROZ1MZ1 500V 24X2X0.5 2RH | 28.8 | 6 | Manlleu | GFR380+GFR380 | '-- | 40 | 20 | No | 2019-04-03 | B2_s1_d1 | 0.58 | 5.4 | 6.7 | 1443 | 29.1 | B2 | 1.2 | 0.01 | s1 | y | n | d1
|  | 70911 | 520327Y | KX-ROZ1MZ1 500V 1X2X1.3 2RH | 11.4 | 14 | Manlleu | 6010SEES+GFR380 | '-- | 45 | 20 | No | 2019-04-03 | B2_s1_d2 | 1.03 | 11.8 | 19.8 | 975 | 40 | B2 | 10.2 | 0.02 | s1 | y | y | d2
|  | 70798 | 522913J | RZ1MZ1 1KV 2X2.5 2RH | 13.9 | 11 | Manlleu | 6010SEES+GFR380 | '-- | 45 | 20 | No | 2019-04-03 | B2_s1_d2 | 0.91 | 12.1 | 20.4 | 1002 | 32.6 | B2 | 9.6 | 0.02 | s1 | y | y | d2
|  | 70770 | 530586Z | ROZ1MZ1 500V 1X2X1.5 2RH | 11.6 | 13 | Manlleu | GFR380+GFR380 | '-- | 40 | 20 | No | 2019-04-03 | B2_s1_d1 | 0.44 | 4.9 | 10.4 | 981 | 21.9 | B2 | 3.5 | 0.01 | s1 | y | n | d1
|  | 70771 | 498703U | ROZ1MZ1 500V 12X2X1.5 2RH | 28 | 6 | Manlleu | GFR380+GFR380 | '-- | 40 | 20 | No | 2019-04-03 | B2_s1_d1 | 0.49 | 5.7 | 8 | 981 | 25.9 | B2 | 0 | 0 | s1 | y | n | d1
|  | 409667 |  | RED ELEC RHZ1-RA-2OL (AS) 1X2000MM2 127/220KV +T375AL | 123.5 | 2 | Manlleu | XLPE+TUBEAL+60ACESNATUREL+SKINSC | '-- | 40 | 20 | No | 2019-04-04 | B2_s1_d1 | 0.96 | 5.5 | 7 | 1026 | 15.5 | B2 | 0.3 | 0 | s1 | y | n | d1
TN_2019_1444 |  | OP69810 20284398 | 530723Y | AL-AFUMEX DZ1F3Z1 CL2 ADIF B2CA 3KV 3X16MM² | 28.89 | 6 | Vilanova | CUBIERTAINTERNA1602+ACEROSNCORRUGADO+LANTOR+CUBIERTATPR55 | CD | 78.2 | 16.3 | No | 2019-04-03 | B2_s1_d2 | 0.72 | 8.6 | 18.3 | 1500 | 24.8 | B2 | 3.2 | 0.02 | s1 | n | y | d2
TN_2019_1445 |  | OP69811 20284399 | 530715P | AL-AFUMEX DZ1F3Z1 CL2 ADIF B2CA 3KV 3X25MM² | 32.18 | 6 | Vilanova | CUBIERTAINTERNA1602+ACEROSNCORRUGADO+LANTOR+CUBIERTATPR55 | CD | 69.1 | 17.7 | No | 2019-04-03 | B2_s1_d2 | 0.39 | 8.3 | 10.1 | 1176 | 29 | B2 | 6 | 0.01 | s1 | n | y | d2
TN_2019_1446 |  | OP71129 | 524434M | AFUMEX CLASS RZ1-K (AS) 1KV 3X16 | 18.65 | 8 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 67.1 | 18.2 | No | 2019-04-03 | C_s1_d1 | 0.9 | 15.6 | 35.1 | 1500 | 29.3 | C | 14.1 | 0.04 | s1 | y | n | d1
TN_2019_1447 |  |  | TL-E80500 | RG16H1M16 1X240 MM² - 12/20 KV | 40.35 | 5 | Vilanova | PENDINGTOCONFIRM | OD | 44.9 | 12.1 | No | 2019-04-04 | B2_s1_d0 | 0.51 | 4.8 | 7.5 | 702 | 19.5 | B2 | 10.8 | 0.02 | s1 | n | n | d0
TN_2019_1448 |  |  | TL-C03992 | RG16H1M16 1X50 MM² - 12/20 KV | 29.78 | 6 | Vilanova | PENDINGTOCONFIRM | OD | 39.9 | 14.1 | No | 2019-04-04 | B2_s1_d1 | 0.42 | 4.3 | 6.3 | 669 | 19.1 | B2 | 21.7 | 0.03 | s1 | y | n | d1
TN_2019_1449 |  |  | S/N 2 | RG16H1M16 1X95 MM² - 18/30 KV | 37.73 | 5 | Vilanova | PENDINGTOCONFIRM | OD | 38.2 | 14.7 | No | 2019-04-04 | B2_s1_d0 | 0.57 | 4.3 | 6.1 | 834 | 18.1 | B2 | 1.4 | 0 | s1 | n | n | d0
TN_2019_1451 |  |  |  | 750-7G2.5-SH-NF F 55-625-255 | 16.74 | 9 | Vilanova | ID3100FR/SV3300FR+0400FEIT+5300SEIT | CD | 68.9 | 11.5 | No | 2019-04-08 | B2_s1_d2 | 0.73 | 9.9 | 16.2 | 1104 | 24.3 | B2 | 9.9 | 0.03 | s1 | n | y | d2
TN_2019_1452 |  |  |  | 750-3G1.5-SH-NF F 55-625-255 | 10.69 | 14 | Vilanova | ID3100FR/SV3300FR+0400FEIT+5300SEIT | CD | 67 | 12.1 | No | 2019-04-08 | C_s1_d2 | 1.08 | 14.9 | 33 | 897 | 59.1 | C | 34.6 | 0.09 | s1 | n | y | d2
TN_2019_1453 |  | 82978611 | 524521G | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 11.6 | 13 | Vilanova | SXLPE+1420FEES+16FA_ES | CD | 62.5 | 14.2 | No | 2019-04-08 | C_s1_d1 | 1.78 | 27 | 37.6 | 1125 | 53.6 | C | 35.2 | 0.09 | s1 | y | n | d1
TN_2019_1454 |  | OP70755 20289847 | 523093E | AL-VOLTALENE XZ1(AS)1X50K 0.6/1.0KV | 16.86 | 9 | Vilanova | SXLPE+1420FEES+6000SEES | CD | 58.7 | 16.2 | No | 2019-04-08 | C_s1_d2 | 1.57 | 20.1 | 41.6 | 1446 | 43.2 | C | 17.1 | 0.03 | s1 | n | y | d2
TN_2019_1455 |  | OP71129 | 524434M | AFUMEX CLASS RZ1-K (AS) 1KV 3G16 | 18.65 | 8 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 49.8 | 19 | No | 2019-04-08 | C_s1_d2 | 1.22 | 17.3 | 44.1 | 1482 | 37.4 | C | 20.5 | 0.03 | s1 | n | y | d2
|  | 274941 | 06N1376 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 9.8 | 15 | Manlleu | PRS-03+TPR-45+TPR-49+TPR-54 | '-- | 38 | 20 | No | 2019-04-08 | D_s1_d1 | 3 | 45 | 59.9 | 930 | 95.6 | D | 34 | 0.07 | s1 | y | n | d1
|  | 274955 | 06N1303 | EXZHELLENT RZ1-K (AS) 1KV 5G2.5 | 13.3 | 12 | Manlleu | PRS-03+TPR-28+TPR-49+TPR-54 | '-- | 38 | 20 | No | 2019-04-08 | C_s1_d1 | 1.73 | 24.4 | 43.9 | 1500 | 41.4 | C | 11.8 | 0.03 | s1 | y | n | d1
|  | 274787 | 06N1161 | EXZHELLENT RZ1-K (AS) 1KV 1X10 | 9.5 | 15 | Manlleu | PRS-03+TPR-35 | '-- | 40 | 20 | No | 2019-04-08 | B2_s1_d2 | 1.42 | 14.6 | 20.7 | 1098 | 37 | B2 | 24.3 | 0.04 | s1 | y | y | d2
|  | 704576 |  | HO7Z1-K (AS) 750V 1X1.5 EXZHELLENT | 2.8 | 180 | Manlleu | TPR-52+SKINTPR-53 | '-- | 40 | 20 | No | 2019-04-08 | C_s2_d1 | 1.83 | 18.5 | 28.4 | 906 | 63.9 | C | 51.5 | 0.08 | s2 | y | n | d1
|  | 70773 | 530589C | KX-ROZ1MZ1 500V 1X2X1.3 2RH | 11.4 | 14 | Manlleu | GFR380+GFR380 | '-- | 38 | 20 | No | 2019-04-08 | B2_s1_d2 | 0.63 | 5 | 10.9 | 822 | 22.1 | B2 | 3.9 | 0.01 | s1 | y | y | d2
19040006 |  | 17720 | -- | 750-7G2.5-SH-NF F 55-625-255 | 16.5 | 9 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 32.1 | 24.4 | No | 2019-04-10 | B2_s1_d2 | 0.75 | 12.5 | 22.2 | 1140 | 28 | B2 | 19 | 0.06 | s1 | y | y | d2
19040007 |  | 17782 | -- | 750-3G1.5-SH-NF F 55-625-255 | 10.7 | 14 | Paron | IX1100FR+400FEIT+5300SEIT | -- | 39.6 | 21.8 | No | 2019-04-10 | C_s1_d0 | 1.1 | 17.8 | 36.4 | 906 | 64 | C | 22 | 0.04 | s1 | n | n | d0
19040008 |  | 17782 | -- | 750-3G1.5-SH-NF F 55-625-255 | 10.7 | 14 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 22.1 | 39.4 | No | 2019-04-10 | B2_s1_d0 | 0.75 | 13 | 22.6 | 918 | 53 | B2 | 16 | 0.02 | s1 | n | n | d0
19040009 |  | 17780 | -- | 750-3G10-SH-NF F 55-625-255 | 17.6 | 8 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 22.2 | 39.3 | No | 2019-04-10 | B2_s1_d2 | 0.72 | 6.8 | 10.7 | 1491 | 26 | B2 | 5 | 0.01 | s1 | y | y | d2
|  | 70774 | 530588B | RHOZ1MZ1 500V 2X2X1.5 2RH | 17 | 9 | Manlleu | GFR380+GFR380 | '-- | 19 | 40 | No | 2019-04-10 | B2_s1_d2 | 0.72 | 9.3 | 19.3 | 1185 | 22 | B2 | 13.5 | 0.04 | s1 | Y | Y | d2
|  | 70776 | 530591E | ATEX RZ1MZ1 1KV 2X2.5 2RH | 18 | 40 | Manlleu | GFR380+GFR380 | '-- | 18 | 40 | No | 2019-04-10 | B2_s1_d1 | 0.46 | 5.2 | 7.8 | 861 | 24.2 | B2 | 7.1 | 0.01 | s1 | Y | N | d1
|  | 70777 | 525956S | ATEX RZ1MZ1 1KV 24X1.5 2RH | 19 | 40 | Manlleu | GFR380+GFR380 | '-- | 19 | 40 | No | 2019-04-10 | B2_s1_d1 | 0.66 | 3.7 | 5.1 | 1323 | 10.8 | B2 | 0.3 | 0 | s1 | Y | N | d1
|  | 704839 | 699527 | EXZHELLENT RZ1-K (AS) 1KV 1X35 | 18 | 45 | Manlleu | PRS-03+TPR-54 | '-- | 18 | 45 | No | 2019-04-11 | C_s1_d2 | 1.82 | 26.8 | 42.4 | 1170 | 54.9 | C | 16.1 | 0.04 | s1 | Y | Y | d2
TN_2019_1456 |  |  |  | K25 5G1.50-SH-NF F 55-625-255 | 12.91 | 12 | Vilanova | ID3100FR/SV3300FR+0400FEIT+5300SEIT | CD | 71.9 | 14.2 | No | 2019-04-09 | B2_s1_d2 | 0.81 | 11.7 | 21.1 | 888 | 37.1 | B2 | 24.5 | 0.05 | s1 | n | y | d2
TN_2019_1457 |  | OP70346 20284005 | 526026T | AFUMEX CLASS O 1Z1C7Z1-K 1KV 37X1 | 29.44 | 6 | Vilanova | LANTOR+TPR55 | CD | 65.8 | 14.9 | No | 2019-04-09 | B2_s1_d2 | 0.67 | 8.5 | 21.5 | 1497 | 18 | B2 | 3.4 | 0.01 | s1 | n | y | d2
TN_2019_1458 |  | OP70347 20284006 | 526029W | AFUMEX CLASS O 1Z1C7Z1-K 1KV 37X2.5 | 34.13 | 5 | Vilanova | LANTOR+TPR55 | CD | 57.7 | 16.3 | No | 2019-04-09 | B2_s1_d2 | 0.44 | 3.7 | 10.2 | 1500 | 13.2 | B2 | 3.7 | 0.01 | s1 | n | y | d2
TN_2019_1459 |  | OP70344 20284012 | 530721W | AFUMEX CLASS O 1Z1C7Z1-K 1KV 14X1 | 20.53 | 7 | Vilanova | LANTOR+TPR55 | CD | 54.9 | 17.1 | No | 2019-04-09 | B2_s1_d2 | 0.47 | 10.1 | 15.8 | 1125 | 19.1 | B2 | 5.5 | 0.01 | s1 | n | y | d2
TN_2019_1460 |  |  | TW/H22023 | FG16OR16 3X35 MM² - 0.6/1 KV | 23.19 | 7 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 59.9 | 12.3 | No | 2019-04-11 | C_s2_d2 | 1.09 | 16.3 | 33.6 | 1299 | 34.9 | C | 273.3 | 0.44 | s2 | n | y | d2
TN_2019_1461 |  |  | 07/F85453 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.63 | 14 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 45.7 | 16.1 | No | 2019-04-11 | C_s2_d0 | 1.1 | 11.1 | 30.5 | 735 | 84.7 | C | 200.1 | 0.54 | s2 | n | n | d0
TN_2019_1462 |  |  | 07/C82284 | FG16OR16 1X10 MM² - 0.6/1 KV | 8.79 | 17 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 28.7 | 20 | No | 2019-04-11 | B2_s2_d1 | 0.7 | 4.9 | 13.3 | 570 | 50.1 | B2 | 82.4 | 0.29 | s2 | y | n | d1
TN_2019_1463 |  |  | TW/H22023 | FG16OR16 3X35 MM² - 0.6/1 KV | 23.19 | 7 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 27.1 | 21.4 | No | 2019-04-11 | C_s2_d2 | 1.03 | 18.9 | 29.1 | 1212 | 42.6 | C | 261.6 | 0.38 | s2 | n | y | d2
19040011 |  | 17780 | -- | 750-19X1.5-SH-NF F 55-625-255 | 21.5 | 7 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 26.6 | 21.4 | No | 2019-04-11 | B2_s1_d0 | 0.4 | 4.2 | 7.1 | 1500 | 17.6 | B2 | 4.2 | 0.01 | s1 | n | n | d0
19040010 |  | 17780 | -- | FR-N1 X1G1-U- 3G1.5 MM² | 10.06 | 15 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 29.2 | 20.6 | No | 2019-04-11 | B2_s1_d1 | 1 | 14.1 | 22.4 | 1071 | 41.9 | B2 | 35 | 0.09 | s1 | y | n | d1
|  | 70703 | 530717S | EXZHELLENT RZ1-K (AS) 1KV 1X240 | 26.7 | 6 | Manlleu | PRS-03+TPR-54 | '-- | 44 | 18 | No | 2019-04-11 | B2_s1_d2 | 0.81 | 8 | 16.5 | 1479 | 17.7 | B2 | 1.1 | 0 | s1 | Y | Y | d2
|  |  | 533590P | EXZHELLENT RZ1-K (AS) 1KV 1X50 | 15.2 | 10 | Manlleu | PRS-03+TPR-54 | '-- | 40 | 20 | No | 2019-04-11 | C_s1_d2 | 1.41 | 20.8 | 36.6 | 1398 | 34.4 | C | 6 | 0.02 | s1 | Y | Y | d2
|  | 70775 | 524433L | RHOZ1MZ1 500V 6X3X1.5 2RH | 26 | 6 | Manlleu | GFR380+GFR380 | '-- | 38 | 20 | No | 2019-04-11 | B2_s1_d1 | 0.54 | 4.9 | 8.4 | 1500 | 15.1 | B2 | 0.4 | 0 | s1 | Y | N | d1
|  | 70908 | 498690E | ROZ1MZ1 500V 1X2X1.5 2RH | 11.7 | 13 | Manlleu | 6010SEES+GFR380 | '-- | 42 | 20 | No | 2019-04-12 | B2_s1_d1 | 0.81 | 8.4 | 15.4 | 855 | 29.2 | B2 | 1.3 | 0.01 | s1 | Y | N | d1
TN_2019_1464 |  |  | TW/H49991 | FG16OR16 3X35 MM² - 0.6/1 KV | 23.72 | 7 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 52.2 | 13.7 | No | 2019-04-12 | C_s2_d2 | 1.16 | 19.4 | 36.7 | 1296 | 38.9 | C | 374 | 0.56 | s2 | n | y | d2
TN_2019_1465 |  |  | 12/H24899 | FG16OR16 3X35 MM² - 0.6/1 KV | 23.13 | 7 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 51.1 | 13.6 | No | 2019-04-12 | C_s2_d2 | 1.18 | 20.2 | 42 | 1227 | 45.7 | C | 342.1 | 0.6 | s2 | n | y | d2
TN_2019_1466 |  |  | 07/F88664 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.62 | 14 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 47.8 | 15.7 | No | 2019-04-12 | B2_s2_d0 | 1.05 | 13.4 | 27.7 | 774 | 74.5 | B2 | 242.6 | 0.62 | s2 | n | n | d0
TN_2019_1467 |  |  | TW/H49991 | FG16OR16 3X35 MM² - 0.6/1 KV | 23.72 | 7 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 42.1 | 18.3 | No | 2019-04-12 | C_s2_d2 | 1.24 | 19.1 | 42.5 | 1257 | 46.4 | C | 349.1 | 0.65 | s2 | n | y | d2
TN_2019_1468 |  |  | 07/D37621 | FG16OR16 4G1.5 MM² - 0.6/1 KV | 10.71 | 14 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 37.1 | 20.7 | No | 2019-04-12 | B2_s2_d0 | 1.18 | 12.9 | 29.9 | 690 | 86.6 | B2 | 252.9 | 0.74 | s2 | n | n | d0
TN_2019_1469 |  | OP70755 20289847 | 523093E | AL-VOLTALENE XZ1(AS)1X50K 0.6/1.0KV | 16.86 | 9 | Vilanova | XLPE+1420+6000 | CD | 59.7 | 15.5 | No | 2019-04-15 | C_s1_d2 | 0.75 | 15.3 | 21 | 1059 | 37.6 | C | 33.4 | 0.06 | s1 | n | y | d2
TN_2019_1470 |  | OP70733 20215693 | 523236K | AL-VOLTALENE XZ1(AS)1X240K 0.6/1.0KV | 27.89 | 6 | Vilanova | XLPE+1420+6000 | CD | 47.6 | 17.2 | No | 2019-04-15 | C_s1_d2 | 1.18 | 16 | 27.1 | 1497 | 41.8 | C | 24.9 | 0.05 | s1 | n | y | d2
TN_2019_1471 |  |  | 07/F86021 | FG16OR16 1X10 MM² - 0.6/1 KV | 8.79 | 17 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 47.2 | 18.4 | No | 2019-04-15 | B2_s2_d0 | 0.66 | 5.7 | 15.6 | 606 | 52.8 | B2 | 106 | 0.4 | s2 | n | n | d0
TN_2019_1472 |  | OP71128 | 524434M | AFUMEX CLASS RZ1-K (AS) 1KV 3X16 | 18.65 | 8 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 51.8 | 13.4 | No | 2019-04-16 | C_s1_d1 | 1.05 | 13.9 | 32.9 | 1500 | 27.4 | C | 14.9 | 0.03 | s1 | y | n | d1
TN_2019_1473 |  |  | 07/C83188 | FG16OR16 1X10 MM² - 0.6/1 KV | 8.66 | 17 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 55.5 | 13.9 | No | 2019-04-16 | B2_s2_d0 | 0.62 | 5 | 13 | 618 | 46.2 | B2 | 86.1 | 0.3 | s2 | n | n | d0
19040012 |  | 17782 | EBM156666 | 750-3G1.5-SH-NF F 55-625-255 | 10.7 | 14 | Paron | IX1100FR+400FEIT+5300SEIT | -- | 43.8 | 21.3 | No | 2019-04-17 | B2_s1_d0 | 0.7 | 7.6 | 15.9 | 786 | 45 | B2 | 11 | 0.03 | s1 | n | n | d0
19040014 |  | 17782 | EBM198736 | 750-3G1.5-SH-NF F 55-625-255 | 10.7 | 14 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 44 | 22.2 | No | 2019-04-17 | B2_s1_d0 | 0.45 | 7.1 | 13.3 | 858 | 37 | B2 | 8 | 0.01 | s1 | n | n | d0
19040013 |  |  | CE6639 | K25 5G1.50-SH-NF F 55-625-255 | 12.8 | 12 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 42.4 | 22.5 | No | 2019-04-17 | C_s2_d2 | 1.55 | 25.1 | 57.9 | 1101 | 103 | C | 56 | 0.15 | s2 | y | y | d2
|  | 705039 | 08S9687 | EXZHELLENT RZ1-K (AS) 1KV 1X240 | 25.8 | 6 | Manlleu | PRS-03+TPR-54 | '-- | 35 | 19 | No | 2019-04-12 | C_s1_d2 | 0.87 | 10.5 | 31.5 | 1500 | 23.2 | C | 3.3 | 0.02 | s1 | y | y | d2
|  | 275166 | 699837 | EXZHELLENT RZ1-K (AS) 1KV 5G4 | 13.8 | 11 | Manlleu | PRS-03+TPR-45+TPR-28+TPR-49+TPR-54 | '-- | 35 | 19 | No | 2019-04-12 | D_s1_d2 | 2.32 | 38 | 74.9 | 1371 | 70.4 | D | 34 | 0.09 | s1 | Y | Y | d2
|  | 996934 | 14J4417 | HEPRZ1 (AS) 1X50MM2 12/20KV | 29.4 | 6 | Manlleu | SMC-01+GOM-14+SMC-05+TPR-49+TPO-03 | '-- | 35 | 20 | No | 2019-04-12 | C_s2_d2 | 1.86 | 28.1 | 44.4 | 1497 | 65.2 | C | 77.9 | 0.29 | s2 | Y | Y | d2
|  | 890718 | 07Y2624 | EXZHELLENT RZ1-K (AS) 1KV 2X2.5 | 9.4 | 17 | Manlleu | XLPE+GFR380+GFR380 | '-- | 37 | 20 | No | 2019-04-17 | D_s1_d1 | 2.42 | 30.2 | 49.3 | 888 | 84.7 | D | 25.3 | 0.04 | s1 | y | n | d1
TN_2019_1474 |  |  | 537369X | AFUMEX CLASS RZ1-K (AS) 1KV 5G2.5 | 13.55 | 11 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 65.9 | 16.9 | No | 2019-04-23 | D_s1_d2 | 2.13 | 29.7 | 45 | 1347 | 53.4 | D | 23.1 | 0.06 | s1 | n | y | d2
TN_2019_1475 |  |  |  | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 11.75 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 63.9 | 17.6 | No | 2019-04-23 | D_s1_d2 | 3.3 | 45.5 | 105.4 | 1494 | 88.3 | D | 25 | 0.04 | s1 | n | y | d2
TN_2019_1476 |  |  | 533664V | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 27.6 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 60.3 | 18.9 | No | 2019-04-23 | B2_s1_d0 | 0.52 | 5.4 | 8.6 | 1482 | 16.3 | B2 | 0.8 | 0 | s1 | n | n | d0
TN_2019_1477 |  |  | C326 | RED ELEC RHZ1-RA-2OL(AS) 1X1600MM2 76/132KV | 104.31 | 2 | Vilanova | XLPE+ALFOIL+60AC+SKINDELE0563+20%1602 | CD | 41.6 | 19.1 | No | 2019-04-24 | B2_s1_d2 | 0.86 | 11.5 | 17.7 | 1497 | 34 | B2 | 7.7 | 0.01 | s1 | n | y | d2
|  | 70773 | 530589C | KX-ROZ1MZ1 500V 1X2X1.3 2RH | 11.4 | 14 | Manlleu | XLPE+GFR380+GFR380 | '-- | 37 | 20 | No | 2019-04-17 | B2_s1_d2 | 0.48 | 2.8 | 6.9 | 801 | 14.7 | B2 | 2.2 | 0.01 | s1 | y | y | d2
|  | 70774 | 530588B | RHOZ1MZ1 500V 2X2X1.5 2RH | 17.1 | 9 | Manlleu | XLPE+GFR380+GFR380 | '-- | 40 | 19 | No | 2019-04-17 | B2_s1_d1 | 0.66 | 4.5 | 6.8 | 1185 | 9.7 | B2 | 0.8 | 0.01 | s1 | Y | N | d1
|  | 274766 | 06N1277 | EXZHELLENT RZ1-K (AS) 1KV 3G2.5 | 11.4 | 14 | Manlleu | PRS-03+VPE-08+TPR-49+TPR-54 | '-- | 29 | 20 | No | 2019-04-24 | D_s1_d1 | 2.34 | 31.5 | 47.9 | 1152 | 59.8 | D | 25.4 | 0.07 | s1 | y | n | d1
|  | 71394 | 539182T | MRZF3Z1-K 1KV 5G1.5 | 16.2 | 9 | Manlleu |  | '-- | 40 | 19 | No | 2019-04-24 | B2_s1_d2 | 0.66 | 6.6 | 11.3 | 1116 | 20 | B2 | 19.1 | 0.05 | s1 | Y | Y | d2
|  | 71395 | 539183U | RZ1F3Z1-K (AS) 1KV 5G1.5 | 16.2 | 9 | Manlleu |  | '-- | 40 | 20 | No | 2019-04-24 | B2_s1_d1 | 0.52 | 9.2 | 15.1 | 858 | 27.1 | B2 | 33.4 | 0.07 | s1 | Y | N | d1
|  | 69997 | 52447B | AL-DZ1 ADIF DCA 3.6/6KV 95 MM2 | 23.4 | 7 | Manlleu |  | '-- | 39 | 19 | No | 2019-04-24 | E ou F_s2_d2 | 3.3 | 110.3 | 172.8 | 1185 | 200.9 | E ou F | 110.5 | 0.24 | s2 | y | y | d2
TN_2019_1478 |  | OP 71244/010 | 536360A | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 38.63 | 5 | Vilanova | HEPR+14202.11MM+60002.79MM | CD | 72.6 | 17.3 | No | 2019-04-25 | D_s1_d2 | 1.63 | 33.1 | 47.5 | 1497 | 68.4 | D | 7.6 | 0.04 | s1 | n | y | d2
TN_2019_1479 |  | OP71199 20293469 | 528855T | RZ1C4OZ1-K 1KV VFD CLASS 3X240+3G50MM² | 62.64 | 3 | Vilanova | XLPE+INTERNALSHEATH1602SEES+COPPERTAPE+AL/POTAPE+LANTORLONGITUDINALTAPE+SHEATH1602SEES | CD | 69.6 | 18.7 | No | 2019-04-25 | B2_s1_d0 | 0.58 | 5.9 | 7.6 | 777 | 17.4 | B2 | 11 | 0.01 | s1 | n | n | d0
TN_2019_1480 |  | OP71198 20293459 | 533601B | RZ1C4OZ1-K 1KV VFD CLASS 3X2.5+3G0.75MM² | 15.13 | 10 | Vilanova | XLPE+INTERNALSHEATH1602SEES+COPPERTAPE+AL/POTAPE+LANTORLONGITUDINALTAPE+SHEATH1602SEES | CD | 68.1 | 19.2 | No | 2019-04-25 | C_s1_d0 | 0.78 | 17.9 | 32.9 | 1077 | 42.3 | C | 20.1 | 0.05 | s1 | n | n | d0
TN_2019_1481 |  | OP 71244/010 | 536360A | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 38.63 | 5 | Vilanova | HEPR+14202.11MM+60002.79MM | CD | 68.9 | 16.5 | No | 2019-04-29 | D_s1_d2 | 1.8 | 36 | 57.7 | 1374 | 58.6 | D | 16.2 | 0.04 | s1 | n | y | d2
TN_2019_1482 |  |  | C326 | RED ELEC RHZ1-RA-2OL(AS) 1X1600MM2 76/132KV | 104.31 | 2 | Vilanova | XLPE+ALFOIL+60AC+SKINDELE0563+20%1602 | CD | 66.6 | 17.4 | No | 2019-04-29 | B2_s1_d2 | 0.83 | 10 | 12 | 1470 | 31.4 | B2 | 0.8 | 0.01 | s1 | n | y | d2
|  | 71394 | 539182T | MRZF3Z1-K 1KV 5G1.5 | 16.2 | 9 | Manlleu |  | '-- | 40 | 18 | No | 2019-04-29 | B2_s1_d1 | 0.52 | 6.4 | 10.5 | 891 | 33.4 | B2 | 18.8 | 0.05 | s1 | y | n | d1
|  | 69811 | 531829A | AL-AFUMEX DZ1F3Z1 3KV 3X25 MM2 | 32.4 | 6 | Manlleu | EPR+GFR380 | '-- | 49 | 18.5 | No | 2019-04-25 | B2_s1_d2 | 0.73 | 6.9 | 8.3 | 1497 | 29.6 | B2 | 2.2 | 0.01 | s1 | Y | Y | d2
|  | 69810 | 537725J | AL-AFUMEX DZ1F3Z1 3KV 3X16 MM2 | 29.7 | 6 | Manlleu | EPR+GFR380 | '-- | 51 | 18 | No | 2019-04-25 | B2_s1_d2 | 0.77 | 9.7 | 16 | 1500 | 24.6 | B2 | 10.4 | 0.06 | s1 | Y | Y | d2
|  | 69812 | 252975Y | AL-AFUMEX DZ1F3Z1 3KV 2X150 MM2 | 48 | 4 | Manlleu | EPR+GFR380 | '-- | 48 | 4 | No | 2019-04-25 | B2_s1_d0 | 0.55 | 5.5 | 7.7 | 540 | 32.2 | B2 | 0.7 | 0 | s1 | N | N | d0
|  | 890658 | 12J4101 | CCTSST FR 0.3 5X4X1.4 | 27 | 6 | Manlleu |  | '-- | 47 | 19 | No | 2019-04-25 | B2_s1_d2 | 0.64 | 8.2 | 18.4 | 1479 | 45.7 | B2 | 5 | 0.03 | s1 | Y | Y | d2
|  | 890661 | 10J2586 | CCTSST FR 0.3 4X1.4 | 15.9 | 9 | Manlleu |  | '-- | 48 | 18 | No | 2019-04-25 | B2_s1_d2 | 0.72 | 6.9 | 13 | 1023 | 42.4 | B2 | 5.9 | 0.02 | s1 | Y | Y | d2
TN_2019_1483 |  |  |  | 750-7G2.5-SH-NF F 55-625-255 | 16.57 | 9 | Vilanova | ID3100FR/SV3300FR+0400FEIT+5300SEIT | CD | 63.1 | 17.8 | No | 2019-04-29 | B2_s1_d2 | 0.78 | 9.9 | 16.7 | 1164 | 20.6 | B2 | 10.2 | 0.03 | s1 | n | y | d2
TN_2019_1484 |  |  | -- | 750-3G2.5-SH-NF F 55-625-255 | 12.41 | 13 | Vilanova | ID3100FR/SV3300FR+0400FEIT+5300SEIT | CD | 79 | 16.6 | No | 2019-04-30 | C_s2_d2 | 1.17 | 16.2 | 29 | 1011 | 47.2 | C | 81.8 | 0.11 | s2 | n | y | d2
TN_2019_1485 |  |  |  | K25 5G1.50-SH-NF F 55-625-255 | 13.03 | 12 | Vilanova | ID3100FR/SV3300FR+0400FEIT+5300SEIT | CD | 73.9 | 17.4 | No | 2019-04-30 | C_s2_d2 | 0.88 | 20.9 | 27.6 | 912 | 46.6 | C | 73.6 | 0.11 | s2 | n | y | d2
TN_2019_1486 |  |  |  | 750-3G1.5-SH-NF F 55-625-255 | 10.86 | 14 | Vilanova | PENDINGTOCONFIRM | CD | 70.7 | 18.4 | No | 2019-04-30 | B2_s1_d2 | 1.12 | 13.7 | 30 | 918 | 54.4 | B2 | 47 | 0.1 | s1 | n | y | d2
TN_2019_1487 |  | OP83074273 | 536624M | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 40.98 | 5 | Vilanova | HEPR+1420FEES+6000SEES | CD | 66.1 | 19.1 | No | 2019-04-30 | D_s1_d2 | 1.46 | 31.5 | 60.3 | 1482 | 51.6 | D | 23.5 | 0.03 | s1 | n | y | d2
19050001 |  | 996967 | roll | HO7Z1-K TYPE2 (AS) 1X1.5MM2 GGC | 2.85 | 180 | Efectis | 1602SEES+SKINTPR-53 | -- | 61.5 | 16.7 | No | 2019-05-02 | D_s2_d0 | 3.3 | 52.6 | 81.9 | 1083 | 138.3 | D | 54.7 | 0.08 | s2 | n | n | d0
|  | 997051 | roll | ES05Z1-K (AS) 300/500 1X0.5 EXZHELLENT | 2.15 | 300 | Manlleu | TPR-56+TPR-53 | '-- | 52 | 18 | No | 2019-05-03 | D_s1_d0 | 3.3 | 48.1 | 73 | 804 | 153.9 | D | 42.9 | 0.07 | s1 | N | N | d0
|  | 997052 | roll | ES05Z1-K (AS) 300/500 1X0.75 EXZHELLENT | 2.32 | 270 | Manlleu | TPR-56+TPR-53 | '-- | 50 | 18 | No | 2019-05-03 | D_s2_d0 | 3.3 | 36.9 | 53.5 | 888 | 113.2 | D | 64.1 | 0.11 | s2 | N | N | d0
|  | 997053 | roll | ES05Z1-K (AS) 300/500 1X1 EXZHELLENT | 2.12 | 240 | Manlleu | TPR-56+TPR-53 | '-- | 50 | 19 | No | 2019-05-03 | D_s2_d0 | 2.12 | 23.4 | 40.2 | 840 | 107.1 | D | 100.5 | 0.19 | s2 | N | N | d0
|  | 704878 | roll | H07Z1-K (AS) 1X2.5 | 3.55 | 105 | Manlleu | TPR-52+SKINTPR-53 | '-- | 50 | 18 | No | 2019-05-03 | B2_s2_d1 | 1.43 | 11.8 | 29.6 | 648 | 85.3 | B2 | 288 | 0.09 | s2 | y | n | d1
|  | 409497 |  | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.8 | 3 | Manlleu |  | '-- | 55 | 18 | No | 2019-05-03 | B2_s1_d1 | 1.11 | 13.1 | 16.3 | 1110 | 31.1 | B2 | 4 | 0.02 | s1 | Y | N | d1
19040013 |  | 17822 | CE6639 | K25 5G1.50-SH-NF F 55-625-255 | 12.8 | 12 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 42.4 | 22.5 | No | 2019-04-17 | C_s2_d2 | 1.55 | 25.1 | 57.9 | 1101 | 103 | C | 56 | 0.15 | s2 | y | y | d2
19040018 |  | 17822 | EBM187849 | 750-7G2.5-SH-NF F 55-625-255 | 16.6 | 9 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 35.3 | 22.9 | No | 2019-04-30 | C_s1_d2 | 0.8 | 15.9 | 30.2 | 1140 | 37 | C | 24 | 0.06 | s1 | y | y | d2
19040019 |  | 17822 | EBM134207 | K25 5G1.50-SH-NF F 55-625-255 | 12.7 | 12 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 36.6 | 21.6 | No | 2019-04-30 | C_s1_d2 | 0.85 | 18.5 | 33.9 | 927 | 55 | C | 43 | 0.11 | s1 | y | y | d2
1905001 |  | 17822 | EBM143009 | K25 5G2.50-SH-NF F 55-625-255 | 14.4 | 11 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 34.2 | 24.7 | No | 2019-05-02 | B2_s1_d2 | 0.75 | 13.4 | 22.2 | 1035 | 40 | B2 | 31 | 0.08 | s1 | y | y | d2
1905002 |  | 17822 | EBM181748 | K25 5G1.50-SH-NF F 55-625-255 | 12.7 | 12 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 40.8 | 22.5 | No | 2019-05-02 | C_s1_d2 | 0.85 | 15 | 31.5 | 930 | 50 | C | 28 | 0.06 | s1 | y | y | d2
TN_2019_1488 |  | 20193984 | 82978931 | AFUMEX CLASS 750V HO7Z1-K (AS) TYPE2 1X2.5 | 3.58 | 105 | Vilanova | 1602SEES | CD | 51.5 | 16.2 | No | 2019-05-06 | D_s1_d1 | 3.3 | 34 | 52.1 | 705 | 164.9 | D | 35.9 | 0.06 | s1 | y | n | d1
TN_2019_1489 |  | OP83074273 | 536624M | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 40.98 | 5 | Vilanova | HEPR+1420FEES+6000SEES | CD | 49 | 17.6 | No | 2019-05-06 | D_s1_d2 | 1.36 | 34.5 | 73.9 | 1500 | 61.6 | D | 10.3 | 0.03 | s1 | n | y | d2
TN_2019_1490 |  | OP71314 | 538728Z | AFUMEX CLASS RZ1-K (AS) 1KV 4G16 | 20.71 | 7 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 48.5 | 18.5 | No | 2019-05-06 | C_s1_d2 | 1.11 | 12.5 | 39.1 | 1497 | 32.7 | C | 13.9 | 0.03 | s1 | n | y | d2
TN_2019_1491 |  | OP71198 20293459 | 533601B | RZ1C4OZ1-K 1KV VFD CLASS 3X2.5+3G0.75MM² | 15.13 | 10 | Vilanova | XLPE+INTERNALSHEATH1602SEES+COPPERTAPE+AL/POTAPE+LANTORLONGITUDINALTAPE+SHEATH1602SEES | CD | 62.7 | 14.8 | No | 2019-05-07 | B2_s1_d0 | 0.73 | 12.3 | 23 | 1080 | 35.3 | B2 | 25.8 | 0.06 | s1 | n | n | d0
TN_2019_1492 |  | OP71199 20293469 | 528855T | RZ1C4OZ1-K 1KV VFD CLASS 3X240+3G50MM² | 62.64 | 3 | Vilanova | XLPE+INTERNALSHEATH1602SEES+COPPERTAPE+AL/POTAPE+LANTORLONGITUDINALTAPE+SHEATH1602SEES | CD | 64.2 | 15.5 | No | 2019-05-07 | B2_s1_d0 | 0.56 | 5 | 6.9 | 807 | 20.7 | B2 | 6.6 | 0.01 | s1 | n | n | d0
TN_2019_1493 |  | OP82467468 | 487169G | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.83 | 8 | Vilanova | COPPERTAPE50%+MICA+LANTOR+1602 | CD | 70.5 | 17.3 | No | 2019-05-07 | D_s1_d2 | 1.23 | 29.1 | 67.5 | 1500 | 57.6 | D | 33.9 | 0.09 | s1 | n | y | d2
TN_2019_1494 |  |  | TE-H85923 | FG16OR16 2X70MM² - 0.6/1 KV | 30.13 | 6 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 69.9 | 18.4 | No | 2019-05-07 | B2_s2_d1 | 0.95 | 11 | 24 | 1500 | 33.9 | B2 | 334.3 | 0.51 | s2 | y | n | d1
TN_2019_1495 |  |  | T1-E60770 | FG16OR16 2X70MM² - 0.6/1 KV | 30.53 | 6 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 81.2 | 17.7 | No | 2019-05-08 | C_s3_d2 | 1.01 | 10.4 | 31.3 | 1497 | 32.5 | C | 526.6 | 0.71 | s3 | n | y | d2
TN_2019_1496 |  |  | TW-H23707 | FG16R16 1X240MM² - 0.6/1 KV | 27.99 | 6 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 78 | 18.6 | No | 2019-05-08 | C_s2_d1 | 1.16 | 16.5 | 47.8 | 1500 | 40 | C | 221.2 | 0.59 | s2 | y | n | d1
TN_2019_1497 |  |  | TW-H22504 | FG16R16 1X240MM² - 0.6/1 KV | 28.31 | 6 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 74.7 | 19.3 | No | 2019-05-08 | C_s2_d2 | 1.25 | 11.6 | 45.5 | 1500 | 37.9 | C | 246.2 | 0.68 | s2 | n | y | d2
TN_2019_1498 |  |  | T8-G69608 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.16 | 13 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 73.2 | 20.3 | No | 2019-05-08 | C_s2_d1 | 1.17 | 15.4 | 29.5 | 795 | 67.2 | C | 268.5 | 0.6 | s2 | y | n | d1
TN_2019_1499 |  |  | T8-G69601 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.13 | 13 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 44.8 | 16.7 | No | 2019-05-09 | B2_s2_d1 | 1.04 | 13.9 | 26.8 | 897 | 62.8 | B2 | 264.3 | 0.46 | s2 | y | n | d1
TN_2019_1500 |  |  | TE-H85923 | FG16OR16 2X70MM² - 0.6/1 KV | 30.13 | 6 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 48.9 | 19 | No | 2019-05-09 | B2_s2_d2 | 0.9 | 10.4 | 16.1 | 1473 | 33.2 | B2 | 287.6 | 0.35 | s2 | n | y | d2
TN_2019_1501 |  |  | TW-H22504 | FG16R16 1X240MM² - 0.6/1 KV | 28.31 | 6 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 54.8 | 20.8 | No | 2019-05-09 | B2_s2_d2 | 1.05 | 5 | 27.3 | 1494 | 22.8 | B2 | 198.8 | 0.37 | s2 | n | y | d2
TN_2019_1502 |  |  | T8-G69610 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.66 | 13 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 57.6 | 20.8 | No | 2019-05-09 | B2_s2_d1 | 1.47 | 10 | 28.9 | 780 | 63.3 | B2 | 360.2 | 0.75 | s2 | y | n | d1
TN_2019_1503 |  |  | T8-G69600 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.65 | 13 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 54.3 | 17.4 | No | 2019-05-10 | C_s3_d1 | 1.51 | 20.9 | 37.1 | 741 | 92.4 | C | 401.9 | 0.87 | s3 | y | n | d1
TN_2019_1504 |  |  | TW-H23707 | FG16R16 1X240MM² - 0.6/1 KV | 27.99 | 6 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 52.4 | 18.1 | No | 2019-05-10 | C_s2_d2 | 1.16 | 15.1 | 41.6 | 1497 | 35.1 | C | 250.9 | 0.5 | s2 | n | y | d2
TN_2019_1505 |  |  | T8-G69532 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.11 | 13 | Vilanova | 19AA+05AJFPIT+20AHPIT | CD | 48.5 | 20.3 | No | 2019-05-10 | C_s2_d1 | 1.49 | 18.1 | 32.7 | 807 | 71.1 | C | 368.3 | 0.65 | s2 | y | n | d1
TN_2019_1506 |  |  | T8-G69496 | FG16OR16 5G1.5MM² - 0.6/1 KV | 12.08 | 13 | Vilanova | INTUMESCENCE++05AJFPIT+20AHPIT | CD | 51.2 | 21.4 | No | 2019-05-10 | C_s2_d2 | 1.68 | 21.9 | 46.4 | 768 | 99.5 | C | 370 | 0.74 | s2 | n | y | d2
TN_2019_1507 |  |  | T1-E60770 | FG16OR16 2X70MM² - 0.6/1 KV | 30.53 | 6 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 48.7 | 22.4 | No | 2019-05-10 | B2_s2_d1 | 0.97 | 10.2 | 25.5 | 1500 | 32.4 | B2 | 295.7 | 0.53 | s2 | y | n | d1
19050003 |  | 17823 | -- | K25 5G1.50-SH-NF F 55-625-255 | 12.55 | 12 | Paron | ID3100/SV3300FR+400FEIT+54AASEIT | -- | 34.3 | 24.8 | No | 2019-05-10 | C_s1_d2 | 1.1 | 17.8 | 36.3 | 876 | 63 | C | 36 | 0.06 | s1 | y | y | d2
19050005 |  | 17823 | -- | 750-7G2.5-SH-NF F 55-625-255 | 16.6 | 9 | Paron | ID3100/SV3300FR+400FEIT+54AASEIT | -- | 35.6 | 34.8 | No | 2019-05-10 | B2_s1_d2 | 0.8 | 11.6 | 18.2 | 1155 | 29 | B2 | 18 | 0.05 | s1 | y | y | d2
|  | 409497 |  | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.8 | 3 | Manlleu | SMC-21+PRC-07+SMC-01+TPO-03+SMC-17 | -- | 52 | 19 | No | 2019-05-09 | B2_s1_d0 | 1.08 | 13.4 | 16.6 | 1500 | 27.9 | B2 | 0 | 0 | s1 | N | N | d0
|  | 409497 |  | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.8 | 3 | Manlleu | SMC-21+PRC-07+SMC-01+TPO-03+SMC-17 | '-- | 52 | 19 | No | 2019-05-09 | B2_s1_d0 | 0.82 | 10.9 | 12.5 | 906 | 28.5 | B2 | 4.4 | 0.01 | s1 | N | N | d0
|  | 997085 |  | H07Z1-K (AS) 1X1.5 | 2.91 | 165 | Manlleu | FPT572+TPR-53 | '-- | 35 | 19 | No | 2019-05-09 | D_s1_d0 | 3.3 | 68.5 | 148.9 | 945 | 259.7 | D | 14.7 | 0.05 | s1 | N | N | d0
|  | 408995 | 2053081 | HEPRZ1 (AS) 1X400MM2 12/20KV | 44.7 | 4 | Manlleu | SMC-01+GOM-14+SMC-05+TPR-49+TPO-03 | '-- | 40 | 19 | No | 2019-05-09 | D_s1_d0 | 1.83 | 30.3 | 37.3 | 972 | 69.1 | D | 42.8 | 0.2 | s1 | N | N | d0
TN_2019_1508 |  | 83082411 | 360461F | RHZ1-RA+2OL (AS) 76/132 KV 1X630 AL | 79.88 | 3 | Vilanova | XLPE+ALFOIL+60AC+SKINDELE0563+20%1602 | CD | 49.5 | 18.2 | No | 2019-05-14 | C_s1_d2 | 1.24 | 21.5 | 29.6 | 1251 | 46 | C | 31.7 | 0.04 | s1 | n | y | d2
TN_2019_1509 |  |  | 544202Z | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 38.77 | 5 | Vilanova | HEPR+14202.22MM+60002.43MM | CD | 56.4 | 18.2 | No | 2019-05-15 | D_s1_d2 | 1.48 | 34.6 | 66.4 | 1395 | 60.7 | D | 19.6 | 0.12 | s1 | n | y | d2
TN_2019_1510 |  |  | 544147-P | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 36.57 | 5 | Vilanova | HEPR+14201.09MM+60002.63MM | CD | 49.7 | 20 | No | 2019-05-15 | D_s1_d2 | 3.05 | 48.6 | 109.7 | 1497 | 91.7 | D | 2.5 | 0.04 | s1 | n | y | d2
1905006 |  | 17823 | -- | 750-7G2.5-SH-NF F 55-625-255 | 16.6 | 9 | Paron | ID3100/SV3300FR+400FEIT+54AASEIT | -- | 29.6 | 21.7 | No | 2019-05-16 | B2_s1_d2 | 0.45 | 8.3 | 11.3 | 1200 | 24 | B2 | 8 | 0.02 | s1 | y | y | d2
TN_2019_1511 |  |  | 544202Z | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 38.77 | 5 | Vilanova | HEPR+14202.22MM+60002.43MM | CD | 50.8 | 17.6 | No | 2019-05-16 | D_s1_d2 | 1.46 | 32.6 | 58.1 | 1440 | 54.4 | D | 24.9 | 0.05 | s1 | n | y | d2
TN_2019_1512 |  |  | 544202Z | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 38.77 | 5 | Vilanova | HEPR+14202.22MM+60002.43MM | CD | 47.5 | 19.9 | No | 2019-05-16 | D_s1_d2 | 1.63 | 68.4 | 61.9 | 1413 | 66.2 | D | 30.4 | 0.09 | s1 | n | y | d2
TN_2019_1513 |  |  | 544377P | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 40.17 | 5 | Vilanova | HEPR+14202.34MM+60003.34MM | CD | 78 | 16.5 | No | 2019-05-17 | D_s1_d2 | 1.49 | 38.4 | 65.4 | 1491 | 65 | D | 5.1 | 0.03 | s1 | n | y | d2
TN_2019_1514 |  |  | 544197U | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 38.93 | 5 | Vilanova | HEPR+14202.73MM+60002.25MM | OD | 77.5 | 16.4 | No | 2019-05-17 | C_s1_d2 | 1.57 | 24.4 | 37.2 | 1260 | 45.6 | C | 3.5 | 0.02 | s1 | n | y | d2
1905007 |  | 17834 | -- | 750-3G4-SH-NF F 55-625-255 | 13.9 | 11 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 40.9 | 20.7 | No | 2019-05-17 | B2_s1_d0 | 0.5 | 9 | 12.9 | 1092 | 28 | B2 | 15 | 0.02 | s1 | n | n | d0
|  | 71605 | 540850F | RZ1MZ1-K 2RH 1KV 19X1.5 | 22.1 | 7 | Manlleu | XLPE+6010+GFR380 | '-- | 44 | 20 | No | 2019-05-17 | B2_s1_d2 | 0.92 | 8.9 | 25 | 1491 | 36.1 | B2 | 9.8 | 0.06 | s1 | Y | Y | d2
|  | 71606 | 538861V | RZ1MZ1-K 2RH 1KV 5X120 | 64 | 3 | Manlleu | XLPE+6010+GFR380 | '-- | 45 | 20 | No | 2019-05-17 | B2_s1_d0 | 0.72 | 3.2 | 5.8 | 681 | 16.3 | B2 | 2 | 0.01 | s1 | N | N | d0
|  | 71991 | 543473G | DZ1F3Z1 ADIF B2CA 3X16 | 29 | 6 | Manlleu | XLPE+6010+GFR320 | '-- | 45 | 20 | No | 2019-05-17 | D_s1_d2 | 2.51 | 59.4 | 183.6 | 1500 | 153 | D | 36.6 | 0.13 | s1 | Y | Y | d2
|  | 71992 | 542557L | DZ1F3Z1 ADIF B2CA 3X25 | 31.5 | 6 | Manlleu | XLPE+6010+GFR320 | '-- | 45 | 20 | No | 2019-05-17 | C_s1_d2 | 1.23 | 26.2 | 51.9 | 1500 | 80.9 | C | 16.2 | 0.05 | s1 | Y | Y | d2
19050008 |  | 17834 | -- | K25 5G2.50-SH-NF F 55-625-255 | 14.3 | 11 | Paron | IX1400FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 41.2 | 25.5 | No | 2019-05-20 | C_s1_d2 | 0.8 | 16.6 | 33 | 1113 | 42 | C | 19 | 0.04 | s1 | y | y | d2
19050009 |  | 17834 | -- | 750-7G2.5-SH-NF F 55-625-255 | 17.3 | 9 | Paron | ID3100/SV3300FR+RUBANSCAPARUBANNÉ+0400FEIT+54ABSEIT | -- | 45.5 | 23.6 | No | 2019-05-20 | B2_s1_d2 | 0.7 | 11.2 | 17.5 | 1353 | 31 | B2 | 17 | 0.04 | s1 | y | y | d2
TN_2019_1515 |  |  | 544197U | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 38.93 | 5 | Vilanova | HEPR+14202.73MM+60002.25MM | OD | 72.8 | 14.9 | No | 2019-05-20 | D_s1_d2 | 1.73 | 33.6 | 56.8 | 1290 | 61.6 | D | 8.9 | 0.09 | s1 | n | y | d2
TN_2019_1516 |  | 70960/010 | 544200X | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 41.04 | 5 | Vilanova | 14200.95MM+60002.89MM | CD | 65 | 17.4 | No | 2019-05-20 | D_s1_d2 | 2.7 | 47.8 | 95 | 1500 | 79.2 | D | 18.3 | 0.04 | s1 | n | y | d2
TN_2019_1517 |  | 70960/010 | 544149S | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 41.3 | 5 | Vilanova | TPR-491.10MM+60003MM | CD | 54.9 | 20.9 | No | 2019-05-20 | E ou F_s1_d2 | 3.3 | 72.9 | 222.6 | 1500 | 185.5 | E ou F | 18.6 | 0.07 | s1 | n | y | d2
TN_2019_1518 |  |  | 544197U | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 38.93 | 5 | Vilanova | HEPR+14202.6MM+60002.28MM | OD | 73.2 | 18.5 | No | 2019-05-22 | D_s1_d2 | 1.35 | 30.6 | 51.9 | 1290 | 59.2 | D | 18.5 | 0.15 | s1 | n | y | d2
19050012 |  | 17834 | -- | 750-7G2.5-SH-NF F 55-625-255 | 17.4 | 9 | Paron | ID3100/SV3300FR+RUBANSCAPARUBANNÉ+0400FEIT+16GASEIT | -- | 33.5 | 24.2 | No | 2019-05-22 | B2_s1_d2 | 0.8 | 11.9 | 21.1 | 1230 | 23 | B2 | 18 | 0.06 | s1 | y | y | d2
19050011 |  | 17834 | -- | 750-7G2.5-SH-NF F 55-625-255 | 17.4 | 9 | Paron | ID3100/SV3300FR+RUBANSCAPARUBANNÉ+0400FEIT+54AASEIT | -- | 37 | 24 | No | 2019-05-22 | B2_s1_d2 | 0.7 | 7.7 | 12.6 | 1362 | 21.7 | B2 | 7.3 | 0.02 | s1 | y | y | d2
|  | 890671 | 14J7742 | EATST (X) 10X4X1.4 | 37.3 | 5 | Manlleu | TPR28+TPR55 | '-- | 49 | 20 | No | 2019-04-23 | B2_s1_d0 | 0.66 | 8.6 | 11.6 | 867 | 27.1 | B2 | 10.5 | 0.02 | s1 | n | n | d0
|  | 890673 | 14J7736 | CCTSST (X) FR 1X4X1.4 | 18.6 | 8 | Manlleu | TPR-55 | '-- | 48 | 20 | No | 2019-05-23 | B2_s1_d1 | 0.28 | 4.3 | 7.9 | 1500 | 25.1 | B2 | 0.3 | 0 | s1 | Y | N | d1
|  | 890674 | 14J7294 | CCTSST (X) FR 10X4X1.4 | 38.8 | 5 | Manlleu | TPR-55 | '-- | 35 | 20 | No | 2019-05-23 | B2_s1_d0 | 0.62 | 8.5 | 11.4 | 870 | 25.3 | B2 | 1.8 | 0.01 | s1 | N | N | d0
|  | 890664 | 10J2754 | EATST (H) 2X1.4 | 13.8 | 11 | Manlleu | TPR-28+TPR-55 | '-- | 41 | 20 | No | 2019-05-23 | B2_s1_d2 | 0.72 | 11.2 | 18.1 | 1047 | 42.5 | B2 | 3.4 | 0.01 | s1 | Y | Y | d2
|  |  |  | AFIRENAS-X H07Z1-K 1X1.5 | 2.92 | 165 | Manlleu | COMPETITORSAMPLE | '-- | 40 | 20 | No | 2019-05-22 | C_s1_d1 | 1.62 | 16.5 | 28.1 | 843 | 71.5 | C | 41.9 | 0.14 | s1 | y | n | d1
TN_2019_1519 |  |  | OF434 | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 76/132KV | 95.88 | 2 | Vilanova | XLPE+ALFOIL+60ACESNOIR+SKINSC SKIN:LE0563+30%1602 | OD | 69 | 20.4 | No | 2019-05-22 | B2_s1_d2 | 0.92 | 14.3 | 27.7 | 1476 | 30.2 | B2 | 13.4 | 0.03 | s1 | n | y | d2
TN_2019_1520 |  | OP71313 | 540792T | AFUMEX CLASS RZ1-K (AS) 1KV 1X25 | 12.42 | 13 | Vilanova | XLPE+1420+1602 | CD | 60 | 20.2 | No | 2019-05-23 | D_s1_d2 | 3.3 | 52.5 | 162.2 | 1497 | 135.5 | D | 37.7 | 0.06 | s1 | n | y | d2
TN_2019_1521 |  | OP71313 | 540792T | AFUMEX CLASS RZ1-K (AS) 1KV 1X25 | 12.42 | 13 | Vilanova | XLPE+1420+1602 | CD | 56 | 22.7 | No | 2019-05-23 | E ou F_s1_d2 | 3.3 | 70.2 | 221.7 | 1497 | 185.2 | E ou F | 42.5 | 0.15 | s1 | n | y | d2
TN_2019_1522 |  |  | TW-H83406 | FG16OR16 2X70MM² - 0.6/1 KV | 31.21 | 6 | Vilanova | 19AA_MEIT40%+05AJ_GPIT+20AH_SPIT0.50+1.80 | CD | 61.6 | 17.4 | No | 2019-05-26 | B2_s2_d0 | 0.76 | 3.8 | 6.9 | 1476 | 13.5 | B2 | 220.1 | 0.32 | s2 | n | n | d0
TN_2019_1523 |  |  | TW-H49976 | FG16R16 1X240MM² - 0.6/1 KV | 28.42 | 6 | Vilanova | 19AA_MEIT40%+05AJFPIT+20AHPIT | CD | 47.4 | 23.5 | No | 2019-05-26 | B2_s2_d2 | 1.09 | 5.4 | 19.5 | 1479 | 16.5 | B2 | 76.5 | 0.21 | s2 | n | y | d2
TN_2019_1524 |  |  | 545758R | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 39.15 | 5 | Vilanova | HEPR+14202.80MM+60002.16MM | OD | 49.8 | 22.8 | No | 2019-05-27 | B2_s1_d2 | 1.01 | 12.6 | 21.5 | 875 | 48.2 | B2 | 49 | 0.13 | s1 | n | y | d2
TN_2019_1525 |  |  | TW-H49976 | FG16R16 1X240MM² - 0.6/1 KV | 28.42 | 6 | Vilanova | 19AA_MEIT40%+05AJFPIT+20AHPIT | CD | 48.1 | 23.3 | No | 2019-05-27 | C_s2_d2 | 1.27 | 10.9 | 39.3 | 1500 | 32.8 | C | 265.1 | 0.52 | s2 | n | y | d2
TN_2019_1526 |  |  | TW-H83406 | FG16OR16 2X70MM² - 0.6/1 KV | 31.21 | 6 | Vilanova | 19AA_MEIT40%+05AJ_GPIT+20AH_SPIT0.50+1.80 | CD | 45.4 | 24.8 | No | 2019-05-27 | B2_s2_d1 | 1.28 | 4.6 | 25.6 | 1497 | 21.4 | B2 | 356.4 | 0.76 | s2 | y | n | d1
|  | 890664 | 10J2614 | EATST (H) 2X1.4 | 14.1 | 11 | Manlleu | TPR28+TPR55 | '-- | 38 | 22.1 | No | 2019-05-27 | B2_s1_d0 | 0.47 | 8.4 | 10.1 | 801 | 44.5 | B2 | 0 | 0.01 | s1 | N | N | d0
|  | 890668 | 14J7150 | EAST (H) 14X4X0.9 | 34.5 | 5 | Manlleu | TPR-55 | '-- | 42 | 22.8 | No | 2019-05-27 | B2_s1_d0 | 0.66 | 8.1 | 10.3 | 759 | 29.4 | B2 | 0.9 | 0 | s1 | N | N | d0
|  | 890669 | 16i4591 | EAST (H) 25X4X0.9 | 40.5 | 5 | Manlleu | TPR-55 | '-- | 43 | 21.5 | No | 2019-05-27 | B2_s1_d0 | 0.61 | 8.8 | 13.6 | 684 | 39.2 | B2 | 1.7 | 0 | s1 | N | N | d0
|  | 890675 | 14J7252 | CCTSST (X) FR 01 14X4X0.9 | 34.1 | 5 | Manlleu | TPR-55 | '-- | 43 | 20.3 | No | 2019-05-27 | B2_s1_d0 | 0.46 | 4.8 | 6.7 | 1005 | 15.3 | B2 | 2.8 | 0.01 | s1 | N | N | d0
|  | 890672 | 14J7744 | CCTSST (X) FR 01 25X4X0.9 | 39 | 5 | Manlleu | TPR-55 | '-- | 43 | 19.3 | No | 2019-05-27 | B2_s1_d0 | 0.38 | 4.2 | 7.2 | 684 | 20.3 | B2 | 0.6 | 0 | s1 | N | N | d0
TN_2019_1527 |  |  | 545758R | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 39.15 | 5 | Vilanova | HEPR+14202.80MM+60002.16MM | CD | 45.2 | 23.3 | No | 2019-05-28 | B2_s1_d2 | 0.7 | 10.9 | 16.3 | 786 | 42.7 | B2 | 18.9 | 0.05 | s1 | n | y | d2
TN_2019_1528 |  |  | 545758R | HEPRZ1(AS) 1X240MM2 3.6/6.0KV | 39.15 | 5 | Vilanova | HEPR+14202.80MM+60002.16MM | OD | 48.4 | 19 | No | 2019-05-29 | C_s1_d2 | 1.65 | 29.8 | 46.9 | 1143 | 57.4 | C | 24.8 | 0.12 | s1 | n | y | d2
TN_2019_1529 |  | 83082411 | 360461F | RHZ1-RA+2OL (AS) 76/132 KV 1X630 AL | 79.88 | 3 | Vilanova | XLPE+ALFOIL+60AC+SKINDELE0563+20%1602 | OD | 42.4 | 19.1 | No | 2019-05-29 | C_s1_d2 | 1.2 | 18.7 | 33.1 | 1479 | 35.2 | C | 37.7 | 0.09 | s1 | n | y | d2
|  | 274949 | 06N1524 | SZ1-K (AS+) 1KV 3G2.5 | 12.1 | 13 | Manlleu | VSI-15+TPR-49+TPR-55 | '-- | 38 | 23.6 | No | 2019-05-27 | B2_s1_d1 | 0.76 | 9.2 | 18.5 | 858 | 38.6 | B2 | 8.7 | 0.03 | s1 | Y | N | d1
|  | 274941 | 699131 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 9.95 | 15 | Manlleu | PRS-08+TPR-45+TPR-49+TPR-54 | '-- | 52 | 21.3 | No | 2019-05-28 | D_s1_d2 | 2.15 | 28.5 | 44 | 996 | 72.6 | D | 32.3 | 0.07 | s1 | Y | Y | d2
|  | 275088 | 697490 | EXZHELLENT RZ1-K (AS) 1KV 1X16 | 10.6 | 14 | Manlleu | PRS-03+TPR-54 | '-- | 50 | 22.9 | No | 2019-05-29 | B2_s1_d1 | 0.76 | 10.5 | 17.8 | 942 | 28.7 | B2 | 2.2 | 0.01 | s1 | Y | N | d1
|  | 890664 | 10J2754 | EATST (H) 2X1.4 | 13.8 | 11 | Manlleu | TPR-28+TPR-55 | '-- | 44 | 21.5 | No | 2019-05-30 | B2_s1_d2 | 0.64 | 8.4 | 12.1 | 807 | 36.3 | B2 | 3.7 | 0.01 | s1 | y | y | d2
19060001 |  | 17852 | -- | 750-3G4-SH-NF F 55-625-255 | 14 | 11 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 50.3 | 24.4 | No | 2019-06-03 | B2_s1_d0 | 0.7 | 9.9 | 17.9 | 1152 | 36 | B2 | 10 | 0.02 | s1 | n | n | d0
19060002 |  | 17834 |  | K25 5G2.50-SH-NF F 55-625-255 | 14.2 | 11 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 51.2 | 23.7 | No | 2019-06-03 | B2_s1_d2 | 0.8 | 12.7 | 23.4 | 1095 | 29 | B2 | 16 | 0.03 | s1 | y | y | d2
19060003 |  | 17761 | CE6627 | K25 750V 1X4.0 -SH-NF F 55-625-255 ( IRRADIÉ) | 4.3 | 75 | Paron | 1602SEES | -- | 50.5 | 24.3 | No | 2019-06-03 | C_s1_d1 | 1.7 | 15.4 | 39.4 | 783 | 85 | C | 42 | 0.16 | s1 | y | n | d1
19060004 |  | 17761 | CE6627 | K25 750V 1X2.5-SH-NF F 55-625-255 ( IRRADIÉ) | 3.56 | 105 | Paron | 1602SEES | -- | 47.8 | 24.6 | No | 2019-06-03 | C_s1_d1 | 1.55 | 13.5 | 36 | 708 | 92 | C | 35 | 0.15 | s1 | y | n | d1
|  | 275257 | 06F9594 | EXZHELLENT RZ1-K (AS) 1KV) 3G1.5 | 9.9 | 15 | Manlleu |  | '-- | 36 | 22 | No | 2019-06-03 | D_s1_d2 | 2.53 | 37.4 | 50.8 | 978 | 75.3 | D | 42.5 | 0.09 | s1 | Y | Y | d2
|  |  |  | TOXFREE ZH H07Z1-K 1X1.5 | 2.96 | 165 | Manlleu | COMPETITORSAMPLE | '-- | 37 | 22 | No | 2019-04-03 | B2_s1_d1 | 1.42 | 10.5 | 25.4 | 855 | 56.1 | B2 | 19.8 | 0.06 | s1 | Y | N | d1
1906005 |  | 17761 | CE6627 | K25 750V 1X1.5 -SH-NF F 55-625-255 ( IRRADIÉ) | 3.17 | 135 | Paron | 1602SEES | -- | 51.9 | 24.6 | No | 2019-06-05 | D_s2_d2 | 3.3 | 34.5 | 71 | 723 | 177 | D | 68 | 0.13 | s2 | y | y | d2
|  | 71991 | 547583Z | DZ1F3Z1 ADIF B2CA 3KV 3X16 AL | 30.2 | 6 | Manlleu | HEPR+1602+5300 | '-- | 35 | 22 | No | 2019-06-06 | B2_s1_d2 | 0.71 | 9.2 | 12.4 | 1434 | 23.7 | B2 | 1.4 | 0.01 | s1 | Y | Y | d2
|  | 71991 | 547606Z | DZ1F3Z1 ADIF B2CA 3KV 3X16 AL | 29.3 | 6 | Manlleu | HEPR+1602+S663 | '-- | 35 | 21.9 | No | 2019-06-06 | B2_s1_d2 | 0.68 | 9.3 | 13.4 | 1488 | 20.7 | B2 | 7 | 0.03 | s1 | Y | Y | d2
|  | 71992 | 544504C | DZ1F3Z1 ADIF B2CA 3KV 3X25 AL | 31.7 | 6 | Manlleu | HEPR+1602+5300 | '-- | 36 | 22.7 | No | 2019-06-06 | B2_s1_d2 | 0.65 | 7.1 | 10.3 | 1278 | 20.1 | B2 | 0.9 | 0.01 | s1 | Y | Y | d2
|  | 71992 | 547582Y | DZ1F3Z1 ADIF B2CA 3KV 3X25 AL | 32.3 | 6 | Manlleu | HEPR+1602+S663 | '-- | 34 | 21.9 | No | 2019-06-06 | B2_s1_d2 | 0.72 | 12.7 | 22.4 | 1500 | 22.2 | B2 | 2.7 | 0.01 | s1 | Y | Y | d2
1906006 |  | 17861 |  | 750-5G6MM²-SH-NF F 55-625-255 | 17 | 9 | Paron | IX1400FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 52.9 | 20.6 | No | 2019-06-12 | B2_s1_d2 | 0.7 | 10.3 | 20.2 | 1338 | 28 | B2 | 12 | 0.03 | s1 | y | y | d2
1906007 |  | 17861 |  | 750-5G6MM²-SH-NF F 55-625-255 | 17.5 | 8 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 52.7 | 21.3 | No | 2019-06-12 | B2_s1_d2 | 0.7 | 8 | 21.6 | 1491 | 20 | B2 | 9 | 0.03 | s1 | y | y | d2
|  | 739662 | 16I4600 | EXAVB 0.6/1 3X95 | 36.4 | 5 | Manlleu |  | '-- | 45 | 20.6 | No | 2019-06-12 | B2_s2_d1 | 0.69 | 4.8 | 5.8 | 495 | 30.1 | B2 | 213.1 | 0.3 | s2 | Y | N | d1
|  | 408995 | 2053081 | HEPRZ1(AS) 1X240MM2 12/20 | 44.7 | 4 | Manlleu |  | '-- | 45 | 21 | No | 2019-06-12 | C_s2_d0 | 1.87 | 21.7 | 28.7 | 900 | 62.4 | C | 61.2 | 0.22 | s2 | N | N | d0
|  | 739351 | 16i4600 | XVB 0.6/1 4X70 | 33.6 | 5 | Manlleu |  | '-- | 33.6 | 5 | No | 2019-06-12 | C_s2_d2 | 1.12 | 11.9 | 43.9 | 1494 | 36.8 | C | 266.9 | 0.82 | s2 | Y | Y | d2
|  | 738772 | ROLL | XGB 4X70 | 32.7 | 6 | Manlleu |  | '-- | 32.7 | 6 | No | 2019-06-12 | B2_s1_d0 | 0.41 | 3.8 | 6 | 786 | 17.2 | B2 | 13.2 | 0.02 | s1 | N | N | d0
TN_2019_1543 |  |  |  | 4X10 RTE S 740 PRYSMIAN 255 2018 37 | 21.53 | 7 | Vilanova | 4300IP+1400FP+4300IP+2800SP | -- | 73.6 | 18.7 | No | 2019-06-16 | B2_s3_d0 | 0.56 | 8.2 | 14.1 | 855 | 51.8 | B2 | 420 | 0.84 | s3 | n | n | d0
TN_2019_1544 |  |  |  | 4X1.5 RTE S 740 PRYSMIAN 255 2019 19 | 15.16 | 10 | Vilanova | 4300IP+1400FP+4300IP+2800SP | -- | 63 | 22.5 | No | 2019-06-16 | B2_s2_d1 | 0.7 | 5.7 | 17.7 | 585 | 63.3 | B2 | 389.2 | 1.2 | s2 | y | n | d1
TN_2019_1538 |  |  | 423059X | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.92 | 3 | Vilanova |  | CD | 60.9 | 22.6 | No | 2019-06-17 | C_s1_d2 | 1.06 | 22 | 43.6 | 1500 | 37.1 | C | 14.63 | 0.02 | s1 | n | y | d2
TN_2019_1539 |  |  | 529884L | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 127/220KV AL +H250 | 103.48 | 2 | Vilanova | XLPE+ALFOIL+60ACESNOIR+SKINSC | CD | 68 | 19.9 | No | 2019-06-17 | B2_s1_d2 | 0.85 | 9.8 | 16.4 | 1491 | 22.6 | B2 | 9.5 | 0.01 | s1 | n | y | d2
TN_2019_1542 |  | OP71198 20293459 | 533601B | RZ1C4OZ1-K 1KV VFD CLASS 3X2.5+3G0.75MM² | 15.13 | 10 | Vilanova | XLPE+INTERNALSHEATH1602SEES+COPPERTAPE+AL/POTAPE+LANTORLONGITUDINALTAPE+SHEATH1602SEES | CD | 74.4 | 18.2 | No | 2019-06-16 | B2_s1_d1 | 0.73 | 12 | 23.1 | 1131 | 29.9 | B2 | 34.8 | 0.08 | s1 | y | n | d1
TN_2019_1545 |  | OP71199 20293469 | 528855T | RZ1C4OZ1-K 1KV VFD CLASS 3X240+3G50MM² | 62.64 | 3 | Vilanova | XLPE+INTERNALSHEATH1602SEES+COPPERTAPE+AL/POTAPE+LANTORLONGITUDINALTAPE+SHEATH1602SEES | CD | 64.5 | 23.6 | No | 2019-06-16 | B2_s1_d0 | 0.54 | 4.2 | 5.6 | 864 | 17 | B2 | 6.6 | 0.01 | s1 | n | n | d0
|  | 43556 | 547584A | CCTSST (H) FR03 4X1.4 | 15.3 | 10 | Manlleu | TPR-55 | '-- | 48 | 23.6 | No | 2019-06-17 | B2_s1_d2 | 0.65 | 11 | 18.1 | 876 | 63 | B2 | 7.9 | 0.02 | s1 | Y | Y | d2
|  | 43556 | 544582M | CCTSST (H) FR03 5X4X1.4 | 27.6 | 6 | Manlleu | TPR-55 | '-- | 48 | 24.5 | No | 2019-06-17 | B2_s1_d2 | 0.83 | 6.6 | 19.8 | 1494 | 31.9 | B2 | 4.4 | 0.03 | s1 | Y | Y | d2
|  | 71820 | 20296008 | EXZHELLENT RZ1-K (AS) 1KV 1X35 | 13.6 | 11 | Manlleu | XLPE/TPR-54RETICULATALACEL·LA | '-- | 13.6 | 11 | No | 2019-06-17 | B2_s1_d2 | 0.85 | 11.1 | 18.2 | 1092 | 22.9 | B2 | 0 | 0 | s1 | Y | Y | d2
19060008 |  | 17882 | -- | 750-5G2.5-SH-NF F 55-625-255 | 15 | 10 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 59.1 | 24.6 | No | 2019-06-19 | B2_s1_d1 | 0.7 | 8.1 | 14.3 | 1359 | 27 | B2 | 10 | 0.02 | s1 | y | n | d1
19060009 |  | 17882 | -- | 750-5G6MM²-SH-NF F 55-625-255 | 18.7 | 8 | Paron | IX1400FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 55.1 | 25.1 | No | 2019-06-19 | B2_s1_d1 | 0.55 | 4.2 | 8.6 | 1494 | 24 | B2 | 5 | 0.01 | s1 | y | n | d1
19060010 |  | 17882 | -- | 750-5G6MM²-SH-NF F 55-625-255 | 18.2 | 8 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 51.4 | 26.4 | No | 2019-06-19 | B2_s1_d1 | 0.5 | 3.4 | 6.6 | 1494 | 19 | B2 | 6 | 0.01 | s1 | y | n | d1
TN_2019_1546 |  |  | T7-I33651 | FG16OR16 5G1.5MM² - 0.6/1 KV | 11.62 | 13 | Vilanova | INSULATIONSTANDARD+05AJ+20AH | OD | 70 | 21.1 | No | 2019-06-18 | B2_s2_d1 | 1.09 | 14.5 | 28.5 | 909 | 74.2 | B2 | 283.2 | 0.63 | s2 | y | n | d1
TN_2019_1547 |  |  | T7-I33494 | FG16R16 1X10MM² - 0.6/1 KV | 8.85 | 17 | Vilanova | INSULATIONSTANDARD+05AJ+20AH | OD | 62 | 22.6 | No | 2019-06-18 | B2_s2_d1 | 0.69 | 6 | 17.5 | 570 | 68.9 | B2 | 109.7 | 0.4 | s2 | y | n | d1
TN_2019_1548 |  |  | T9-I26483 | FG16R16 1X240MM² - 0.6/1 KV | 28.34 | 6 | Vilanova | SXLPE+05AJFPIT+20AHPIT | OD | 52.5 | 23.6 | No | 2019-06-18 | C_s2_d1 | 1.21 | 14.9 | 42 | 1500 | 37.7 | C | 217.9 | 0.44 | s2 | y | n | d1
TN_2019_1549 |  |  | T9-I26491 | FG16OR16 2X70MM² - 0.6/1 KV | 31.06 | 6 | Vilanova | INSULATION19AA+05AJ+20AH | OD | 47.1 | 25 | No | 2019-06-18 | B2_s2_d1 | 0.96 | 12.9 | 30 | 1500 | 40 | B2 | 297.4 | 0.56 | s2 | y | n | d1
TN_2019_1550 |  |  | T9-D61258 | FG16R16 1X240MM² - 0.6/1 KV | 28.99 | 6 | Vilanova | SXLPE+05AJFPIT+20AHPIT | CD | 70.3 | 22.5 | No | 2019-06-19 | C_s2_d2 | 1.12 | 10.8 | 31.4 | 1491 | 34.7 | C | 199.6 | 0.38 | s2 | n | y | d2
TN_2019_1551 |  | 71127 | 543464X | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 27.74 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 63 | 24 | No | 2019-06-19 | B2_s1_d1 | 0.64 | 5 | 10.4 | 1497 | 15.3 | B2 | 7.6 | 0.01 | s1 | y | n | d1
TN_2019_1552 |  | 71127 | 543464X | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 27.74 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 61.8 | 25.2 | No | 2019-06-19 | B2_s1_d1 | 0.85 | 6.4 | 10.8 | 1497 | 14.7 | B2 | 5 | 0.01 | s1 | y | n | d1
TN_2019_1553 |  | 70346 | 553456H | AFUMEX CLASS 1Z1C7Z1-K 0.6/1 KV 37X1MM2 | 28.83 | 6 | Vilanova | CUBIERTADE5300SEIT+CINTADEFIBRADEVIDRIOBAJOCUBIERTA. | CD | 74.2 | 22.6 | No | 2019-06-20 | B2_s1_d2 | 0.5 | 6.5 | 10.6 | 1371 | 27 | B2 | 8.8 | 0.02 | s1 | n | y | d2
TN_2019_1554 |  | 70346 | 553455G | AFUMEX CLASS 1Z1C7Z1-K 0.6/1 KV 37X1MM2 | 28.51 | 6 | Vilanova | CUBIERTADE5300SEIT | CD | 71.2 | 23.5 | No | 2019-06-20 | B2_s1_d2 | 0.78 | 11.7 | 23.1 | 1491 | 21.8 | B2 | 10.3 | 0.03 | s1 | n | y | d2
TN_2019_1555 |  | 71314 | 539667V | AFUMEX CLASS RZ1-K (AS) 1KV 4G16 | 20.48 | 8 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 70.3 | 21 | No | 2019-06-21 | C_s1_d2 | 0.85 | 10.5 | 32.3 | 1500 | 26.9 | C | 15 | 0.03 | s1 | n | y | d2
TN_2019_1556 |  | 71314 | 539672A | AFUMEX CLASS RZ1-K (AS) 1KV 4G16 | 20.6 | 7 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 70.9 | 21.6 | No | 2019-06-21 | C_s1_d2 | 1.83 | 10.8 | 32 | 1497 | 26.7 | C | 12.2 | 0.03 | s1 | n | y | d2
TN_2019_1557 |  | 72205 | 545960K | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 15.07 | 10 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 65.9 | 23.8 | No | 2019-06-21 | C_s1_d2 | 1.16 | 16.4 | 25.3 | 1401 | 31.3 | C | 19.9 | 0.06 | s1 | n | y | d2
TN_2019_1558 |  | 72205 | 545961L | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 14.96 | 10 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 62.2 | 24.6 | No | 2019-06-21 | C_s1_d1 | 1.17 | 17.3 | 31.3 | 1500 | 31.9 | C | 16.4 | 0.04 | s1 | y | n | d1
TN_2019_1559 |  | 72618 | 555106B | AFUMEX CLASS RZ1 (AS) 3 KV METRO 1X630 MM2 | 41.18 | 5 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 58.7 | 25.8 | No | 2019-06-21 | B2_s1_d2 | 0.47 | 11.2 | 20.5 | 1500 | 21.6 | B2 | 7.1 | 0.01 | s1 | n | y | d2
19060011 |  | 17861 |  | 750-5G6MM²-SH-NF F 55-625-255 | 17.5 | 8 | Paron | IX1400FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 49.4 | 21.8 | No | 2019-06-21 | B2_s1_d1 | 0.55 | 7 | 18.2 | 1500 | 23 | B2 | 8 | 0.03 | s1 | y | n | d1
19060012 |  | 17903 | EBM 186979 | 750 NE -SH-70MM²-CT 442-PRYSMIAN | 18.7 | 8 | Paron | ID3100FR/SV3300FR+SV3200FR | -- | 22.1 | 45.1 | No | 2019-06-22 | B2_s1_d2 | 0.4 | 5.9 | 9.3 | 1125 | 22 | B2 | 11 | 0.04 | s1 | y | y | d2
19060013 |  | 17881 | DBP 164837 | 750 NE -SH-70MM²-CT 442-PRYSMIAN | 16.5 | 9 | Paron | ID3800FR/SV3200FR | -- | 21.4 | 47.4 | No | 2019-06-22 | C_s1_d2 | 1.5 | 17.1 | 41.1 | 1488 | 35 | C | 45 | 0.13 | s1 | y | y | d2
19060014 |  | 17882 |  | 750-5G6MM²-SH-NF F 55-625-255 | 18.2 | 8 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 60.8 | 24.7 | No | 2019-06-24 | B2_s1_d2 | 0.42 | 3.9 | 7.8 | 1488 | 17 | B2 | 7 | 0.01 | s1 | y | y | d2
19060015 |  | 17882 | -- | 750-5G6MM²-SH-NF F 55-625-255 | 18.7 | 8 | Paron | IX1400FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 61.3 | 25.6 | No | 2019-06-24 | B2_s1_d0 | 0.4 | 2.1 | 4.5 | 558 | 18 | B2 | 7 | 0.01 | s1 | n | n | d0
19060016 |  | 17882 | -- | 750-5G2.5-SH-NF F 55-625-255 | 15 | 10 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 53.4 | 27.9 | No | 2019-06-24 | B2_s1_d2 | 0.6 | 5.9 | 10 | 1422 | 19 | B2 | 11 | 0.02 | s1 | y | y | d2
TN_2019_1560 |  | OP83081402 | 547690R | EPROTENAX DHVFAV(I) 20KV 1X50 +H16 | 36.53 | 5 | Vilanova | EPDM+PVC | CD | 68.5 | 24.5 | No | 2019-06-25 | D_s3_d2 | 3.3 | 60.7 | 193.1 | 1497 | 161.4 | D | 2047 | 4.12 | s3 | n | y | d2
TN_2019_1561 |  |  | 524460R | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.66 | 8 | Vilanova | COPPERTAPE50%+MICA+LANTOR+1602 | CD | 60.4 | 27.3 | No | 2019-06-25 | C_s1_d2 | 1.15 | 28.4 | 56.2 | 1500 | 52.8 | C | 29.2 | 0.11 | s1 | n | y | d2
TN_2019_1532 |  | OP8297262 | 549170Z | AFUMEX CLASS RZ1-K (AS) 1KV 1X16 | 11.4 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 42.8 | 28.2 | No | 2019-06-27 | D_s1_d2 | 2.09 | 25.2 | 35.7 | 831 | 68.1 | D | 46.4 | 0.09 | s1 | n | y | d2
TN_2019_1533 |  | OP82979510 | 549133J | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.53 | 14 | Vilanova | XLPE+1420+1602 | CD | 65.8 | 27.7 | No | 2019-06-28 | D_s2_d2 | 2.07 | 27.2 | 37 | 894 | 70.2 | D | 50.5 | 0.1 | s2 | n | y | d2
TN_2019_1562 |  |  | BBT909121 | 14X1.5 RTE S 740 PRYSMIAN 255 2019 18 | 21.57 | 7 | Vilanova | PENDINGTOCONFIRM | CD | 48 | 24 | No | 2019-06-28 | B2_s3_d2 | 0.68 | 6 | 10.5 | 555 | 47.9 | B2 | 615.3 | 1.07 | s3 | n | y | d2
TN_2019_1563 |  |  | ACP01519493 | 4X1.5 RTE S 740 PRYSMIAN 255 2019 19 | 15.33 | 10 | Vilanova | PENDINGTOCONFIRM | CD | 46.3 | 24.4 | No | 2019-06-28 | B2_s2_d0 | 0.69 | 5.6 | 13.4 | 717 | 62 | B2 | 355.2 | 1.01 | s2 | n | n | d0
TN_2019_1564 |  |  | BBT909068 | 4X6 RTE S 740 PRYSMIAN 255 2018 4 | 19.41 | 8 | Vilanova | PENDINGTOCONFIRM | CD | 43.3 | 27 | No | 2019-06-28 | B2_s3_d2 | 0.69 | 13.9 | 17.9 | 651 | 81.9 | B2 | 461.5 | 0.96 | s3 | n | y | d2
|  | 275581 | 09T4201 | SZ1-K PH120(AS+) 4G2.5 | 13.1 | 12 | Manlleu |  | -- | 44 | 25.7 | No | 2019-06-28 | B2_s1_d1 | 0.75 | 8.8 | 16.6 | 903 | 35 | B2 | 9.3 | 0.03 | s1 | y | n | d1
|  | 67477 | 540715J | ATEX DZ1MZ1-K 2RH 19X1.5 | 23.4 | 7 | Manlleu | XLPE+6010+TPU | -- | 31 | 32.4 | No | 2019-06-28 | B2_s2_d2 | 0.87 | 13.6 | 22.1 | 1233 | 83.3 | B2 | 149.6 | 0.31 | s2 | Y | Y | d2
|  | 706039 |  | H07Z1-K (AS) 1X1.5 | 2.98 | 165 | Manlleu | FPT578AMBCALOXOL | -- | 31 | 31.4 | No | 2019-06-26 | D_s1_d0 | 3.3 | 66.7 | 136.9 | 960 | 231.6 | D | 20.3 | 0.06 | s1 | n | n | d0
|  | 706039 |  | H07Z1-K (AS) 1X1.5 | 2.98 | 165 | Manlleu | FPT577AMBCALOXOL | -- | 40 | 27.3 | No | 2019-06-26 | D_s1_d0 | 3.3 | 50.1 | 80.6 | 873 | 153.5 | D | 11.3 | 0.05 | s1 | N | N | d0
|  | 706039 |  | H07Z1-K (AS) 1X1.5 | 2.92 | 165 | Manlleu | FPT577SINCALOXOL | -- | 34 | 28.5 | No | 2019-06-26 | D_s1_d0 | 3.3 | 55.4 | 76 | 768 | 178.9 | D | 40.7 | 0.07 | s1 | N | N | d0
|  | 706039 |  | H07Z1-K (AS) 1X1.5 | 2.98 | 165 | Manlleu | FPT578SINCALOXOL | -- | 31 | 28.6 | No | 2019-06-27 | D_s1_d0 | 3.3 | 45.8 | 74.4 | 873 | 136.7 | D | 19.9 | 0.04 | s1 | N | N | d0
|  | 83074993 | 235821C | H07Z1-K (AS) 1X1.5 | 2.85 | 165 | Manlleu | 1602SEESSTANDARD+SKIN1510SEES | -- | 40 | 29.6 | No | 2019-06-28 | C_s1_d0 | 1.43 | 12.3 | 30.2 | 690 | 99.3 | C | 23.9 | 0.09 | s1 | N | N | d0
|  | 83074993 | 235818Z | H07Z1-K (AS) 1X1.5 | 2.95 | 165 | Manlleu | 1602SEESCONECOPIREN | -- | 40 | 28.6 | No | 2019-06-28 | C_s1_d0 | 1.8 | 22.6 | 47.4 | 597 | 168 | C | 33.6 | 0.13 | s1 | N | N | d0
|  | 83074993 |  | H07Z1-K (AS) 1X1.5 | 2.76 | 180 | Manlleu | 16GASEES | -- | 44 | 27.3 | No | 2019-06-28 | C_s1_d0 | 1.41 | 14.1 | 35.5 | 669 | 102.4 | C | 16.8 | 0.06 | s1 | N | N | d0
|  |  | 546201X | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.6 | 15 | Manlleu | SXLPE+1420FEES+1602SEES | -- | 33 | 25.7 | No | 2019-06-27 |  | 1.73 | 27.4 | 36.9 | 951 | 60.4 |  | 32.9 | 0.07 |  | Y | Y
TN_2019_1565 |  |  | BBT909079 | 4X1.5 RTE S 740 PRYSMIAN 255 2018 42 | 15.43 | 10 | Vilanova | PENDINGTOCONFIRM | CD | 42.2 | 28.5 | No | 2019-06-28 | B2_s3_d2 | 0.86 | 9.3 | 22.5 | 687 | 61.4 | B2 | 530.5 | 1.37 | s3 | n | y | d2
|  | 890724 | 12S9933 | XGB 3X35 +16 | 26.6 | 20 | Manlleu | 1400/1602 | -- | 45 | 29.6 | No | 2019-07-05 | B2_s1_d1 | 0.67 | 6.2 | 8.5 | 963 | 16.5 | B2 | 8 | 0.02 | s1 | y | n | d1
19060019 |  | CEL-0542 | 697490 | EXZHELLENT RZ1-K (AS) 1KV 1X16 | 11.19 | 16 | CEIS | PRS-03+TPR-54 | -- | 42 | 19.1 | No | 2019-06-11 | B2_s1_d0 | 0.45 | 7.9 | 13.2 | 861 | 32.9 | B2 | 5.7 | 0.02 | s1 | n | n | d0
TN_2019_1566 |  | 83043237 | 554031H | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 27.13 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 53.6 | 24.2 | No | 2019-06-30 | B2_s1_d0 | 0.46 | 4 | 8.7 | 1500 | 8.7 | B2 | 1.2 | 0 | s1 | n | n | d0
TN_2019_1567 |  | 82384360 | 553137L | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 11.44 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 54.4 | 24.6 | No | 2019-06-30 | C_s1_d1 | 1.85 | 25.6 | 36 | 894 | 60.9 | C | 33.9 | 0.08 | s1 | y | n | d1
TN_2019_1568 |  | 83026901 | 554128N | AFUMEX CLASS RZ1-K (AS) 1KV 5G2.5 | 13.46 | 12 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 66.4 | 26.9 | No | 2019-06-30 | D_s1_d2 | 2.46 | 34.4 | 60.2 | 1356 | 71.2 | D | 26.9 | 0.05 | s1 | n | y | d2
TN_2019_1569 |  |  | 5096922 | EXZHELLENT RZ1-K (AS) 1KV 1X16 | 10.75 | 14 | Vilanova | PRS-03+TPR-54 | CD | 63 | 28.4 | No | 2019-06-30 | C_s1_d0 | 1.43 | 18.5 | 23.1 | 1113 | 40.5 | C | 18.6 | 0.03 | s1 | n | n | d0
|  |  |  | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.02 | 15 | CEIS | PRS-08+TPR-45+TPR-49+TPR-54 | -- | 43 | 19.9 | No | 2019-06-11 | B2_s1_d0 | 0.4 | 10.3 | 17 | 717 | 51.7 | B2 | 7.5 | 0.02 | s1 | n | n | d0
TN_2019_1570 |  |  | 5096924 | AFUMEX CLASS 750V HO7Z1-K (AS) TYPE2 1X2.5 | 3.63 | 105 | Vilanova | 1602SEES | CD | 65.9 | 24.4 | No | 2019-07-02 | B2_s1_d0 | 1.25 | 9 | 24 | 633 | 82.5 | B2 | 41.3 | 0.14 | s1 | n | n | d0
TN_2019_1571 |  |  | 5096920 | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 9.92 | 15 | Vilanova | PRS-08+TPR-45+TPR-49+TPR-54 | CD | 64.4 | 25.2 | No | 2019-07-02 | D_s1_d0 | 2.63 | 31.3 | 42.3 | 1050 | 63.6 | D | 36.9 | 0.07 | s1 | n | n | d0
TN_2019_1572 |  |  |  | CABLES RCT ARA-Z1 RZ1-K (AS) 0.6/1KV 1X16 | 10.03 | 15 | Vilanova | COMPETITORSAMPLE | CD | 59.8 | 27.4 | No | 2019-07-02 | C_s1_d0 | 1.86 | 14.9 | 22.8 | 906 | 44.6 | C | 36.1 | 0.07 | s1 | n | n | d0
TN_2019_1573 |  | 72618 | 555106B | AFUMEX CLASS RZ1 (AS) 3 KV METRO 1X630 MM2 | 41.18 | 5 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 62.4 | 28.3 | No | 2019-07-02 | B2_s1_d1 | 0.5 | 3.7 | 4.8 | 882 | 9.6 | B2 | 6.2 | 0.01 | s1 | y | n | d1
TN_2019_1574 |  |  | 5096934 | CABLES RCT ARA-Z1 RZ1-K (AS) 0.6/1KV 3G1.5 | 10.67 | 14 | Vilanova | COMPETITORSAMPLE | CD | 62.3 | 28.3 | No | 2019-07-02 | B2_s1_d0 | 0.72 | 12.4 | 26.9 | 759 | 59.6 | B2 | 38.1 | 0.12 | s1 | n | n | d0
19070001 |  | 17916 |  | 750-5G2.5-SH-NF F 55-625-255 | 16 | 9 | Paron | IX1400FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 38.8 | 23.3 | No | 2019-07-04 | B2_s1_d2 | 0.5 | 7.4 | 14.3 | 1497 | 25 | B2 | 9 | 0.2 | s1 | y | y | d2
19070002 |  | 17916 |  | 750-7G2.5-SH-NF F 55-625-255 | 17.6 | 8 | Paron | ID3100/SV3300FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 39.3 | 23.5 | No | 2019-07-04 | B2_s1_d2 | 0.3 | 4.7 | 5.8 | 1242 | 18 | B2 | 8 | 0.01 | s1 | y | y | d2
19070003 |  | 17916 |  | 750-5G1.5-SH-NF F 55-625-255 | 15 | 10 | Paron | ID3100/SV3300FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 37.9 | 27.6 | No | 2019-07-04 | B2_s1_d2 | 0.9 | 5.9 | 11.9 | 957 | 18 | B2 | 15 | 0.03 | s1 | y | y | d2
19070004 |  | 17825 | -- | PRYSMIAN 255/2019-1*2500 AL-320 000V ELECTRIC CABLE -9791 | 124.6 | 2 | Paron | XLPE+TUBEAL+60ACESNOIR+SKINSC | -- | 35.9 | 26.7 | No | 2019-07-04 | B2_s1_d0 | 0.8 | 3.8 | 8.1 | 696 | 21 | B2 | 9 | 0.01 | s1 | n | n | d0
|  | 890726 | 16I4653 | XGB 1X240 | 25.3 | 7 | Manlleu | TPR-55 | -- | 48 | 48 | No | 2019-07-01 | C_s1_d0 | 1.11 | 19.4 | 47.8 | 1413 | 43.2 | C | 15.5 | 0.06 | s1 | N | N | d0
|  | 890725 | 10J2904 | XGB 1X35 | 11.8 | 13 | Manlleu | TPR-55 | -- | 38 | 31.4 | No | 2019-07-01 | B2_s1_d2 | 1.23 | 14.7 | 21.3 | 1065 | 37.2 | B2 | 2.9 | 0.01 | s1 | Y | Y | d2
|  |  |  | FO DROP 1MM 20D01 | 2 | 325 | Manlleu |  | -- | 32 | 31.3 | No | 2019-07-01 | C_s1_d1 | 1.53 | 19.8 | 38.9 | 786 | 89.3 | C | 13 | 0.04 | s1 | Y | N | d1
|  | 82979510 | 549133J | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.8 | 14 | Manlleu |  | -- | 41 | 30.6 | No | 2019-07-02 | D_s1_d2 | 2.41 | 48.2 | 67.1 | 927 | 112.7 | D | 29.1 | 0.08 | s1 | Y | Y | d2
|  |  | 546960X | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.4 | 15 | Manlleu |  | -- | 42 | 27.2 | No | 2019-07-02 | D_s1_d1 | 1.85 | 32.5 | 45 | 1206 | 66.9 | D | 23.6 | 0.04 | s1 | Y | N | d1
|  |  | 545245H | EXZHELLENT RZ1-K (AS) 1KV 3G1.5 | 10.4 | 15 | Manlleu |  | -- | 44 | 28.7 | No | 2019-07-02 | C_s1_d1 | 1.33 | 23.7 | 35.9 | 963 | 63 | C | 17.9 | 0.03 | s1 | Y | N | d1
|  | 996950 | 14J7116 | HEPRZ1 (AS) 1X50MM2 12/20KV | 31.1 | 6 | Manlleu | REPLLÈBEIG | -- | 41 | 29.6 | No | 2019-07-04 | D_s1_d1 | 2.05 | 42.3 | 60.3 | 1497 | 71.9 | D | 2.7 | 0.02 | s1 | y | n | d1
|  | 996950 | 14J7116 | HEPRZ1 (AS) 1X50MM2 12/20KV | 30.5 | 6 | Manlleu | REPLÈNEGRO | -- | 46 | 27.3 | No | 2019-07-04 | C_s1_d2 | 1.18 | 23.9 | 36 | 1497 | 51.5 | C | 21.1 | 0.05 | s1 | y | y | d2
19070006 |  |  |  | PRYSMIAN 255/2019-1*2500 CU-320 000V ELECTRIC CABLE -9727 | 124.6 | 2 | Paron | XLPE+TUBEAL+60ACESNOIR+SKINSC | -- | 44.2 | 25.2 | No | 2019-07-05 | B2_s1_d0 | 0.7 | 5.1 | 9 | 729 | 25 | B2 | 9 | 0.02 | s1 | n | n | d0
19070008 |  | 17916 |  | 750-5G2.5-SH-NF F 55-625-255 | 16 | 9 | Paron | IX1400FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 40.2 | 22.5 | No | 2019-07-09 | B2_s1_d1 | 0.45 | 3.3 | 6.4 | 1329 | 15 | B2 | 5 | 0.01 | s1 | y | n | d1
19070007 |  | 17916 |  | 750-7G2.5-SH-NF F 55-625-255 | 17.6 | 8 | Paron | ID3100/SV3300FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 39.9 | 22.5 | No | 2019-07-09 | B2_s1_d2 | 0.6 | 10.1 | 18.8 | 1239 | 24 | B2 | 14 | 0.03 | s1 | y | y | d2
19070009 |  | 17916 |  | 750-5G1.5-SH-NF F 55-625-255 | 15 | 10 | Paron | ID3100/SV3300FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 35.2 | 23.4 | No | 2019-07-09 | B2_s1_d2 | 0.7 | 8.7 | 15.6 | 1086 | 25 | B2 | 23 | 0.06 | s1 | y | y | d2
TN_2019_1575 |  |  | 5096933 | CABLES RCT ARA-Z1 RZ1-K (AS) 0.6/1KV 5G1.5 | 12.11 | 13 | Vilanova | COMPETITORSAMPLE | CD | 54.4 | 24.6 | No | 2019-07-04 | E ou F_s2_d2 | 3.3 | 90.8 | 240.6 | 1410 | 220.5 | E ou F | 160.7 | 0.82 | s2 | n | y | d2
TN_2019_1576 |  |  |  | CABLES RCT H07Z1-K TYPE 2 1X2.5 | 3.57 | 105 | Vilanova | COMPETITORSAMPLE | CD | 49.9 | 27.6 | No | 2019-07-04 | B2_s1_d1 | 0.88 | 8.4 | 20 | 627 | 63.9 | B2 | 38.1 | 0.13 | s1 | y | n | d1
TN_2019_1577 |  |  |  | CABLES RCT H07Z1-K TYPE 2 1X1.5 | 2.93 | 165 | Vilanova | COMPETITORSAMPLE | CD | 52.7 | 28.3 | No | 2019-07-04 | C_s1_d0 | 1.84 | 14.3 | 29.4 | 813 | 81.2 | C | 45.5 | 0.09 | s1 | n | n | d0
TN_2019_1578 |  |  |  | CABLES RCT ARA-Z1 RZ1-K (AS) 0.6/1KV 1X240 | 29.01 | 6 | Vilanova | COMPETITORSAMPLE | CD | 53.5 | 28.9 | No | 2019-07-04 | B2_s1_d2 | 0.56 | 4.8 | 12.8 | 1482 | 29.2 | B2 | 8.3 | 0.01 | s1 | n | y | d2
TN_2019_1579 |  |  | 083117K | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 1X240MM² | 27.23 | 6 | Vilanova | COMPETITORSAMPLE | CD | 51.6 | 29.3 | No | 2019-07-04 | C_s1_d2 | 0.78 | 12.7 | 37.3 | 1500 | 31.2 | C | 9.2 | 0.03 | s1 | n | y | d2
TN_2019_1580 |  |  | 524460R | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.66 | 8 | Vilanova | COPPERTAPE50%+MICA+LANTOR+1602 | CD | 72.6 | 26 | No | 2019-07-08 | D_s1_d2 | 1.59 | 30.5 | 78.3 | 1461 | 70.5 | D | 30.3 | 0.1 | s1 | n | y | d2
TN_2019_1581 |  |  |  | MIGUELEZ AFIRENAS H07Z1-K 1X1.5MM2 | 3.06 | 150 | Vilanova | COMPETITORSAMPLE | CD | 66.1 | 27.4 | No | 2019-07-08 | C_s2_d1 | 1.67 | 14.5 | 28.2 | 786 | 76 | C | 72.7 | 0.19 | s2 | y | n | d1
TN_2019_1582 |  |  |  | MIGUELEZ AFIRENAS H07Z1-K 1X2.5MM2 | 3.59 | 105 | Vilanova | COMPETITORSAMPLE | CD | 74 | 26.6 | No | 2019-07-08 | C_s1_d1 | 1.61 | 11.4 | 28.9 | 660 | 82.3 | C | 18.1 | 0.09 | s1 | y | n | d1
TN_2019_1584 |  |  |  | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 1X16 MM² | 9.6 | 15 | Vilanova | COMPETITORSAMPLE | CD | 58.9 | 22.5 | No | 2019-07-10 | D_s1_d0 | 2.05 | 20.3 | 27.7 | 1056 | 45.8 | D | 36.4 | 0.07 | s1 | n | n | d0
|  | 410325 |  | HEPRZ1 12/20 1X240AL | 40.3 | 5 | Manlleu | SMC01+GOM-14+SMV-05+TPR-49+TPO-03 | -- | 50 | 26.7 | No | 2019-07-04 | C_s1_d1 | 1.08 | 21.2 | 25.5 | 978 | 54.6 | C | 24.9 | 0.07 | s1 | Y | N | d1
|  | 70772 | 530641J | ROZ1MZ1 500V 24X2X0.5 2RH | 28.8 | 6 | Manlleu | GFR380+GFR380 | -- | 41 | 30.7 | No | 2019-07-08 | B2_s1_d0 | 0.35 | 14.9 | 16.2 | 567 | 88.8 | B2 | 1.3 | 0 | s1 | N | N | d0
|  | 70771 | 498703U | ROZ1MZ1 500V 12X2X1.5 2RH | 28 | 6 | Manlleu | GFR380+GFR380 | -- | 46 | 28.5 | No | 2019-07-08 | B2_s1_d0 | 0.48 | 7.4 | 9.2 | 1338 | 39.6 | B2 | 5.9 | 0.01 | s1 | N | N | d0
|  | 70770 | 530586Z | ROZ1MZ1 500V 1X2X1.5 2RH | 11.9 | 13 | Manlleu | GFR380+GFR380 | -- | 42 | 29.2 | No | 2019-07-08 | B2_s1_d0 | 0.37 | 11.3 | 16.1 | 792 | 89.9 | B2 | 4.7 | 0.01 | s1 | N | N | d0
|  | 70775 | 524433L | RHOZ1MZ1 500V 6X3X1.5 2RH | 25.8 | 6 | Manlleu | GFR380+GFR380 | -- | 50 | 26.5 | No | 2019-07-09 | C_s1_d0 | 0.4 | 18.8 | 25.1 | 1500 | 104.5 | C | 0 | 0 | s1 | N | N | d0
|  | 70774 | 530588B | RHOZ1MZ1 500V 2X2X1.5 2RH | 25.5 | 9 | Manlleu | GFR380+GFR380 | -- | 54 | 25.5 | No | 2019-07-09 | C_s1_d0 | 0.41 | 17.3 | 19.2 | 1128 | 74.5 | C | 1.4 | 0 | s1 | N | N | d0
|  | 275258 | 06N1850 | RZ1-K (AS) 1KV 3G2.5 | 10.3 | 15 | Manlleu | PRS-03+TPR-45+TPR-49+TPR-54 | -- | 40 | 29.4 | No | 2019-07-10 | C_s2_d0 | 0.76 | 21.3 | 41.9 | 756 | 95.5 | C | 25.6 | 0.7 | s2 | N | N | d0
|  | 705725 |  | H07Z1-K (AS) 1X1.5 | 3.52 | 120 | Manlleu | TPR-52+TPR-53 | -- | 44 | 26.9 | No | 2019-07-10 | C_s1_d2 | 1.96 | 26.8 | 45.8 | 735 | 112.3 | C | 22.3 | 0.05 | s1 | Y | Y | d2
19070011 |  | 17911 | CEC2019-031 | CÂBLE L1081-1 (FO) | 2 | 375 | Paron | 5200SMIT+1700SEES | -- | 50.7 | 23.4 | No | 2019-07-13 | B2_s1_d0 | 1.3 | 11.2 | 25.6 | 747 | 89 | B2 | 16 | 0.04 | s1 | n | n | d0
19070010 |  | 17924 | CEC 2019-033 | RISER @ 72FO | 10.5 | 14 | Paron | SANTOPRENE+TPR249 | -- | 46.9 | 24.7 | No | 2019-07-13 | B2_s1_d0 | 1 | 8.5 | 16.9 | 507 | 86 | B2 | 33 | 0.09 | s1 | n | n | d0
|  | 704816 | 12T4643 | RZ1-K (AS) 1KV 1X240 | 26 | 6 | Manlleu | PRS-03+TPR-54 | -- | 40 | 28.5 | No | 2019-07-11 | C_s1_d1 | 0.74 | 19.3 | 42.3 | 1500 | 35.2 | C | 1.7 | 0.01 | s1 | Y | N | d1
|  | 275325 | 06N1716 | RZ1-K (AS) 1KV 5G2.5 | 12.4 | 13 | Manlleu | PRS-03+TPR-45+TPR-28+TPR-49+TPR-54 | -- | 47 | 26.1 | No | 2019-07-11 | D_s1_d2 | 2.04 | 38.3 | 56.9 | 1494 | 73.7 | D | 5.4 | 0.02 | s1 | Y | Y | d2
|  | 72582 | 550507C | KX-ROZ1MZ1 500V 1X2X1.3 2RH | 12 | 13 | Manlleu | XLPE+GFR380+ARMAT+GFR380 | -- | 44 | 27 | No | 2019-07-11 | D_s1_d2 | 1.06 | 37.4 | 50.7 | 882 | 158.3 | D | 10.3 | 0.03 | s1 | Y | Y | d2
|  | 996950 | 14J7116 | HEPRZ1 (AS) 1X50 | 30.9 | 6 | Manlleu |  | -- | 34 | 29.2 | No | 2019-07-11 | D_s1_d2 | 1.27 | 43 | 51.4 | 1500 | 109.4 | D | 21.4 | 0.07 | s1 | Y | Y | d2
|  | 43556 | 557691L | CCTSST FR03 4X1.4 | 16.1 | 9 | Manlleu | TPR-55 | -- | 45 | 25.7 | No | 2019-07-17 | B2_s1_d2 | 0.46 | 8.6 | 11 | 1143 | 32.3 | B2 | 8 | 0.02 | s1 | y | y | d2
|  | 43556 | 544582M | CCTSST FR03 5X4X1.4 | 28.1 | 6 | Manlleu | TPR-55 | -- | 45 | 25.7 | No | 2019-07-17 | B2_s1_d1 | 0.39 | 7.4 | 9.2 | 1497 | 30.2 | B2 | 3 | 0.01 | s1 | y | n | d1
19070012 |  | 17922 | -- | CEI 332-GENERAL CABLE 6 SILEC CEI 60840-RTE-1600AL PR11.6AL 52/90 (100KV) -C18X-CSC ( YPAREX) | 91.5 | 2 | Paron | XLPE+TUBEAL+6000SEES+SKINSC | -- | 41.5 | 22.1 | No | 2019-07-16 | B2_s1_d2 | 0.7 | 6.1 | 7.2 | 1488 | 21.2 | B2 | 3.1 | 0.01 | s1 | y | y | d2
19070013 |  | 17922 | -- | CEI 332-GENERAL CABLE 6 SILEC CEI 60840-RTE-1600AL PR11.6AL 52/90 (100KV) -C18X-CSC ( LUCALEN) | 91.5 | 2 | Paron | XLPE+TUBEAL+6000SEES+SKINSC | -- | 49.2 | 21.9 | No | 2019-07-16 | B2_s1_d2 | 0.8 | 9.1 | 16.1 | 1494 | 24.5 | B2 | 7 | 0.01 | s1 | y | y | d2
19070014 |  | 17922 | -- | TERNA 1X2500 AL-XLPE-20-AL-320/340 KV DC ( YPAREX) | 126 | 2 | Paron | XLPE+TUBEAL+6000SEES+SKINSC | -- | 48.2 | 22.4 | No | 2019-07-16 | B2_s1_d2 | 1 | 5.3 | 8.6 | 807 | 23.3 | B2 | 8.3 | 0.01 | s1 | y | y | d2
19070015 |  | 17922 | -- | TERNA 1X2500 AL-XLPE-20-AL-320/340 KV DC ( LUCALEN) | 127.5 | 2 | Paron | XLPE+TUBEAL+6000SEES+SKINSC | -- | 44.2 | 23.4 | No | 2019-07-16 | B2_s1_d2 | 1.1 | 11 | 18 | 1380 | 35.3 | B2 | 10.4 | 0.02 | s1 | y | y | d2
|  | 72556 | 561972P | AL-AFUMEX RZ1F3Z1 3KV 3X16 | 29 | 6 | Manlleu | XLPE+GFR380+LANTOR+GFR380 | -- | 46 | 25.1 | No | 2019-07-17 | B2_s1_d0 | 0.36 | 7.3 | 8.5 | 525 | 49.2 | B2 | 4.7 | 0.02 | s1 | N | N | d0
|  | 72556 | 561981Z | AL-AFUMEX RZ1F3Z1 3KV 3X16 | 28.8 | 6 | Manlleu | XLPE+GFR380+GFR380 | -- | 46 | 25 | No | 2019-07-17 | B2_s1_d1 | 0.41 | 8.1 | 9.3 | 1122 | 49.2 | B2 | 8.6 | 0.03 | s1 | Y | N | d1
|  | 72557 | 561982A | AL-AFUMEX RZ1F3Z1 3KV 3X25 | 32.5 | 6 | Manlleu | XLPE+GFR380+LANTOR+GFR380 | -- | 37 | 29 | No | 2019-07-17 | B2_s1_d0 | 0.58 | 9.5 | 10.4 | 585 | 46.6 | B2 | 8.8 | 0.04 | s1 | n | n | d0
|  | 72557 | 561983B | AL-AFUMEX RZ1F3Z1 3KV 3X25 | 32.1 | 6 | Manlleu | XLPE+GFR380+GFR380 | -- | 40 | 27.2 | No | 2019-07-17 | B2_s1_d1 | 0.53 | 10.8 | 13.5 | 1056 | 53.3 | B2 | 3.1 | 0.03 | s1 | y | n | d1
|  | 71990 | 550267S | DZ1 ADIF B2CA 3.6/6 1X300AL | 30.4 | 6 | Manlleu | AL+IRN267+6001.8MM | -- | 53 | 23 | No | 2019-07-18 | _ _d2 | 3.3 | [8 empty] | Y | Y | d2
|  | 71850 | 556171B | DZ1 ADIF B2CA 3.6/6 1X150AL | 27.3 | 6 | Manlleu | AL+IRN267+14201.5MM+6001.4MM | -- | 60 | 26.6 | No | 2019-07-18 | D_s3_d2 | 2.31 | 47.7 | 97.1 | 1479 | 82.7 | D | 0.11 | 29.3 | s3 | Y | Y | d2
|  | 71989 | 556143D | DZ1 ADIF DCA 3.6/6 1X400AL | 34.9 | 5 | Manlleu | AL+IRN267+14200.5MM+6001.9MM | -- | 58 | 25.9 | No | 2019-07-18 | C_s2_d2 | 1.21 | 21.6 | 38.2 | 873 | 79.9 | C | 53.6 | 0.21 | s2 | Y | Y | d2
19070018 |  | 17935 | -- | 750-7G2.5-SH-NF F 55-625-255 | 17.6 | 8 | Paron | IX1400FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 49.2 | 25.4 | No | 2019-07-18 | B2_s1_d0 | 0.6 | 4.1 | 7.8 | 1497 | 19 | B2 | 7 | 0.02 | s1 | n | n | d0
1907016 |  | 17935 | -- | 750-5G1.5-SH-NF F 55-625-255 | 14.6 | 10 | Paron | IX1400FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 49.2 | 24.4 | No | 2019-07-18 | B2_s1_d2 | 0.6 | 7.4 | 9.7 | 1224 | 31 | B2 | 7 | 0.02 | s1 | y | y | d2
1907017 |  | 17935 | -- | 750-5G1.5-SH-NF F 55-625-255 | 14.6 | 10 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 36.5 | 24.3 | No | 2019-07-18 | B2_s1_d1 | 0.7 | 9.4 | 16.8 | 1179 | 27 | B2 | 10 | 0.02 | s1 | y | n | d1
|  | 71759 | 556204V | DZ1 ADIF B2CA 3.6/6 BED1.5 + DMZ2 1X150CU | 24.8 | 7 | Manlleu | IRN267+1420FEES1.5MM+6000SEES1.5MM | -- | 48 | 28.1 | No | 2019-07-18 | D_s1_d2 | 2.31 | 38.3 | 128.1 | 1473 | 109.2 | D | 37.1 | 0.13 | s1 | Y | Y | d2
19070019 |  | 17935 | DBM171259 | 750-5G2.5-SH-NF F 55-625-255 | 14 | 11 | Paron | IX4800FR+0400FEIT+5300SEIT | -- | 59.2 | 25.1 | No | 2019-07-19 | B2_s1_d0 | 0.7 | 8.2 | 10.7 | 1452 | 21 | B2 | 8 | 0.02 | s1 | n | n | d0
19070020 |  | 17935 | DBM115780 | 750-5G2.5-SH-NF F 55-625-255 | 14 | 11 | Paron | IX4800FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 56.2 | 25.2 | No | 2019-07-19 | B2_s1_d2 | 0.6 | 6 | 7.5 | 1296 | 17 | B2 | 5 | 0.01 | s1 | y | y | d2
19070021 |  | 17825 | 9719 | PRYSMIAN 255/2019-1*2500 AL-320 000V ELECTRIC CABLE -9719 | 124.2 | 2 | Paron | XLPE+TUBEAL+60ACESNOIR+SKINSC | -- | 52.6 | 24.8 | No | 2019-07-20 | B2_s1_d0 | 0.75 | 6.8 | 13.1 | 705 | 33 | B2 | 6 | 0.01 | s1 | n | n | d0
19070022 |  | 17935 | -- | 750-7G2.5-SH-NF F 55-625-255 | 17.6 | 8 | Paron | IX1400FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 53.6 | 24 | No | 2019-07-20 | B2_s1_d0 | 0.5 | 3.9 | 5.9 | 657 | 20 | B2 | 2 | 0.01 | s1 | n | n | d0
19070023 |  | 17945 | -- | FR-N1X1G1 5G1.5MM² | 13 | 12 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 51.6 | 25 | No | 2019-07-20 | B2_s1_d2 | 0.9 | 10.2 | 17.6 | 1200 | 28 | B2 | 15 | 0.03 | s1 | y | y | d2
|  | 997097 |  | FG17 450/750 1X1.5 | 2.9 | 165 | Manlleu | FPS166 | - | 44 | 26 | No | 2019-07-22 | D_s1_d1 | 3.3 | 67.3 | 114.9 | 1110 | 158.9 | D | 48.6 | 0.11 | s1 | Y | N | d1
|  | 71759 | 556115Y | DZ1 ADIF B2CA 3.6/6 BED 1.5 + DMZ2 1X150 | 25.8 | 6 | Manlleu | IRN267+14201.5MM+6001.5MM | - | 42 | 27 | No | 2019-07-22 | _ _d2 | 3.3 | [8 empty] | Y | Y | d2
|  | 71851 | 556114X | DZ1 ADIF B2CA 3.6/6 BED 0.5 + DMZ2 1X150 AL | 25.8 | 6 | Manlleu | IRN267+14200.5MM+6001.5MM |  | 38 | 29.1 | No | 2019-07-22 | _ _d2 | 3.3 | [8 empty] | y | y | d2
|  | 71820 | 540868C | RZ1-K (AS) 1KV 1X35 | 13.2 | 12 | Manlleu | XLPE+TPR-54 |  | 35 | 28.7 | No | 2019-07-23 | C_s1_d1 | 1.32 | 20.8 | 29.6 | 138.6 | 38.7 | C | 17.7 | 0.04 | s1 | Y | N | d1
|  | 72727 | 560695B | RZ1-K (AS) 1KV 1X4 | 8.3 | 19 | Manlleu | XLPE+TPR-55.PRESIÓN2MM |  | 39 | 27.8 | No | 2019-07-23 | D_s1_d0 | 2.14 | 27.6 | 33.5 | 939 | 68.9 | D | 34.4 | 0.05 | s1 | n | n | d0
|  | 72727 | 560705M | RZ1-K (AS) 1KV 1X4 | 8.7 | 17 | Manlleu | XLPE+TPR-55.PRESIÓN6MM |  | 40 | 28.2 | No | 2019-07-23 | B2_s1_d0 | 1.06 | 10.7 | 17.3 | 654 | 57.9 | B2 | 14.4 | 0.05 | s1 | n | n | d0
TN_2019_1585 |  |  |  | TOP CABLE TOXFREE ZH H07Z1-K (AS) TYPE 2 1X2.5 | 3.55 | 105 | Vilanova | COMPETITORSAMPLE | CD | 53.9 | 23.6 | No | 2019-07-10 | C_s1_d1 | 1.47 | 14.5 | 33.8 | 621 | 106.3 | C | 36.3 | 0.13 | s1 | y | n | d1
TN_2019_1586 |  |  |  | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 5G1.5MM2 | 12.46 | 13 | Vilanova | COMPETITORSAMPLE | CD | 49.2 | 25.6 | No | 2019-07-11 | D_s2_d2 | 3.3 | 49.9 | 151.2 | 1500 | 126 | D | 71.7 | 0.15 | s2 | n | y | d2
TN_2019_1587 |  |  |  | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G1.5MM2 | 9.65 | 15 | Vilanova | COMPETITORSAMPLE | CD | 43.6 | 28 | No | 2019-07-10 | D_s2_d2 | 3.3 | 55.1 | 155.8 | 1500 | 130.1 | D | 106.2 | 0.38 | s2 | n | y | d2
TN_2019_1588 |  |  |  | TOP CABLE TOXFREE ZH H07Z1-K (AS) TYPE 2 1X1.5 | 2.94 | 165 | Vilanova | COMPETITORSAMPLE | CD | 43 | 29.2 | No | 2019-07-10 | C_s1_d1 | 1.71 | 17.3 | 32.6 | 804 | 97.3 | C | 37.6 | 0.11 | s1 | y | n | d1
TN_2019_1589 |  |  | 524460R | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.66 | 8 | Vilanova | COPPERTAPE50%+MICA+LANTOR+1602 | CD | 72.2 | 23.6 | No | 2019-07-11 | D_s1_d2 | 1.6 | 27.3 | 74 | 1500 | 62.9 | D | 33.3 | 0.1 | s1 | n | y | d2
TN_2019_1590 |  |  | T1-E78440 | FG16M16 AFUMEX 1000 PLUS 0.6/1KV 1X400 | 36.08 | 5 | Vilanova | ID2900IT+0400FEIT+5300SEIT | CD | 68 | 24.5 | No | 2019-07-11 | B2_s1_d0 | 0.3 | 2.4 | 4.3 | 672 | 13.7 | B2 | 0 | 0 | s1 | n | n | d0
TN_2019_1591 |  |  | 423059X | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.92 | 3 | Vilanova |  | CD | 70.2 | 26.6 | No | 2019-07-11 | C_s1_d2 | 0.92 | 19.7 | 35.6 | 1500 | 42.5 | C | 7.2 | 0.01 | s1 | n | y | d2
TN_2019_1592 |  |  | T1-E78440 | FG16M16 AFUMEX 1000 PLUS 0.6/1KV 1X400 | 36.08 | 5 | Vilanova | ID2900IT+0400FEIT+5300SEIT | CD | 68.2 | 28.1 | No | 2019-07-11 | B2_s1_d0 | 0.53 | 2.6 | 4.8 | 519 | 15.5 | B2 | 0.9 | 0 | s1 | n | n | d0
TN_2019_1593 |  |  | 249410Y | NEXANS AL SECURE RZ1-K (AS) 1KV 1X240 | 28.48 | 6 | Vilanova | COMPETITORSAMPLE | CD | 68.8 | 24.3 | No | 2019-07-14 | C_s1_d2 | 0.66 | 16.5 | 39.4 | 1494 | 33.6 | C | 6.8 | 0.02 | s1 | n | y | d2
TN_2019_1594 |  |  | 5096946 | TOP CABLE TOXFREE ZH C RZ1-K (AS) 1KV 5G1.5 | 12.61 | 12 | Vilanova | COMPETITORSAMPLE | CD | 66.8 | 24.9 | No | 2019-07-14 | C_s1_d0 | 1.27 | 17.4 | 25.3 | 918 | 49.3 | C | 14.6 | 0.03 | s1 | n | n | d0
TN_2019_1595 |  |  | 722997 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 1X240 | 26.88 | 6 | Vilanova | COMPETITORSAMPLE | CD | 49.1 | 27.3 | No | 2019-07-14 | B2_s1_d0 | 0.42 | 5.3 | 10.5 | 1500 | 27.7 | B2 | 1.7 | 0 | s1 | n | n | d0
TN_2019_1596 |  |  |  | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 1X16 | 10.63 | 14 | Vilanova | COMPETITORSAMPLE | CD | 51.2 | 27.6 | No | 2019-07-14 | B2_s1_d0 | 0.86 | 13.7 | 27.2 | 852 | 52.9 | B2 | 16.2 | 0.04 | s1 | n | n | d0
TN_2019_1601 |  |  |  | AFUMEX CLASS 750V HO7Z1-K (AS) TYPE2 1X4 | 4.03 | 90 | Vilanova |  | CD | 57.1 | 24.5 | No | 2019-07-22 | B2_s1_d0 | 0.84 | 5.7 | 15.3 | 639 | 48.3 | B2 | 17.3 | 0.03 | s1 | n | n | d0
TN_2019_1602 |  |  | ACP 01519733 | 5G2.5 CU 750 NR | 16.19 | 9 | Vilanova | INSULATIONID3100FR+SV3300FR+SCAPATAPEONTHELAY+BEDDING0400FEIT+OUTERSHEATH5300SEIT | CD | 59.1 | 26.7 | No | 2019-07-22 | B2_s1_d1 | 0.59 | 5 | 10.4 | 1500 | 19 | B2 | 7 | 0.01 | s1 | y | n | d1
TN_2019_1603 |  |  | ACP 01519736 | 7G2.5 CU 750 NR | 17.59 | 8 | Vilanova | INSULATIONID3100FR+SV3300FR+SCAPATAPEONTHELAY+BEDDING0400FEIT+OUTERSHEATH5300SEIT | CD | 54.1 | 28 | No | 2019-07-22 | C_s1_d2 | 0.56 | 17 | 24.7 | 1500 | 36.6 | C | 12.8 | 0.03 | s1 | n | y | d2
TN_2019_1604 |  | OP71199 20293469 | 528855T | RZ1C4OZ1-K 1KV VFD CLASS 3X240+3G50MM² | 62.64 | 3 | Vilanova | XLPE+INTERNALSHEATH1602SEES+COPPERTAPE+AL/POTAPE+LANTORLONGITUDINALTAPE+SHEATH1602SEES | CD | 52.3 | 28.1 | No | 2019-07-23 | B2_s1_d0 | 0.55 | 3.3 | 5.8 | 1188 | 13.5 | B2 | 3 | 0.01 | s1 | n | n | d0
TN_2019_1605 |  | OP71198 20293459 | 533601B | RZ1C4OZ1-K 1KV VFD CLASS 3X2.5+3G0.75MM² | 15.13 | 10 | Vilanova | XLPE+INTERNALSHEATH1602SEES+COPPERTAPE+AL/POTAPE+LANTORLONGITUDINALTAPE+SHEATH1602SEES | CD | 53 | 29.7 | No | 2019-07-23 | C_s1_d0 | 0.92 | 16.1 | 34.5 | 993 | 49.9 | C | 33.5 | 0.06 | s1 | n | n | d0
TN_2019_1606 |  |  | 529884L | RED ELEC RHZ1 RA 2OL (AS) 1X1200 MM2 127/220KV AL +H250 | 103.48 | 2 | Vilanova | XLPE+ALFOIL+60ACESNOIR+SKINSC | CD | 43.5 | 31.2 | No | 2019-07-23 | B2_s1_d2 | 0.85 | 10.4 | 20.5 | 1443 | 32.8 | B2 | 8.4 | 0.01 | s1 | n | y | d2
19070025 |  | 17935 | -- | 750-5G1.5-SH-NF F 55-625-255 | 14.6 | 10 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 48.1 | 26.1 | No | 2019-07-23 | B2_s1_d1 | 0.7 | 7.6 | 11.3 | 1167 | 22 | B2 | 10 | 0.02 | s1 | y | n | d1
19070024 |  | 17935 | -- | 750-5G1.5-SH-NF F 55-625-255 | 14.6 | 10 | Paron | IX1400FR+RUBANSCAPARUBANNÉ+0400FEIT+5300SEIT | -- | 45.2 | 25.3 | No | 2019-07-23 | B2_s1_d2 | 0.7 | 10.3 | 19.9 | 1212 | 27 | B2 | 13 | 0.03 | s1 | y | y | d2
179070026 |  | 17946 | -- | K25 750V 1X6.0 -SH-NF F 55-625-255 ( IRRADIÉ) | 5.3 | 30 | Paron | 1602SEES | -- | 44.4 | 27.1 | No | 2019-07-24 | D_s1_d2 | 2.05 | 10.8 | 39.2 | 579 | 156 | D | 25 | 0.09 | s1 | y | y | d2
|  | 71852 | 556144E | DZ1 ADIF B2CA 3.6/6 BED 1.5 + DMZ2 1X150 | 26.6 | 6 | Manlleu | IRN267+14201.5MM+6001.5MM | -- | 31 | 29.1 | No | 2019-07-23 | E ou F_s1_d2 | 3.3 | 74.1 | 178.7 | 1425 | 159.3 | E ou F | 40.2 | 0.24 | s1 | y | y | d2
|  | 72560 | 574642N | AL-AFUMEX RZ1F3Z1 3KV 3X16 | 29 | 6 | Manlleu | XLPE+TPR55+LANTOR+TPR55 | -- | 42 | 27 | No | 2019-07-24 | B2_s1_d1 | 0.38 | 5.1 | 8.3 | 681 | 27.8 | B2 | 10.7 | 0.05 | s1 | y | n | d1
|  | 72561 | 547632C | AL-AFUMEX RZ1F3Z1 3KV 3X25 | 32 | 6 | Manlleu | XLPE+TPR55+LANTOR+TPR55 | -- | 43 | 24 | No | 2019-07-24 | B2_s1_d1 | 0.43 | 5.7 | 8 | 741 | 23.7 | B2 | 9.3 | 0.02 | s1 | y | n | d1
TN_2019_1607 |  | 83146553 | 561993M | BLINDEX Z1C4Z1-K 1KV (AS) 3X95 | 38.71 | 5 | Vilanova |  | CD | 71.8 | 25.7 | No | 2019-07-24 | B2_s1_d2 | 0.74 | 10.5 | 14.8 | 1047 | 32.9 | B2 | 5.4 | 0.02 | s1 | n | y | d2
|  | 72558 | 546670G | AL-AFUMEX RZ1F3Z1 3KV 3X16 | 28.9 | 6 | Manlleu | XLPE+5300SEIT+LANTOR+5300SEIT | -- | 40 | 27.5 | No | 2019-07-24 | B2_s1_d2 | 0.76 | 9.7 | 15.2 | 1362 | 26.4 | B2 | 3.2 | 0.01 | s1 | Y | Y | d2
|  | 72558 | 547647U | AL-AFUMEX RZ1F3Z1 3KV 3X16 | 29.7 | 6 | Manlleu | XLPE+5300SEIT+5300SEIT | -- | 33 | 30 | No | 2019-07-24 | B2_s1_d2 | 0.74 | 12.1 | 17.4 | 1479 | 27.4 | B2 | 4 | 0.01 | s1 | Y | Y | d2
|  | 72559 | 546669F | AL-AFUMEX RZ1F3Z1 3KV 3X25 | 32.5 | 6 | Manlleu | XLPE+5300SEIT+5300SEIT | -- | 39 | 29 | No | 2019-07-24 | B2_s1_d2 | 0.72 | 12.4 | 17.5 | 1296 | 26.7 | B2 | 3.7 | 0.01 | s1 | Y | Y | d2
TN_2019_1610 |  |  | T7-I31471 | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11.93 | 13 | Vilanova | 1420+1500 | CD | 66.8 | 24.5 | No | 2019-07-25 | D_s1_d2 | 3 | 43.2 | 71.5 | 1338 | 78.6 | D | 40.8 | 0.1 | s1 | n | y | d2
TN_2019_1611 |  | 20094105 OP8309026 | 553462P | RZ1F3Z1-K (AS) 0.6/1KV 2X2.5MM² + 2FO | 16.1 | 9 | Vilanova | XLPE+1602SEES+2FOOPSYTUB+TAPESTEELSNCORRUGATED+1602SEES | CD | 67.7 | 26.9 | No | 2019-07-25 | C_s1_d2 | 1.03 | 25.6 | 33.7 | 1359 | 51.2 | C | 28.6 | 0.06 | s1 | n | y | d2
TN_2019_1611 |  | 20094105 OP8309026 | 553462P | RZ1F3Z1-K (AS) 0.6/1KV 2X2.5MM² + 2FO | 16.1 | 9 | CEIS | XLPE+1602SEES+2FOOPSYTUB+TAPESTEELSNCORRUGATED+1602SEES | -- | 48 | 25.5 | No | 2019-09-20 | C_s1_d2 | 0.8 | 17.4 | 20.7 | 1206 | 48.1 | C | 17.9 | 0.04 | s1 | n | y | d2
TN_2019_1612 |  |  |  | AENOR USE HAR 336 NX HO7Z1-K TYPE 2 (AS) 2019 1X2.5 | 3.55 | 105 | Vilanova | COMPETITORSAMPLE | CD | 66.3 | 28.1 | No | 2019-07-25 | B2_s1_d1 | 1.11 | 6.9 | 21.3 | 732 | 62.5 | B2 | 37 | 0.13 | s1 | y | n | d1
|  | 72559 | 547643P | AL-AFUMEX RZ1F3Z1 3KV 3X25 | 32.1 | 6 | Manlleu | 5300SEIT+LANTOR+5300SEIT |  | 43 | 25 | No | 2019-07-26 | B2_s1_d2 | 0.58 | 7.8 | 9.7 | 1482 | 25.7 | B2 | 0 | 0.01 | s1 | Y | Y | d2
|  | 996409B | 12T5797 | RZ1-K (AS) 1KV 5G1.5 | 12.3 | 13 | Manlleu | 1420FEES+TPR-54 |  | 43 | 26.5 | No | 2019-07-26 | D_s1_d2 | 2.31 | 35.1 | 54.8 | 1491 | 67.4 | D | 27.7 | 0.05 | s1 | Y | Y | d2
|  | 996521A | 12S6141 | RZ1-K (AS) 1KV 3G1.5 | 9.4 | 17 | Manlleu | TPR-49+TPR-54 |  | 35 | 28.3 | No | 2019-07-26 | D_s2_d2 | 3.3 | 47.3 | 61.7 | 1290 | 89.4 | D | 59.1 | 0.1 | s2 | Y | Y | d2
|  | 996409D | 12T7532 | RZ1-K (AS) 1KV 5G1.5 | 12.3 | 13 | Manlleu | 0400FEIT+TPR-54 |  | 30 | 30.2 | No | 2019-07-26 | B2_s1_d0 | 0.68 | 13.2 | 22.5 | 1080 | 36.4 | B2 | 9.8 | 0.03 | s1 | N | N | d0
TN_2019_1613 |  |  | T8-G67892 | AFUMEX CLASS RZ1-K (AS) 1KV 3X25 | 21.78 | 7 | Vilanova | 1420+1500 | CD | 66.1 | 25.6 | No | 2019-07-29 | B2_s1_d2 | 0.73 | 7.6 | 22.9 | 1491 | 19.2 | B2 | 1.6 | 0.02 | s1 | n | y | d2
TN_2019_1614 |  |  |  | FS17 1X1.5 | 2.89 | 165 | Vilanova | 28AKGPIT | CD | 67.3 | 22.3 | No | 2019-07-29 | B2_s2_d0 | 0.9 | 4.1 | 13.1 | 507 | 93.5 | B2 | 228.3 | 0.94 | s2 | n | n | d0
TN_2019_1615 |  |  | T7-I31471 | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11.93 | 13 | Vilanova | 1420+1500 | OD | 65.5 | 22.7 | No | 2019-07-29 | D_s2_d2 | 3.3 | 53.8 | 124.3 | 1497 | 103.9 | D | 50.4 | 0.17 | s2 | n | y | d2
TN_2019_1616 |  |  | Reel nº1 | FG16M16 1X6 MM² - 0.6/1 KV | 9.29 | 17 | Vilanova | 0300FDIT+5300SEIT | CD | 57.2 | 27.5 | No | 2019-07-29 | B2_s1_d2 | 0.72 | 9.4 | 16.3 | 717 | 56.1 | B2 | 25 | 0.04 | s1 | n | y | d2
|  | 996521B | 12I8638 | RZ1-K (AS) 1KV 3G1.5 | 9.2 | 17 | Manlleu | 1420FEES+TPR-54 |  | 41 | 26.8 | No | 2019-07-30 | D_s2_d2 | 3.3 | 58.4 | 107.6 | 1497 | 100.4 | D | 81.2 | 0.28 | s2 | Y | Y | d2
|  | 996409A | 12T7698 | RZ1-K (AS) 1KV 5G1.5 | 12.2 | 13 | Manlleu | TPR-49+TPR-54 |  | 36 | 25.7 | No | 2019-07-30 | D_s1_d0 | 2.23 | 42.6 | 62.7 | 1203 | 74.3 | D | 37.9 | 0.07 | s1 | N | N | d0
|  | 996521C | 12T7293 | RZ1-K (AS) 1KV 3G1.5 | 9.4 | 17 | Manlleu | 0300FEIT+TPR-54 |  | 46 | 26.7 | No | 2019-07-30 | D_s1_d2 | 3 | 53.6 | 75 | 1458 | 96.7 | D | 49.9 | 0.1 | s1 | Y | Y | d2
TN_2019_1617 |  |  |  | FG16R16 1X10MM² - 0.6/1 KV | 8.78 | 17 | Vilanova | INSULATIONSTANDARD+05AM+20AH | CD | 75.7 | 25.2 | No | 2019-07-30 | B2_s2_d1 | 0.65 | 3.7 | 12 | 585 | 44.3 | B2 | 96 | 0.28 | s2 | y | n | d1
TN_2019_1618 |  |  |  | FG16OR16 4G1.5MM² - 0.6/1 KV | 10.54 | 14 | Vilanova | INSULATIONSTANDARD+05AM+20AH | CD | 76 | 25.4 | No | 2019-07-30 | B2_s2_d0 | 1.13 | 10.3 | 27.2 | 627 | 84.8 | B2 | 250.7 | 0.7 | s2 | n | n | d0
TN_2019_1619 |  |  |  | FG16OR16 4G1.5MM² - 0.6/1 KV | 10.75 | 14 | Vilanova | INSULATIONSTANDARD+05AL+20AH | CD | 78.4 | 26.9 | No | 2019-07-30 | B2_s2_d0 | 1.1 | 10.5 | 26.5 | 645 | 79.9 | B2 | 270.3 | 0.76 | s2 | n | n | d0
TN_2019_1620 |  |  |  | FG16OR16 4G1.5MM² - 0.6/1 KV | 10.41 | 15 | Vilanova | INSULATIONSTANDARD+05AK+20AH | CD | 76.3 | 26.6 | No | 2019-07-30 | B2_s2_d0 | 1.18 | 12.3 | 27.1 | 657 | 82.8 | B2 | 242.4 | 0.74 | s2 | n | n | d0
TN_2019_1621 |  |  | Reel nº2 | FG16M16 1X2.5 MM² - 0.6/1 KV | 8.08 | 19 | Vilanova | 0300FDIT+5300SEIT | CD | 65.6 | 28.3 | No | 2019-07-30 | B2_s1_d2 | 0.67 | 6.4 | 14.3 | 558 | 58.4 | B2 | 17.1 | 0.04 | s1 | n | y | d2
TN_2019_1622 |  | 83151986 20301162 | 572663K | AFUMEX RHZ1-RA-OL (AS) DCA-S1B.D2.A1 18_30KV 1X240 | 42.93 | 5 | Vilanova |  | CD | 58.1 | 29.5 | No | 2019-07-30 | B2_s1_d2 | 0.56 | 4.6 | 6.9 | 654 | 20.2 | B2 | 4.5 | 0.01 | s1 | n | y | d2
|  | 996521D | 12T9300 | RZ1-K (AS) 1KV 3G1.5 | 9.5 | 15 | Manlleu | 0400FEIT+TPR-54 |  | 46 | 28.5 | No | 2019-07-30 | B2_s1_d0 | 0.74 | 12 | 21.4 | 780 | 57 | B2 | 17.7 | 0.04 | s1 | N | N | d0
|  | 996409C | 12T8540 | RZ1-K (AS) 1KV 5G1.5 | 12.3 | 13 | Manlleu | 0300FEIT+TPR-54 |  | 44 | 27 | No | 2019-08-01 | B2_s1_d0 | 0.83 | 13.6 | 24.1 | 981 | 38.4 | B2 | 9.2 | 0.02 | s1 | n | n | d0
|  | 72727 | 560705M | RZ1-K (AS) 1KV 1X4 | 8.6 | 17 | Manlleu | XLPE+TPR-55.PRESIÓN6MM |  | 54 | 26.1 | No | 2019-08-01 | C_s1_d0 | 1.76 | 17.8 | 26.4 | 846 | 72.8 | C | 28.4 | 0.07 | s1 | n | n | d0
|  | 72727 | 560695B | RZ1-K (AS) 1KV 1X4 | 8.4 | 19 | Manlleu | XLPE+TPR-55.PRESIÓN2MM |  | 47 | 26.6 | No | 2019-08-01 | D_s1_d0 | 3.05 | 54.8 | 69.7 | 1122 | 111.3 | D | 44.7 | 0.08 | s1 | n | n | d0
|  | 72586 | 559495X | MRHZ1MA1Z-K RH 1X240 | 34.1 | 5 | Manlleu | XLPE+1602SEES+SWA+GFR380 |  | 46 | 26.6 | No | 2019-08-27 | B2_s1_d2 | 0.52 | 6 | 7.5 | 579 | 29.9 | B2 | 0 | 0 | s1 | Y | Y | d2
|  | 72560 | 547644R | AL-AFUMEX RZ1F3Z1 3KV 3X16 | 29.1 | 6 | Manlleu | XLPE+TPR-55+TPR-55 |  | 46 | 26.2 | No | 2019-08-27 | B2_s1_d2 | 0.42 | 5 | 7.4 | 558 | 22.6 | B2 | 2.8 | 0.01 | s1 | Y | Y | d2
|  | 72561 | 547646T | AL-AFUMEX RZ1F3Z1 3KV 3X25 | 31.5 | 6 | Manlleu | XLPE+TPR-55+TPR-55 |  | 47 | 27.5 | No | 2019-08-27 | B2_s1_d2 | 0.58 | 8.7 | 9.7 | 546 | 25.2 | B2 | 9.4 | 0.01 | s1 | y | y | d2
|  | 72554 | 575334N | MRHZ1OZ1MZ-K 1KV 10X2.5 | 27.8 | 6 | Manlleu | XLPE+1602SEES+CINTACU+1602SEES+SWA+GFR380 |  | 47 | 25.5 | No | 2019-08-27 | B2_s1_d2 | 0.48 | 6 | 7.4 | 471 | 32.5 | B2 | 3.5 | 0.01 | s1 | Y | Y | d2
|  | 43556 | 557691L | CCTSST FR03 4X1.4 | 26.4 | 9 | Manlleu |  |  | 47 | 26.4 | No | 2019-08-28 | B2_s1_d2 | 0.51 | 9.2 | 12.9 | 519 | 28.3 | B2 | 8.1 | 0.03 | s1 | Y | Y | d2
19070027 |  | 17962 | -- | 1000-1X70MM²-SH-NF F55-625-255 | 18.4 | 8 | Paron | ???+0400FEIT+5300SEIT | -- | 50.3 | 23.5 | No | 2019-08-29 | B2_s1_d1 | 0.7 | 4.1 | 5.9 | 1497 | 16 | B2 | 2 | 0 | s1 | y | n | d1
|  | 72727 | 580458H | RZ1-K (AS) 0.6/1 1X4 | 26.8 | 7 | Manlleu | XLPE+MEGOLONS670 | -- | 50 | 26.8 | No | 2019-08-29 | D_s2_d2 | 3.3 | 57.2 | 194.9 | 912 | 318 | D | 107.7 | 0.51 | s2 | Y | Y | d2
|  | 72726 | 580459J | RZ1-K (AS) 0.6/1 1X35 | 25.7 | 52 | Manlleu | XLPE+MEGOLONS670 | -- | 52 | 25.7 | No | 2019-08-29 | D_s1_d2 | 2.36 | 34.8 | 69.8 | 807 | 69.8 | D | 33.3 | 0.09 | s1 | y | y | d2
TN_2019_1623 |  | OP83160133 20231837 | 552426N | AL-HEPRZ1(AS) 1X500MM2 26/45KV | 56.41 | 4 | Vilanova | 1420+6000 | CD | 61.2 | 24.3 | No | 2019-08-30 | C_s1_d2 | 1.15 | 22.1 | 37.9 | 1431 | 36.1 | C | 3.4 | 0.01 | s1 | n | y | d2
TN_2019_1624 |  | OP70960 20234939 | 581094Z | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 46.22 | 4 | Vilanova | 14203.27MM+60003.24MM | CD | 79.7 | 24.3 | No | 2019-09-02 | C_s2_d2 | 1.21 | 26.5 | 50 | 1467 | 43.6 | C | 93.6 | 0.11 | s2 | n | y | d2
TN_2019_1625 |  | OP70960 20234939 | 581089U | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 46.56 | 4 | Vilanova | 14203.48MM+60003.00MM | CD | 50.3 | 28.1 | No | 2019-08-30 | C_s1_d2 | 1.26 | 29.8 | 54.6 | 1479 | 49.2 | C | 49.8 | 0.06 | s1 | n | y | d2
TN_2019_1626 |  |  | Reel nº6 | FG16M16 1X4 MM² - 0.6/1 KV | 9.02 | 17 | Vilanova | 0300FDIT+5300SEIT | CD | 58.4 | 26.2 | No | 2019-08-30 | B2_s1_d0 | 0.68 | 5.8 | 14.8 | 651 | 46.5 | B2 | 3.2 | 0.03 | s1 | n | n | d0
TN_2019_1627 |  |  | Reel nº3 | FG16M16 1X1.5 MM² - 0.6/1 KV | 8.02 | 19 | Vilanova | 0300FDIT+5300SEIT | CD | 46 | 30.3 | No | 2019-08-30 | B2_s2_d2 | 0.68 | 6.7 | 14.9 | 555 | 65.5 | B2 | 60.5 | 0.07 | s2 | n | y | d2
TN_2019_1628 |  |  |  | FS17 1X1.5 | 2.89 | 165 | Vilanova | 28AKGPIT | CD | 79.5 | 24.3 | No | 2019-09-02 | B2_s2_d0 | 0.81 | 4.9 | 13.5 | 429 | 109.8 | B2 | 217.2 | 1.02 | s2 | n | n | d0
TN_2019_1629 |  |  | Reel nº5 | FG16M16 1X1.5 MM² - 0.6/1 KV | 6.65 | 21 | Vilanova | 0300FDIT+5300SEIT | CD | 71.7 | 24.6 | No | 2019-09-02 | B2_s1_d1 | 0.79 | 7.2 | 20.5 | 531 | 95.7 | B2 | 44.9 | 0.09 | s1 | y | n | d1
TN_2019_1630 |  |  | Reel nº4 | FG16M16 1X6 MM² - 0.6/1 KV | 8.31 | 19 | Vilanova | 0300FDIT+5300SEIT | CD | 66 | 25.1 | No | 2019-09-02 | B2_s1_d0 | 0.77 | 8.1 | 19.4 | 663 | 55.7 | B2 | 47.8 | 0.12 | s1 | n | n | d0
TN_2019_1631 |  | 83025597 20226053 | 535587K | AFUMEX PANELES HO7ZR (AS) 750V 1X16MM2 | 6.74 | 21 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 58.6 | 26.8 | No | 2019-09-02 | B2_s1_d1 | 0.53 | 1.6 | 7.8 | 495 | 45.2 | B2 | 18.6 | 0.03 | s1 | y | n | d1
TN_2019_1632 |  | OP83084418 20193689 | -- | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.5 | 14 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 60.4 | 21.6 | No | 2019-09-03 | C_s1_d0 | 1.73 | 22.9 | 29.6 | 834 | 56.6 | C | 28.6 | 0.07 | s1 | n | n | d0
TN_2019_1633 |  | OP83021626 20193677 | 570486U | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.03 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 46 | 26.1 | No | 2019-09-03 | E ou F_s2_d2 | 3.3 | 79 | 275.9 | 1467 | 237 | E ou F | 51.2 | 0.19 | s2 | n | y | d2
TN_2019_1635 |  | OP70960 20234939 | 581094Z | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 46.22 | 4 | Vilanova | 14203.27MM+60003.24MM | CD | 55.1 | 23.1 | No | 2019-09-05 | C_s1_d2 | 1.02 | 22.6 | 41.5 | 1497 | 35.1 | C | 3.6 | 0.01 | s1 | n | y | d2
CEL-0895_19-1 |  | OP70960 20234939 | 581094Z | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 47.02 | 4 | CEIS | 14203.27MM+60003.24MM | -- | 49 | 27.67 | No | 2019-09-27 | D_s1_d2 | 1.4 | 32 | 44.6 | 1230 | 56.2 | D | 8.1 | 0.02 | s1 | n | y | d2
|  | 72554 | 583932J | AFUMEX ATEX MRZ1OZ1MZ1-K 1KV RH 10X2.5MM² | 27.8 | 6 | Manlleu | 1602SEES+LANTORHELICOIDAL+GFR380 | -- | 35 | 21 | No | 2019-09-06 | B2_s1_d2 | 0.53 | 6.5 | 11 | 1425 | 18.3 | B2 | 0.4 | 0 | s1 | y | y | d2
|  | 72586 | 586343E | AFUMEX FIRS ATEX MRZ1MAZ1-K RH 1X240MM² | 35.8 | 5 | Manlleu | 1602SEES+LANTORHELICOIDAL+GFR380 | -- | 37 | 21 | No | 2019-09-06 | B2_s1_d2 | 0.48 | 4.4 | 5.3 | 690 | 16.2 | B2 | 0.2 | 0 | s1 | y | y | d2
|  | 72582 | 580741R | KX-ROZ1MZ1 500V 1X2X1.3MM² RH | 12 | 13 | Manlleu | 1602SEES+LANTORHELICOIDAL+GFR380 | -- | 36 | 21 | No | 2019-09-06 | B2_s1_d1 | 0.74 | 12.3 | 19.2 | 885 | 54.8 | B2 | 10.1 | 0.02 | s1 | y | n | d1
TN_2019_1636 |  | 83160172 20298782 | 493561E | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 40.83 | 5 | Vilanova | 14203.78MM+16023.44MM | CD | 23 | 57.4 | No | 2019-09-05 | C_s1_d2 | 1.22 | 25 | 47.3 | 1500 | 39.4 | C | 12.3 | 0.02 | s1 | n | y | d2
TN_2019_1637 |  | 72543 20301161 | 548097H | AFUMEX RHZ1-RA-OL (AS) DCA-S1B.D2.A1 18_30KV 1X400 | 50.16 | 4 | Vilanova |  | CD | 49.7 | 23.7 | No | 2019-09-05 | B2_s1_d0 | 0.55 | 5.4 | 6.7 | 849 | 17.8 | B2 | 20.6 | 0.03 | s1 | n | n | d0
TN_2019_1638 |  | 83025673 20193636 | 568950Z | AFUMEX CLASS RZ1-K (AS) 1KV 1X16 | 10.83 | 14 | Vilanova | 1420+1602 | CD | 48.3 | 24.5 | No | 2019-09-05 | D_s1_d2 | 2.14 | 31.4 | 40.7 | 1437 | 63.5 | D | 32.1 | 0.07 | s1 | n | y | d2
TN_2019_1639 |  |  | CT60-24470 | TECNICAS DEL CABLE RZ1MZ1-K (AS) 1KV 3G6 | 18.55 | 8 | Vilanova | COMPETITORSAMPLE | CD | 45.3 | 26.7 | No | 2019-09-05 | C_s1_d2 | 1.24 | 27.5 | 55.6 | 1008 | 78.6 | C | 39.2 | 0.07 | s1 | n | y | d2
TN_2019_1641 |  |  | T60-0113 | TRATOS HZ1MZ1H-K 1 KV 7G2.5 | 21.2 | 7 | Vilanova | COMPETITORSAMPLE | CD | 49 | 21.6 | No | 2019-09-06 | B2_s1_d2 | 0.53 | 10.1 | 22.6 | 1347 | 21.7 | B2 | 20.7 | 0.07 | s1 | n | y | d2
TN_2019_1642 |  |  |  | TECNICAS DEL CABLE Z1OZ1MZ1(AS) RH 500V 2X1.5 | 11.57 | 13 | Vilanova | COMPETITORSAMPLE | CD | 44.2 | 23.9 | No | 2019-09-06 | B2_s1_d1 | 1.07 | 12.6 | 22.7 | 894 | 54.1 | B2 | 36.6 | 0.07 | s1 | y | n | d1
TN_2019_1643 |  |  |  | TECNICAS DEL CABLE RZ1MZ1-K (AS) RH 1KV 5X1.5 | 16.19 | 9 | Vilanova | COMPETITORSAMPLE | CD | 37.5 | 25.9 | No | 2019-09-06 | C_s2_d2 | 0.83 | 15.8 | 24.9 | 987 | 36.2 | C | 61.9 | 0.08 | s2 | n | y | d2
TN_2019_1644 |  |  |  | NEXANS AL SECURE RZ1-K (AS) 1KV 5G1.5 | 12.39 | 13 | Vilanova | COMPETITORSAMPLE | CD | 65.8 | 21.8 | No | 2019-09-09 | B2_s1_d1 | 0.59 | 10.3 | 25.3 | 747 | 57.8 | B2 | 37.1 | 0.08 | s1 | y | n | d1
TN_2019_1645 |  |  |  | NEXANS AL SECURE RZ1-K (AS) 1KV 3G1.5 | 10.43 | 15 | Vilanova | COMPETITORSAMPLE | CD | 64.8 | 22 | No | 2019-09-09 | C_s2_d1 | 1.99 | 23.7 | 38.2 | 939 | 92.2 | C | 93.9 | 0.1 | s2 | y | n | d1
TN_2019_1646 |  |  |  | NEXANS AL SECURE RZ1-K (AS) 1KV 1X16 | 10.38 | 15 | Vilanova | COMPETITORSAMPLE | CD | 63 | 23.2 | No | 2019-09-09 | B2_s1_d1 | 1.14 | 12.4 | 26 | 756 | 57.3 | B2 | 13.8 | 0.05 | s1 | y | n | d1
TN_2019_1647 |  |  | 080P08742 | NEXANS AL SECURE RZ1-K (AS) 1KV 1X240 | 28.29 | 6 | Vilanova | COMPETITORSAMPLE | CD | 59.6 | 24.3 | No | 2019-09-09 | B2_s1_d1 | 0.44 | 5.2 | 6.2 | 1410 | 17.7 | B2 | 8.2 | 0.01 | s1 | y | n | d1
TN_2019_1648 |  |  |  | AENOR USE HAR 336 NX HO7Z1-K TYPE 3 (AS) 2019 1X1.5 | 2.96 | 165 | Vilanova | COMPETITORSAMPLE | CD | 54.7 | 25.5 | No | 2019-09-09 | B2_s1_d0 | 1.04 | 6.8 | 17.3 | 690 | 58.2 | B2 | 23.7 | 0.07 | s1 | n | n | d0
|  | 83227472 | 575265N | H07Z1-R 1X70 AV | 13.6 | 11 | Manlleu |  | -- | 38 | 21 | No | 2019-09-06 | B2_s1_d1 | 0.68 | 7.1 | 17 | 774 | 41.6 | B2 | 0.3 | 0 | s1 | Y | N | d1
TN_2019_1649 |  |  | 22785 | TECNICAS DEL CABLE RZ1MZ1-K (AS) RH 1KV 4X70 | 42.9 | 5 | Vilanova | COMPETITORSAMPLE | CD | 65.4 | 22.9 | No | 2019-09-10 | B2_s1_d2 | 0.61 | 12.4 | 14.7 | 1278 | 41.4 | B2 | 32.6 | 0.04 | s1 | n | y | d2
TN_2019_1650 |  | OP72900 20298979 | 499331B | RHZ1-2OL (AS) 1X240MM 36_66KV | 53.24 | 4 | Vilanova | 14202.48MM+60002.93MM | CD | 62.7 | 22.1 | No | 2019-09-10 | C_s1_d2 | 1.21 | 29.4 | 46.6 | 1362 | 50.7 | C | 9.9 | 0.05 | s1 | n | y | d2
TN_2019_1651 |  | OP83226691 20303477 | 528826L | RHZ1-2OL (AS) 1X120MM 36_66KV | 50.23 | 4 | Vilanova | 14202.46MM+60002.92MM | CD | 62.2 | 21.5 | No | 2019-09-10 | D_s1_d2 | 1.5 | 32 | 58.5 | 1497 | 51.1 | D | 14.6 | 0.04 | s1 | n | y | d2
TN_2019_1652 |  | 83089747 20193656 | 592264R | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.14 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 53.2 | 22.6 | No | 2019-09-16 | C_s1_d2 | 1.81 | 29.5 | 44.6 | 951 | 68.6 | C | 18.9 | 0.04 | s1 | n | y | d2
TN_2019_1653 |  | 83089747 20193656 | 592264R | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.14 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 50.1 | 24.2 | No | 2019-09-16 | C_s1_d1 | 1.49 | 18.8 | 28.3 | 1230 | 41.7 | C | 46.3 | 0.08 | s1 | y | n | d1
TN_2019_1654 |  | OP83226691 20303477 | 528826L | RHZ1-2OL (AS) 1X120MM 36_66KV | 50.23 | 4 | Vilanova | 14202.46MM+60002.92MM | CD | 48.2 | 25.7 | No | 2019-09-16 | C_s1_d2 | 1.23 | 26.9 | 50.8 | 1500 | 43 | C | 10.1 | 0.02 | s1 | n | y | d2
TN_2019_1655 |  |  | T80-1638 | TECNICAS DEL CABLE RZ1MZ1-K (AS) RH 1KV 5G16 | 28.27 | 6 | Vilanova | COMPETITORSAMPLE | CD | 44.3 | 27.3 | No | 2019-09-16 | B2_s1_d2 | 0.53 | 9.7 | 17.3 | 1497 | 30.6 | B2 | 3.9 | 0.02 | s1 | n | y | d2
TN_2019_1656 |  | OP72742 20184153 | 583489C | LXHIOZ1 1X120 17.5KV | 34.09 | 5 | Vilanova | 14201.32MM+60002.28MM | CD | 55.3 | 22 | No | 2019-09-17 | D_s1_d2 | 3 | 55 | 129.8 | 1497 | 108.4 | D | 23.3 | 0.1 | s1 | n | y | d2
TN_2019_1657 |  | OP72900 20298979 | 499331B | RHZ1-2OL (AS) 1X240MM 36_66KV | 53.24 | 4 | Vilanova | 14202.48MM+60002.93MM | CD | 50.6 | 25.5 | No | 2019-09-17 | C_s1_d2 | 1.45 | 28.8 | 50.5 | 1494 | 49.7 | C | 21.5 | 0.04 | s1 | n | y | d2
1909001 |  | 17995 | -- | FO DROP 1MM 20 D01 | 1.9 | 375 | Paron | 5200SMIT+1700SEES | -- | 57.8 | 22.8 | No | 2019-09-25 | B2_s1_d0 | 1.3 | 13.6 | 29.8 | 825 | 81 | B2 | 20 | 0.06 | s1 | n | n | d0
1909002 |  | 17995 | -- | FO DROP 1MM 41 D01 | 4 | 90 | Paron | 5200SMIT+1700SEES | -- | 54.2 | 23.4 | No | 2019-09-25 | C_s1_d0 | 1.5 | 14.4 | 38.2 | 594 | 140 | C | 31 | 0.09 | s1 | n | n | d0
1909003 |  | 17995 | -- | FO DROP 1MM 29 D01 | 2.9 | 165 | Paron | 5200SMIT+1700SEES | -- | 62.5 | 22.5 | No | 2019-09-25 | C_s1_d1 | 1.3 | 14.5 | 32.7 | 672 | 92 | C | 36 | 0.09 | s1 | y | n | d1
TN_2019_1659 |  | 83175965 20184156 | 558392Y | XHIOZ1 1X500 17.5KV | 50.5 | 4 | Vilanova | 14201.96MM+60002.39MM | CD | 76.2 | 20.9 | No | 2019-09-23 | D_s1_d2 | 1.4 | 32.3 | 51.6 | 1458 | 50.9 | D | 36.6 | 0.08 | s1 | n | y | d2
TN_2019_1661 |  | 83266864 20193656 | 596724N | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.36 | 13 | Vilanova | 14200.57MM+16021.60MM | CD | 58.6 | 25.9 | No | 2019-09-23 | C_s1_d1 | 1.81 | 27.6 | 38.9 | 1338 | 53.6 | C | 33.4 | 0.08 | s1 | y | n | d1
TN_2019_1662 |  | 20307525 | 5096888 | 750-5G70-SH-NF F 55-625-255 | 42.8 | 5 | Vilanova | IX1400FR+0400FEIT/5300SEIT | CD | 70 | 22.9 | No | 2019-09-25 | B2_s1_d0 | 0.4 | 4.7 | 6.2 | 933 | 16.5 | B2 | 5.2 | 0.02 | s1 | n | n | d0
TN_2019_1663 |  | 20310298 | BBT909016 | 1000-1X35MM²-SH-NF F55-625-255 | 13.6 | 11 | Vilanova | IX1400FR+0400FEIT+5300SEIT | CD | 63.3 | 23.8 | No | 2019-09-25 | B2_s2_d1 | 0.73 | 8.5 | 13.7 | 1350 | 28.9 | B2 | 83.8 | 0.16 | s2 | y | n | d1
TN_2019_1664 |  | 20232375 | BBT909023 | 1000-1X35MM²-SH-NF F55-625-255 | 13.9 | 11 | Vilanova | ID3100FR/SV3300FR+0400FEIT+5300SEIT | CD | 60.4 | 24.7 | No | 2019-09-25 | B2_s1_d2 | 0.74 | 8.5 | 18.4 | 987 | 28.9 | B2 | 25.5 | 0.08 | s1 | n | y | d2
TN_2019_1665 |  | 20232377 | BBT909019 | 1X70 R 1 KV SH NOIR | 18.4 | 8 | Vilanova | IX1400FR+0400FEIT/5300SEIT | CD | 59.8 | 25.7 | No | 2019-09-25 | B2_s1_d0 | 0.43 | 2.7 | 4.4 | 627 | 16.2 | B2 | 0.1 | 0.01 | s1 | n | n | d0
19090004 |  | 17995 | -- | FO DROP 2MM 41 D01 | 4.1 | 75 | Paron | 5200SMIT+1700SEES | -- | 64.4 | 23.3 | No | 2019-09-26 | C_s1_d1 | 1.8 | 17 | 44.7 | 687 | 142 | C | 27 | 0.07 | s1 | y | n | d1
19090005 |  | 17970 | -- | ZPFU-SH-28P*1MM²GENERAL CABLE 6 2019 OZ SNCF RESEAU | 34.5 | 5 | Paron | HE6063+TPS290 | -- | 63.2 | 24.1 | No | 2019-09-26 | B2_s1_d0 | 0.5 | 5.7 | 9 | 1410 | 18 | B2 | 7 | 0.01 | s1 | n | n | d0
19090006 |  | 17995 | -- | FO DROP 4MM 43 D01 (JA 10048289) | 4.2 | 75 | Paron | 5200SMIT+1700SEES | -- | 64.2 | 23 | No | 2019-09-26 | C_s1_d1 | 1.98 | 19.1 | 43.3 | 729 | 112 | C | 16 | 0.04 | s1 | y | n | d1
TN_2019_1666 |  | 83266864 20193656 | 596724N | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.36 | 13 | Vilanova | 14200.57MM+16021.60MM | CD | 74 | 21.1 | No | 2019-09-26 | C_s1_d1 | 1.14 | 21 | 27.4 | 1266 | 42.4 | C | 12.1 | 0.05 | s1 | y | n | d1
TN_2019_1667 |  | 20215639 | T1-H19148 | FG16OM16 7G1.5MM² - 0.6/1 KV | 15.11 | 10 | Vilanova | 5300SEIT+0300FDIT | CD | 68.3 | 22.9 | No | 2019-09-26 | C_s2_d2 | 0.67 | 14.1 | 31.8 | 1050 | 42.4 | C | 62.8 | 0.09 | s2 | n | y | d2
TN_2019_1668 |  | 20215466 | T7-I32032 | FG16OR16 7G2.5MM² - 0.6/1 KV | 15.7 | 9 | Vilanova | 2000SPIT+05ABFPIT | CD | 58.6 | 24.6 | No | 2019-09-26 | C_s2_d0 | 1.12 | 15.4 | 30.4 | 939 | 50.2 | C | 135.3 | 0.38 | s2 | n | n | d0
TN_2019_1669 |  | 83200309 20306090 | 594630M | DHZ1MZ1(AS) RH FCA 10KV 3X50 | 53.1 | 4 | Vilanova | EPDMID7140IT+1420+1602+COGEGUMGFR380 | CD | 58.8 | 26.1 | No | 2019-09-26 | B2_s1_d2 | 0.78 | 6.1 | 7.7 | 597 | 28.6 | B2 | 15.5 | 0.04 | s1 | n | y | d2
19090008 |  | 18011 | -- | PESS 1044-28-1.2-NF F 55-623-PRYSMIAN 255 | 28.4 | 6 | Paron | IX1400FR+3000GV+5300SEIT | -- | 52.9 | 22.2 | No | 2019-09-30 | B2_s1_d2 | 0.7 | 10.5 | 14.4 | 747 | 39 | B2 | 8 | 0.01 | s1 | y | y | d2
19090007 |  | 18001 | -- | CEI-60840-RTE-PRYSMIAN 255 -630AL-PR-11-AL-52/90(100)KV | 70 | 3 | Paron | XLPE+TUBEAL+6000SEES+SKINSC | -- | 53.6 | 21.6 | No | 2019-09-30 | C_s1_d1 | 1.3 | 18.2 | 24.3 | 1140 | 38 | C | 22 | 0.07 | s1 | y | n | d1
19090009 |  | 17995 | -- | FO DROP 1MM 41 D02 | 4 | 90 | Paron | 5200SMIT+1700SEES | -- | 54.2 | 22.9 | No | 2019-09-30 | C_s1_d1 | 1.2 | 12.6 | 32.6 | 609 | 121 | C | 20 | 0.05 | s1 | y | n | d1
19090010 |  | 18011 | -- | PESS 1043 -01-1.2-NF F 55-623-PRYSMIAN 255 | 12.8 | 12 | Paron | IX1400FR+3000GV+5300SEIT | -- | 50.8 | 23 | No | 2019-09-30 | B2_s1_d2 | 0.5 | 6.8 | 10.9 | 858 | 34 | B2 | 9 | 0.02 | s1 | y | y | d2
TN_2019_1670 |  | 83266864 20193656 | 596724N | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.36 | 13 | Vilanova | 14200.57MM+16021.60MM | CD | 73.2 | 22.6 | No | 2019-10-01 | C_s1_d0 | 1.37 | 22.7 | 35.4 | 987 | 53.6 | C | 35.7 | 0.1 | s1 | n | n | d0
TN_2019_1671 |  | 83175965 / 83175919 20184156 | 558392Y | XHIOZ1 1X500 17.5KV | 50.5 | 4 | Vilanova | 14201.96MM+60002.39MM | CD | 71.3 | 22.5 | No | 2019-10-01 | C_s1_d2 | 1.7 | 25.6 | 40.2 | 960 | 61.1 | C | 29 | 0.08 | s1 | n | y | d2
TN_2019_1672 |  | 82856493 | 569716G | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.33 | 8 | Vilanova | COPPERTAPE50%+MICA+LANTOR+1602 | CD | 70.3 | 24 | No | 2019-10-01 | D_s1_d2 | 1.76 | 35 | 83.8 | 1371 | 79.1 | D | 32.1 | 0.1 | s1 | n | y | d2
TN_2019_1673 |  | 20215639 | T1-H19148 | FG16OM16 7G1.5MM² - 0.6/1 KV | 15.11 | 10 | Vilanova | 5300SEIT+0300FDIT | CD | 64.9 | 26.8 | No | 2019-10-01 | B2_s1_d2 | 0.66 | 11.6 | 27.9 | 1176 | 31.9 | B2 | 17.6 | 0.04 | s1 | n | y | d2
19100001 |  | 18002 | -- | 1000-1X35MM²-SH-NF F55-625-255 | 13.7 | 11 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 56 | 22 | No | 2019-10-02 | B2_s1_d1 | 0.67 | 14.6 | 20.9 | 1017 | 51 | B2 | 9 | 0.02 | s1 | y | n | d1
19100002 |  | 18002 | -- | 1000-1X35MM²-SH-NF F55-625-255 | 13.9 | 11 | Paron | ID3100FR/SV3600FR+0400FEIT+5300SEIT | -- | 48.8 | 21.9 | No | 2019-10-02 | B2_s1_d2 | 0.67 | 9.9 | 16.5 | 978 | 33 | B2 | 20 | 0.04 | s1 | y | y | d2
19100003 |  | 18002 | -- | 1000-1X70MM²-SH-NF F55-625-255 | 18.6 | 8 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 47.3 | 21.2 | No | 2019-10-02 | B2_s1_d0 | 0.43 | 5.2 | 7.3 | 708 | 25 | B2 | 14 | 0.02 | s1 | n | n | d0
19100004 |  | 18002 | -- | 1000-5G70MM²-SH-NF F55-625-255 | 42.9 | 5 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 61 | 20.3 | No | 2019-10-04 | B2_s1_d0 | 0.57 | 3.9 | 4.8 | 1335 | 12 | B2 | 3 | 0 | s1 | n | n | d0
19100005 |  | 18040 | -- | 750-1X185MM²-SH-NF F 55-625-255 | 23 | 7 | Paron | ID3100FR+SV3200FR | -- | 63.9 | 19.6 | No | 2019-10-04 | B2_s1_d2 | 0.67 | 8.9 | 17.1 | 1407 | 24 | B2 | 17 | 0.05 | s1 | y | y | d2
19100006 |  | 18039 | -- | K25 750V 1X1 -SH-NF F 55-625-255 | 3.3 | 135 | Paron | 1602SEES | -- | 52.4 | 20.2 | No | 2019-10-07 | C_s2_d1 | 1.87 | 18.4 | 47.7 | 606 | 208 | C | 71 | 0.26 | s2 | y | n | d1
TN_2019_1675 |  | 73177 20259187 | 597578S | ROZ1-K 500V 1X2X0.75MM2 | 6.51 | 21 | Vilanova |  | CD | 52.1 | 19.7 | No | 2019-10-08 | D_s2_d2 | 3.3 | 44.4 | 88.3 | 1086 | 191.8 | D | 53.7 | 0.11 | s2 | n | y | d2
TN_2019_1676 |  | 73180 20089252 | 593637H | RHOZ1-K 500V 2X2X0.75MM2 | 10.57 | 14 | Vilanova |  | CD | 51.7 | 19.4 | No | 2019-10-07 | D_s1_d2 | 1.73 | 19.9 | 60.6 | 675 | 192.3 | D | 40.6 | 0.11 | s1 | n | y | d2
TN_2019_1677 |  | 82856493 | 569716G | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.33 | 8 | Vilanova | COPPERTAPE50%+MICA+LANTOR+1602 | CD | 45.2 | 20.2 | No | 2019-10-07 | D_s1_d2 | 1.67 | 31.7 | 73.8 | 1473 | 63 | D | 9.5 | 0.04 | s1 | n | y | d2
TN_2019_1678 |  | 72745 20080658 | 581077F | AL-HEPRZ1(AS) 1X50MM2 12/20KV | 32.95 | 6 | Vilanova | 14202.79MM+60002.82MM | CD | 42.8 | 22.3 | No | 2019-10-07 | D_s1_d2 | 1.98 | 41.4 | 88.3 | 1500 | 73.8 | D | 26.4 | 0.04 | s1 | n | y | d2
TN_2019_1679 |  | 72745 20080658 | 581076E | AL-HEPRZ1(AS) 1X50MM2 12/20KV | 32.6 | 6 | Vilanova | 14202.66MM+60002.52MM | CD | 39.8 | 24.9 | No | 2019-10-07 | D_s1_d2 | 1.96 | 47.1 | 119.1 | 1500 | 99.3 | D | 15.7 | 0.05 | s1 | n | y | d2
TN_2019_1681 |  | 72101 20300070 | TO-H17986 | ES 768 A 3X16 MM2 | 30.81 | 6 | Vilanova | 0400+5300+WST+ARM+SC+5300 | CD | 67.4 | 20.4 | No | 2019-10-08 | B2_s1_d2 | 0.77 | 10 | 14.3 | 612 | 53.6 | B2 | 20.5 | 0.04 | s1 | n | y | d2
TN_2019_1682 |  | 72101 20300070 | TO-H17986 | ES 768 A 3X16 MM2 | 29.79 | 6 | Vilanova | 0400+5300+ARM+SC+5300 | CD | 68 | 22.1 | No | 2019-10-08 | B2_s1_d2 | 0.78 | 14.2 | 22.9 | 1500 | 50.7 | B2 | 27.9 | 0.05 | s1 | n | y | d2
TN_2019_1683 |  | 72102 20300071 | TO-H90184 | ES 768 A 3X70 | 41.6 | 5 | Vilanova | 0400+5300+ARM+SC+5300 | CD | 63.1 | 24 | No | 2019-10-08 | B2_s1_d2 | 0.48 | 11.2 | 14.2 | 897 | 47.3 | B2 | 13.6 | 0.02 | s1 | n | y | d2
1910007 |  | 18049 | -- | 750-5G1.5-SH-NF F 55-625-255 | 14.6 | 10 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 53.3 | 22.5 | No | 2019-10-11 | B2_s1_d1 | 0.67 | 9.4 | 16.1 | 1080 | 27 | B2 | 12 | 0.03 | s1 | y | n | d1
TN_2019_1685 |  | OP73834 20193638 | 507735L | AFUMEX CLASS RZ1-K (AS) 1KV 1X35 | 13.87 | 11 | Vilanova | SXLPE+1420FEES0.78MM+1602SEES1.53MM | CD | 70.2 | 21.4 | No | 2019-10-10 | C_s1_d2 | 0.95 | 17.3 | 28.8 | 984 | 43.2 | C | 40.1 | 0.1 | s1 | n | y | d2
TN_2019_1686 |  | OP83333368 20193655 | 550660U | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 11.2 | 14 | Vilanova | SXLPE+1420FEES0.53MM+1602SEES1.62MM | CD | 77.1 | 21 | No | 2019-10-10 | C_s1_d2 | 1.12 | 16.2 | 25.8 | 810 | 50.9 | C | 30.2 | 0.1 | s1 | n | y | d2
TN_2019_1687 |  | OP73834 20193638 | 507735L | AFUMEX CLASS RZ1-K (AS) 1KV 1X35 | 13.87 | 11 | Vilanova | SXLPE+1420FEES0.78MM+1602SEES1.53MM | CD | 39.2 | 21.4 | No | 2019-10-15 | B2_s1_d2 | 0.96 | 14.1 | 22.1 | 1095 | 34.1 | B2 | 16.2 | 0.04 | s1 | n | y | d2
TN_2019_1688 |  | OP83333368 20193655 | 550660U | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 11.2 | 14 | Vilanova | SXLPE+1420FEES0.53MM+1602SEES1.62MM | CD | 35.5 | 22.8 | No | 2019-10-15 | C_s1_d2 | 1.94 | 26.6 | 37.5 | 858 | 70.6 | C | 26.5 | 0.04 | s1 | n | y | d2
CEL-940/19-1 |  | 83266864 20193656 | 596724N | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.31 | 13 | CEIS | SXLPE+1420FEES+1602SEES | -- | 40 | 29.87 | No | 2019-10-08 | D_s1_d1 | 1.6 | 31 | 44.7 | 954 | 69.3 | D | 16 | 0.03 | s1 | y | n | d1
CEL-940/19-1 |  | 83266864 20193656 | 596724N | AFUMEX CLASS RZ1-K (AS) 1KV 3G4 | 12.31 | 13 | CEIS | SXLPE+1420FEES+1602SEES | -- | 58 | 24.72 | No | 2019-10-11 | D_s1_d1 | 1.6 | 33.8 | 48.7 | 933 | 78.5 | D | 21.5 | 0.03 | s1 | y | n | d1
TN_2019_1689 |  | 72582 20282519 | 580741R | KX-ROZ1MZ1 500V 1X2X1.3MM² RH | 12.24 | 13 | Vilanova | 1602SEES+LANTORHELICOIDAL+GFR380 | CD | 57.1 | 18 | No | 2019-10-17 | B2_s1_d2 | 0.71 | 11 | 22.6 | 717 | 55.8 | B2 | 24.1 | 0.04 | s1 | n | y | d2
TN_2019_1690 |  | 69985 20271635 | 508016S | DZ1 ADIF B2CA 3.6/6KV 1X 300MM² CU | 31.67 | 6 | Vilanova | IRN267+6000SEES | CD | 56.3 | 18.2 | No | 2019-10-17 | C_s1_d2 | 1.81 | 17.8 | 28.4 | 864 | 60.3 | C | 47.5 | 0.13 | s1 | n | y | d2
TN_2019_1691 |  | 73701 20284882 | 599714N | AFUMEX FIRS ATEX MRZ1MAZ1-K RH 1X240 MM2 | 34.31 | 5 | Vilanova | GFR380+ARMADOHILOSACERO+GRF380 | CD | 53.7 | 19.6 | No | 2019-10-17 | B2_s1_d1 | 0.49 | 3 | 5.7 | 402 | 27.1 | B2 | 7.9 | 0.02 | s1 | y | n | d1
TN_2019_1692 |  | OP83226691 20303477 | 528826L | RHZ1-2OL (AS) 1X120MM 36_66KV | 50.23 | 4 | Vilanova | 14202.46MM+60002.92MM | CD | 54.9 | 21.4 | No | 2019-10-17 | D_s1_d2 | 1.52 | 35 | 49.3 | 1359 | 58.6 | D | 14.7 | 0.04 | s1 | n | y | d2
TN_2019_1693 |  |  | 603868D | SEGURFOC CLASS-331 (AS+) 1KV 3G2.5 NJ | 12.31 | 13 | Vilanova | VSI+TPR-49B-600+TPR-55 | CD | 56 | 24.6 | No | 2019-10-17 | B2_s1_d2 | 0.76 | 9.1 | 17.9 | 852 | 42.8 | B2 | 14.1 | 0.03 | s1 | n | y | d2
19100008 |  | 18027 | -- | SNCF RESEAU TFO .144B.L04 GENERAL CABLE 6 | 18.6 | 8 | Paron | MODULEENVPE913+RUBANPOLYESTERINTISSÉ+TPS426+TPR248 | -- | 53.9 | 22.2 | No | 2019-10-18 | B2_s1_d2 | 0.67 | 9.9 | 17.1 | 1305 | 20 | B2 | 35 | 0.07 | s1 | y | y | d2
TN_2019_1697 |  | 72560 20303415 | 547642N | RZ1F3Z1 TPR-55 B2CA 3KV 3X16 WITH LANTOR | 28.7 | 6 | Vilanova | TPR-55WITHLANTOR | CD | 57.1 | 18.8 | No | 2019-10-18 | B2_s1_d1 | 0.53 | 6.2 | 9.4 | 1497 | 27.7 | B2 | 9.9 | 0.02 | s1 | y | n | d1
TN_2019_1698 |  | 69812 20284400 | 252975Y | DZ1F3Z1 ADIF B2CA 2X150 | 48.06 | 4 | Vilanova | EPR+GFR380 | CD | 52.7 | 21.5 | No | 2019-10-18 | B2_s1_d0 | 0.64 | 4.9 | 8.1 | 651 | 27.8 | B2 | 1.1 | 0.01 | s1 | n | n | d0
TN_2019_1700 |  | 72560 20303415 | 547642N | AL-AFUMEX RZ1F3Z1 ADIF B2CA 3/3 KV 3X16 | 28.7 | 6 | Vilanova | TPR-55WITHLANTOR | CD | 57 | 17.6 | No | 2019-10-21 | B2_s1_d1 | 0.44 | 5.5 | 10.4 | 1500 | 24.9 | B2 | 6.8 | 0.03 | s1 | y | n | d1
TN_2019_1701 |  | 69812 20284400 | 252975Y | AL-AFUMEX RZ1F3Z1 ADIF B2CA 3/3 KV 2X150 | 48.06 | 4 | Vilanova | EPR+GFR380 | CD | 57.3 | 17.9 | No | 2019-10-21 | B2_s1_d1 | 0.57 | 4.2 | 7.1 | 627 | 28.1 | B2 | 3.5 | 0.01 | s1 | y | n | d1
TN_2019_1702 |  | 73701 20284882 | 599714N | AFUMEX FIRS ATEX MRZ1MAZ1-K RH 1X240 MM2 | 34.31 | 5 | Vilanova | GFR380+ARMADOHILOSACERO+GRF380 | CD | 56.5 | 18.6 | No | 2019-10-21 | B2_s1_d1 | 0.51 | 3 | 4.8 | 1458 | 17 | B2 | 24.4 | 0.04 | s1 | y | n | d1
TN_2019_1703 |  | 83200309 20306090 | 594630M | DHZ1MZ1(AS) RH FCA 10KV 3X50 | 53.1 | 4 | Vilanova | EPDMID7140IT+1420+1602+COGEGUMGFR380 | CD | 56.3 | 18.9 | No | 2019-10-21 | B2_s1_d2 | 0.78 | 6.5 | 11.4 | 1500 | 28.1 | B2 | 19.6 | 0.04 | s1 | n | y | d2
19100009 |  | 18071 | -- | ZUG-S-SH-6P*1MM²-PRYSMIAN 255 | 13 | 12 | Paron | IW31000+SW3800FR | -- | 45.7 | 19 | No | 2019-10-22 | B2_s1_d1 | 0.87 | 11.2 | 18.8 | 900 | 36 | B2 | 26 | 0.05 | s1 | y | n | d1
TN_2019_1705 |  | OP83226691 20303477 | 528826L | RHZ1-2OL (AS) 1X120MM 36_66KV | 50.23 | 4 | Vilanova | 14202.46MM+60002.92MM | CD | 78.9 | 17.1 | No | 2019-10-22 | C_s1_d2 | 1.42 | 26.9 | 53 | 1500 | 60.3 | C | 2.6 | 0.01 | s1 | n | y | d2
TN_2019_1706 |  | OP72900 20298979 | 499331B | RHZ1-2OL (AS) 1X240MM 36_66KV | 53.24 | 4 | Vilanova | 14202.48MM+60002.93MM | CD | 77.8 | 18.7 | No | 2019-10-22 | C_s1_d2 | 1.4 | 26.7 | 53.1 | 1497 | 49.4 | C | 3.5 | 0.01 | s1 | n | y | d2
TN_2019_1707 |  | 72582 20282519 | 580741R | KX-ROZ1MZ1 500V 1X2X1.3MM² RH | 12.24 | 13 | Vilanova | 1602SEES+LANTORHELICOIDAL+GFR380 | CD | 70.8 | 20.3 | No | 2019-10-22 | C_s1_d1 | 1.67 | 23 | 35.9 | 783 | 76.9 | C | 24.8 | 0.04 | s1 | y | n | d1
TN_2019_1708 |  | 69985 20271635 | 508016S | DZ1 ADIF B2CA 3.6/6KV 1X 300MM² CU | 31.67 | 6 | Vilanova | IRN267+6000SEES | CD | 66.8 | 21.1 | No | 2019-10-22 | C_s2_d1 | 1.48 | 23.5 | 36.3 | 927 | 68.9 | C | 115.4 | 0.23 | s2 | y | n | d1
TN_2019_1709 |  | 69985 20271635 | 508016S | DZ1 ADIF B2CA 3.6/6KV 1X 300MM² CU | 31.67 | 6 | Vilanova | IRN267+6000SEES | CD | 82.8 | 17.9 | No | 2019-10-22 | C_s2_d2 | 1.54 | 29.5 | 42.7 | 1500 | 66.2 | C | 68.4 | 0.17 | s2 | n | y | d2
TN_2019_1710 |  | 73700 20300513 | 610609F | AFUMEX FIRS ATEX MRZ1MAZ1-K RH 10X2.5 | 27 | 6 | Vilanova | GFR380+ARMADOHILOSACERO+GRF380 | CD | 78 | 19.9 | No | 2019-10-23 | B2_s1_d2 | 0.54 | 6.5 | 8.8 | 1152 | 24.6 | B2 | 0.3 | 0.01 | s1 | n | y | d2
TN_2019_1711 |  | 73700 20300513 | 610613K | AFUMEX FIRS ATEX MRZ1MAZ1-K RH 10X2.5 | 27.02 | 6 | Vilanova | 6010SEES+ARMADOHILOSACERO+GRF380 | CD | 65.8 | 21.1 | No | 2019-10-23 | B2_s1_d2 | 0.54 | 6.5 | 8.4 | 1302 | 26.6 | B2 | 5 | 0.01 | s1 | n | y | d2
TN_2019_1712 |  | 73700 20300513 | 610613K | AFUMEX FIRS ATEX MRZ1MAZ1-K RH 10X2.5 | 27.02 | 6 | Vilanova | 6010SEES+ARMADOHILOSACERO+GRF380 | CD | 69.7 | 15.8 | No | 2019-10-24 | B2_s1_d2 | 0.47 | 6.7 | 9.4 | 1371 | 22.5 | B2 | 10 | 0.01 | s1 | n | y | d2
TN_2019_1713 |  | 69985 20271635 | 508016S | DZ1 ADIF B2CA 3.6/6KV 1X 300MM² CU | 31.67 | 6 | Vilanova | IRN267+6000SEES | CD | 67.3 | 16.5 | No | 2019-10-24 | B2_s1_d2 | 1.15 | 13.4 | 21.7 | 939 | 61.3 | B2 | 24 | 0.07 | s1 | n | y | d2
TN_2019_1714 |  | 73700 20300513 | 610609F | AFUMEX FIRS ATEX MRZ1MAZ1-K RH 10X2.5 | 27 | 6 | Vilanova | GFR380+ARMADOHILOSACERO+GRF380 | CD | 63 | 18.1 | No | 2019-10-24 | B2_s1_d2 | 0.56 | 6.6 | 10.9 | 1179 | 21.7 | B2 | 10.6 | 0.02 | s1 | n | y | d2
19100010 |  | 18070 | C6665A | PK3BB494 3G1.5 1KV CU-LSOH | 11.3 | 14 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 48.9 | 23 | No | 2019-10-25 | C_s1_d1 | 1.3 | 16.3 | 25.2 | 852 | 47 | C | 37 | 0.06 | s1 | y | n | d1
19100011 |  | 18070 | C6665B | PK3BB494 3G1.5 1KV CU-LSOH | 11.4 | 14 | Paron | IX1400FR+GV3100FR | -- | 53.9 | 23.1 | No | 2019-10-25 | C_s1_d2 | 1.5 | 20.6 | 31.4 | 1206 | 38 | C | 44 | 0.08 | s1 | y | y | d2
TN_2019_1717 |  | 72834 20307483 | 586858P | RZ1KZ1MZ1-K ATEX 2RH 1KV 3X2.5/2.5 | 38.06 | 5 | Vilanova | PENDINGTOCONFIRM | CD | 70.3 | 18.4 | No | 2019-10-30 | B2_s1_d2 | 0.5 | 6.5 | 11.4 | 1446 | 24.5 | B2 | 13 | 0.03 | s1 | n | y | d2
TN_2019_1718 |  | 80709392 | 599575H | CCTSST FR 0.3 4X1.4 | 28.09 | 6 | Vilanova | TPR38+FLEJEACERO+LANTOR+TPR55 | CD | 67.2 | 19.3 | No | 2019-10-31 | B2_s1_d2 | 0.45 | 6 | 11.6 | 1500 | 21.4 | B2 | 0 | 0 | s1 | n | y | d2
TN_2019_1719 |  | 72834 20281142 | 602285H | RZ1KZ1MZ1-K ATEX 2RH 1KV 3X50 | 17.73 | 8 | Vilanova | PENDINGTOCONFIRM | CD | 66.2 | 19.7 | No | 2019-10-31 | C_s1_d2 | 1.07 | 17.2 | 25.8 | 1284 | 34 | C | 19.6 | 0.04 | s1 | n | y | d2
TN_2019_1720 |  |  | Sample 80 | TEST SAMPLE 80 PBT + GEL STD. 32F | 12.85 | 12 | Vilanova | MEGOLONS670 | CD | 57 | 23.5 | No | 2019-10-31 | E ou F_s2_d2 | 3.3 | 103.4 | 203.4 | 1320 | 207.8 | E ou F | 166.4 | 0.36 | s2 | n | y | d2
TN_2019_1721 |  |  | Sample 79 | TEST SAMPLE 79 PBT + GEL STD. 32F | 12.85 | 12 | Vilanova | AFUMEXCPR | CD | 55.1 | 24.7 | No | 2019-10-31 | E ou F_s2_d2 | 3.3 | 110.9 | 226.3 | 1200 | 261.2 | E ou F | 113.1 | 0.19 | s2 | n | y | d2
TN_2019_1722 |  |  | Sample 75 | TEST SAMPLE 75 PBT + GEL STD. 16F | 11.54 | 13 | Vilanova | AFUMEXCPR | CD | 54.7 | 18.6 | No | 2019-11-04 | E ou F_s2_d2 | 3.3 | 108.2 | 248.3 | 1119 | 305.8 | E ou F | 74.1 | 0.18 | s2 | n | y | d2
TN_2019_1723 |  |  | Sample 86 | TEST SAMPLE 86 PBT-FR + GEL FR (AFO388) 32F | 12.9 | 12 | Vilanova | MEGOLONS670 | CD | 41.9 | 21.9 | No | 2019-11-04 | D_s2_d2 | 3.3 | 47.2 | 78.5 | 1500 | 80.6 | D | 75.7 | 0.15 | s2 | n | y | d2
TN_2019_1724 |  |  | Sample 85 | TEST SAMPLE 85 PBT-FR + GEL FR (AFO392) 32F | 11.3 | 14 | Vilanova | AFUMEXCPR | CD | 41.7 | 24.4 | No | 2019-11-04 | D_s2_d0 | 3.3 | 70 | 100.2 | 1194 | 168.4 | D | 102.3 | 0.19 | s2 | n | n | d0
TN_2019_1725 |  |  | Sample 87 | TEST SAMPLE 87 PBT-FR + GEL FR (AFO393) 32F | 11.26 | 14 | Vilanova | MEGOLONS670 | CD | 37.2 | 25.6 | No | 2019-11-04 | E ou F_s2_d2 | 3.3 | 89.2 | 189.1 | 1236 | 203 | E ou F | 199.4 | 0.47 | s2 | n | y | d2
TN_2019_1726 |  |  | Sample 76 | TEST SAMPLE 76 PBT + GEL STD. 16F | 11.77 | 13 | Vilanova | MEGOLONS670 | CD | 49.8 | 17.9 | No | 2019-11-05 | E ou F_s2_d2 | 3.3 | 96.9 | 202.3 | 1308 | 200.7 | E ou F | 126.5 | 0.28 | s2 | n | y | d2
TN_2019_1727 |  | 73177 20259187 | 586787M | ROZ1-K 500V 1X2X0.75MM2 | 8.85 | 17 | Vilanova | CUBIERTACPRDMZE | CD | 47.9 | 18.4 | No | 2019-11-05 | E ou F_s1_d0 | 3.3 | 72.5 | 204.4 | 1020 | 284 | E ou F | 20.3 | 0.1 | s1 | n | n | d0
TN_2019_1728 |  |  | Sample 84 | TEST SAMPLE 84 PBT-FR + GEL FR (AFO387) 32F | 12.9 | 12 | Vilanova | AFUMEXCPR | CD | 41.7 | 19.8 | No | 2019-11-05 | C_s1_d2 | 1.28 | 21.9 | 36.1 | 810 | 83.7 | C | 40.4 | 0.07 | s1 | n | y | d2
TN_2019_1729 |  | 73179 20295472 | 586796X | ROZ1-K 500V 1X3X0.75MM2 | 8.88 | 17 | Vilanova | CUBIERTACPRDMZE | CD | 36.6 | 21.4 | No | 2019-11-05 | E ou F_s1_d2 | 3.3 | 76.3 | 198.1 | 1239 | 211.4 | E ou F | 50 | 0.16 | s1 | n | y | d2
TN_2019_1732 |  |  | Sample 77 | TEST SAMPLE 77 PBT-FR + GEL FR (AFO386) 16F | 11.6 | 13 | Vilanova | AFUMEXCPR | CD | 51.8 | 15 | No | 2019-11-06 | C_s1_d1 | 1.36 | 22.4 | 39.6 | 879 | 84.4 | C | 37.7 | 0.07 | s1 | y | n | d1
TN_2019_1733 |  | 73700 20300513 | 610609F | AFUMEX FIRS ATEX MRZ1MAZ1-K RH 10X2.5 | 27 | 6 | Vilanova | GFR380+ARMADOHILOSACERO+GRF380 | CD | 53.5 | 15.2 | No | 2019-11-06 | B2_s1_d2 | 0.66 | 11.5 | 14.4 | 10.83 | 44.4 | B2 | 6.8 | 0.01 | s1 | n | y | d2
TN_2019_1734 |  | 73700 20300513 | 610613K | AFUMEX FIRS ATEX MRZ1MAZ1-K RH 10X2.5 | 27.02 | 6 | Vilanova | 6010SEES+ARMADOHILOSACERO+GRF380 | CD | 50.4 | 17.1 | No | 2019-11-06 | B2_s1_d2 | 0.69 | 11.6 | 16.1 | 1221 | 48.7 | B2 | 29.3 | 0.04 | s1 | n | y | d2
TN_2019_1735 |  |  | Sample 88 | TEST SAMPLE 88 PBT-FR + GEL FR (AFO385) 96F | 18.83 | 8 | Vilanova | TPR-37 | CD | 45.6 | 19 | No | 2019-11-06 | C_s1_d0 | 1.02 | 19.4 | 27.1 | 1266 | 43.3 | C | 41.2 | 0.08 | s1 | n | n | d0
TN_2019_1736 |  |  | Sample 89 | TEST SAMPLE 89 PBT-FR + GEL FR (AFO384) 96F | 19.11 | 8 | Vilanova | AFUMEXCPR | CD | 39.3 | 21 | No | 2019-11-06 | C_s1_d1 | 1.1 | 21 | 29.4 | 1158 | 42.6 | C | 43.2 | 0.07 | s1 | y | n | d1
TN_2019_1737 |  | 73180 20089252 | 586797Y | RHOZ1-K 500V 2X2X0.75MM2 | 12.62 | 12 | Vilanova | CUBIERTACPRDMZE | CD | 70 | 12.5 | No | 2019-11-10 | C_s1_d1 | 1.55 | 19.9 | 33.7 | 996 | 59.4 | C | 48.1 | 0.14 | s1 | y | n | d1
TN_2019_1738 |  |  | Sample 81 | TEST SAMPLE 81 PBT-FR + GEL FR (AFO390) 16F | 9.93 | 15 | Vilanova | AFUMEXCPR | CD | 69.8 | 12.9 | No | 2019-11-10 | D_s1_d1 | 3.3 | 66.2 | 113.1 | 1074 | 162.8 | D | 42.2 | 0.06 | s1 | y | n | d1
TN_2019_1739 |  | 73181 20259186 | 586778C | RHOZ1-K 500V 12X2X0.75MM2 | 20.27 | 8 | Vilanova | CUBIERTACPRDMZE | CD | 66.4 | 14.1 | No | 2019-11-10 | D_s1_d2 | 1.47 | 27.4 | 68.5 | 1500 | 57.1 | D | 31.7 | 0.06 | s1 | n | y | d2
TN_2019_1740 |  |  | Sample 82 | TEST SAMPLE 82 PBT-FR + GEL FR (AFO391) 16F | 9.84 | 15 | Vilanova | MEGOLONS670 | CD | 58.8 | 15.6 | No | 2019-11-10 | D_s2_d1 | 3.3 | 69.4 | 139.4 | 1290 | 140.8 | D | 118.6 | 0.22 | s2 | y | n | d1
TN_2019_1741 |  | 72176 20295468 | 591996R | RHOZ1-K 500V 24X2X0.75MM2 | 26.9 | 6 | Vilanova | CUBIERTACPRDMZE | CD | 46 | 18 | No | 2019-11-10 | C_s1_d2 | 1.2 | 17.3 | 40.7 | 1485 | 35.5 | C | 28.7 | 0.07 | s1 | n | y | d2
19110001 |  | 18087 | 581094Z | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 46.2 | 4 | Paron | 14203.27MM+60003.24MM | -- | 34.5 | 21 | No | 2019-11-09 | C_s1_d2 | 1.07 | 17 | 23.2 | 1200 | 32 | C | 14 | 0.04 | s1 | y | y | d2
TN_2019_1742 |  | 83352586 20193656 | 609129X | AFUMEX CLASS 1KV RZ1-K (AS) 3G4MM2 | 12.51 | 12 | Vilanova | 14200.70MM+16021.68MM | CD | 53.6 | 10.1 | No | 2019-11-11 | C_s1_d0 | 1.79 | 29.6 | 42.2 | 1173 | 55.4 | C | 28.5 | 0.05 | s1 | n | n | d0
TN_2019_1743 |  | 83352586 20193656 | 609387C | AFUMEX CLASS 1KV RZ1-K (AS) 3G4MM2 | 12.62 | 12 | Vilanova | 14200.63MM+16021.70MM | CD | 50.9 | 11.1 | No | 2019-11-11 | B2_s1_d0 | 0.81 | 12 | 20.7 | 1053 | 32.1 | B2 | 17.4 | 0.04 | s1 | n | n | d0
TN_2019_1744 |  | 83352586 20193656 | 616875S | AFUMEX CLASS 1KV RZ1-K (AS) 3G4MM2 | 12.24 | 13 | Vilanova | 14200.44MM+16021.72MM | CD | 48.1 | 12.4 | No | 2019-11-11 | D_s1_d2 | 2.61 | 40.5 | 61.2 | 1428 | 75 | D | 24.2 | 0.04 | s1 | n | y | d2
TN_2019_1745 |  | 83352586 20193656 | 609365D | AFUMEX CLASS 1KV RZ1-K (AS) 3G4MM2 | 12.6 | 12 | Vilanova | 14200.66MM+16021.58MM | CD | 45.2 | 13.9 | No | 2019-11-11 | C_s1_d2 | 1.21 | 16.9 | 23.2 | 1059 | 35.1 | C | 18.8 | 0.04 | s1 | n | y | d2
TN_2019_1746 |  |  | 599406D | AFUMEX CLASS 750V H07Z-1-K (AS) 1X70 | 14.14 | 11 | Vilanova |  | CD | 43 | 15.6 | No | 2019-11-11 | B2_s1_d0 | 0.29 | 2.7 | 4.4 | 783 | 15.5 | B2 | 6.3 | 0.01 | s1 | n | n | d0
TN_2019_1747 |  | 73181 20259186 | 586778C | RHOZ1-K 500V 12X2X0.75MM2 | 20.27 | 8 | Vilanova | CUBIERTACPRDMZE | CD | 52.4 | 12.4 | No | 2019-11-12 | D_s1_d2 | 1.54 | 27.7 | 67.8 | 1500 | 56.5 | D | 35.5 | 0.08 | s1 | n | y | d2
19110004 |  | 18095 | -- | FR-N1 X1G1-U- 2*2.5 MM² | 10.6 | 14 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 35.9 | 20.8 | No | 2019-11-16 | B2_s1_d1 | 0.67 | 6.6 | 8.7 | 825 | 35 | B2 | 10 | 0.02 | s1 | y | n | d1
TN_2019_1748 |  | 70233 20286760 | 614000S | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.2 | 8 | Vilanova | COPPERTAPE50%+MICA+LANTOR+1602 | CD | 47.2 | 14.6 | No | 2019-11-12 | D_s2_d2 | 1.77 | 34.5 | 73.4 | 1500 | 72.8 | D | 210.3 | 0.32 | s2 | n | y | d2
TN_2019_1749 |  | 73712 | 610740Y | AL AFUMEX CLASS RZ1 3KV METRO MD L4 500 | 36.65 | 5 | Vilanova | 1420+1602 | CD | 39.4 | 17.1 | No | 2019-11-12 | B2_s1_d0 | 0.57 | 4.2 | 5.9 | 1482 | 13 | B2 | 18.7 | 0.03 | s1 | n | n | d0
TN_2019_1750 |  | 69777 | 599071P | AFUMEX CLASS 1KV RZ1-K (AS) 3X6 | 13.89 | 11 | Vilanova | 1420+1602 | CD | 32.7 | 18.8 | No | 2019-11-12 | C_s1_d2 | 1.12 | 16.9 | 29.2 | 1212 | 32.1 | C | 31.4 | 0.07 | s1 | n | y | d2
TN_2019_1751 |  | 72836 20281143 | 601915F | RZ1KZ1MZ1-K ATEX 2RH 1KV 3X150 | 61.29 | 3 | Vilanova | PENDINGTOCONFIRM | CD | 59.9 | 12.6 | No | 2019-11-13 | B2_s1_d0 | 0.46 | 4.1 | 5 | 552 | 19.9 | B2 | 5.9 | 0.01 | s1 | n | n | d0
TN_2019_1752 |  |  | 613355R | CCTSST FR 0.3 4X1.4 | 16.26 | 9 | Vilanova | CUBIERTAMEGOLON | CD | 60 | 13 | No | 2019-11-13 | B2_s1_d2 | 0.79 | 14.9 | 24.5 | 1125 | 30.3 | B2 | 23.2 | 0.06 | s1 | n | y | d2
TN_2019_1753 |  | 73707 20310601 | 598423K | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 9.26 | 17 | Vilanova | SXLPE+CPR+16GA1.49MM | CD | 78.7 | 15.4 | No | 2019-11-14 | D_s1_d2 | 2.42 | 32.2 | 48.5 | 813 | 94.9 | D | 15.7 | 0.02 | s1 | n | y | d2
TN_2019_1754 |  | 73777 | I26702 | FG16OR16 5G1.5 MM² - 0.6/1 KV | 11.33 | 14 | Vilanova | 05AM+54AB0.4+1.4 | CD | 76.6 | 16.3 | No | 2019-11-14 | C_s2_d1 | 1.37 | 17.2 | 34.2 | 828 | 87 | C | 357.2 | 0.81 | s2 | y | n | d1
TN_2019_1755 |  | 73779 | D46687 | FG16OR16 5G1.5 MM² - 0.6/1 KV | 11.36 | 14 | Vilanova | 05AM+20AH0.4+1.4 | CD | 80 | 16.1 | No | 2019-11-14 | C_s2_d1 | 1.77 | 23.6 | 41.5 | 888 | 86.2 | C | 352.4 | 0.58 | s2 | y | n | d1
TN_2019_1756 |  | 73706 20310601 | 609388D | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 9.16 | 17 | Vilanova | SXLPE+CPR+16021.41MM | CD | 65.4 | 11.3 | No | 2019-11-18 | D_s2_d2 | 2.61 | 35 | 52.3 | 756 | 116.4 | D | 54.7 | 0.08 | s2 | n | y | d2
TN_2019_1757 |  | 73706 20310601 | 609381W | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 9.29 | 17 | Vilanova | SXLPE+CPR+16FA1.50MM | CD | 63.9 | 12.1 | No | 2019-11-18 | D_s2_d2 | 3.3 | 68.8 | 132.2 | 1170 | 152.5 | D | 67.2 | 0.12 | s2 | n | y | d2
TN_2019_1758 |  | 73707 20310601 | 609377S | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 9.41 | 17 | Vilanova | SXLPE+CPR+14200.28MM+16FA1.46MM | CD | 58.2 | 13.8 | No | 2019-11-18 | D_s1_d2 | 3.3 | 57.6 | 149 | 1443 | 130.4 | D | 40.8 | 0.13 | s1 | n | y | d2
TN_2019_1759 |  | 73707 20310601 | 609353R | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 9.44 | 17 | Vilanova | SXLPE+14200.31MM+16GA1.51MM | CD | 57.7 | 14.6 | No | 2019-11-18 | C_s1_d2 | 1.78 | 20.2 | 31.4 | 903 | 62.9 | C | 31.2 | 0.04 | s1 | n | y | d2
TN_2019_1760 |  | 73707 20310601 | 609386B | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 9.52 | 15 | Vilanova | SXLPE+CPR+14200.21MM+16021.44MM | CD | 51.3 | 16.2 | No | 2019-11-18 | D_s1_d2 | 3.3 | 47.6 | 84.6 | 1461 | 93.7 | D | 44.2 | 0.09 | s1 | n | y | d2
TN_2019_1763 |  | 72835 20281142 | 619287N | RZ1KZ1MZ1-K ATEX 2RH 1KV 3X50 | 39.4 | 5 | Vilanova | AISLAMIENTOXLPE+1602SEES+6010SEES+GFR380 | CD | 55.8 | 8.7 | No | 2019-11-19 | B2_s1_d2 | 0.63 | 6.8 | 12.9 | 1500 | 24.5 | B2 | 11.9 | 0.03 | s1 | n | y | d2
TN_2019_1764 |  | 72834 20307483 | 623480W | RZ1KZ1MZ1-K ATEX 2RH 1KV 3X2.5 | 18.31 | 8 | Vilanova | AISLAMIENTOXLPE+1602SEES+6010SEES+GFR380 | CD | 54.9 | 9 | No | 2019-11-19 | B2_s1_d1 | 1.06 | 14.3 | 20.9 | 1095 | 31 | B2 | 9.9 | 0.02 | s1 | y | n | d1
TN_2019_1765 |  | 70345 | 623376H | AFUMEX CLASS O 1Z1C7Z1-K 2X16 | 22.2 | 7 | Vilanova | PENDINGTOCONFIRM | CD | 50.9 | 10.6 | No | 2019-11-19 | B2_s1_d2 | 0.51 | 6.6 | 10.8 | 1059 | 15.3 | B2 | 8.3 | 0.02 | s1 | n | y | d2
TN_2019_1766 |  | 70345 | 623371C | AFUMEX CLASS O 1Z1C7Z1-K 2X16 | 22.31 | 7 | Vilanova | PENDINGTOCONFIRM | CD | 48.7 | 12 | No | 2019-11-19 | B2_s1_d2 | 0.67 | 8.9 | 13 | 1182 | 24.1 | B2 | 8.6 | 0.02 | s1 | n | y | d2
TN_2019_1767 |  | 70345 | 608264G | AFUMEX CLASS O 1Z1C7Z1-K 2X16 | 22.37 | 7 | Vilanova | PENDINGTOCONFIRM | CD | 43.8 | 14.1 | No | 2019-11-19 | B2_s1_d2 | 0.64 | 8.2 | 12.7 | 1047 | 19.2 | B2 | 4.6 | 0.01 | s1 | n | y | d2
TN_2019_1768 |  | 83350207 | 613365B | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 11.33 | 14 | Vilanova | 14200.53MM+16021.59MM | CD | 53.2 | 12 | No | 2019-11-20 | D_s1_d2 | 2.64 | 42.1 | 61.9 | 1500 | 80.9 | D | 33.3 | 0.05 | s1 | n | y | d2
TN_2019_1769 |  | 83350207 | 613364A | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 11.55 | 13 | Vilanova | 14200.63MM+16021.43MM | CD | 52.2 | 15.2 | No | 2019-11-20 | D_s1_d1 | 1.85 | 30.9 | 41.9 | 1284 | 65.3 | D | 46.5 | 0.1 | s1 | y | n | d1
TN_2019_1770 |  | 83350207 | 615742K | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 11.5 | 13 | Vilanova | 14200.48MM+16021.56MM | CD | 65.6 | 11.6 | No | 2019-11-21 | C_s1_d1 | 1.1 | 18 | 28.8 | 924 | 46.3 | C | 34.1 | 0.08 | s1 | y | n | d1
TN_2019_1771 |  | 74135 | 619396G | LXHIOZ1 (CBE. FRT) 15 KV 1X120 | 34.5 | 5 | Vilanova | 14201.84MM+60001.79MM | CD | 64.4 | 11.5 | No | 2019-11-21 | C_s1_d2 | 1.32 | 26.3 | 33.1 | 891 | 64.4 | C | 17.9 | 0.06 | s1 | n | y | d2
TN_2019_1772 |  | 83352586 20193656 | 609129X | AFUMEX CLASS 1KV RZ1-K (AS) 3G4MM2 | 12.51 | 12 | Vilanova | 14200.70MM+16021.68MM | CD | 61.3 | 13.4 | No | 2019-11-21 | C_s1_d1 | 1.78 | 26.3 | 39.3 | 1077 | 52.8 | C | 25.5 | 0.05 | s1 | y | n | d1
TN_2019_1773 |  | 74133 | 619208C | LXHIOZ1 (CBE. FRT) 15 KV 1X120 | 34.78 | 5 | Vilanova | 14202.12MM+60001.85MM | CD | 58.2 | 15 | No | 2019-11-21 | C_s1_d2 | 0.85 | 17.2 | 23.7 | 900 | 45.4 | C | 14.5 | 0.03 | s1 | n | y | d2
TN_2019_1774 |  | 83352586 20193656 | 616875S | AFUMEX CLASS 1KV RZ1-K (AS) 3G4MM2 | 12.24 | 13 | Vilanova | 14200.44MM+16021.72MM | CD | 50.4 | 16.7 | No | 2019-11-21 | D_s1_d1 | 2.12 | 30.8 | 43.2 | 1347 | 61.5 | D | 29.6 | 0.04 | s1 | y | n | d1
TN_2019_1775 |  | 20184146 | PG153333DBM | RTE S740 4X10MM² | 21.6 | 7 | Vilanova | 4300IPFR+1200FPFR+4300IPFR+2800SPFR | CD | 73.4 | 12.1 | No | 2019-11-22 | B2_s3_d1 | 0.77 | 11.1 | 16.1 | 876 | 46.2 | B2 | 602.4 | 0.96 | s3 | y | n | d1
TN_2019_1776 |  | 83352586 20193656 | 609365D | AFUMEX CLASS 1KV RZ1-K (AS) 3G4MM2 | 12.6 | 12 | Vilanova | 14200.66MM+16021.58MM | CD | 74.2 | 12.4 | No | 2019-11-22 | B2_s2_d2 | 0.78 | 14.3 | 23 | 924 | 42.2 | B2 | 57.6 | 0.11 | s2 | n | y | d2
TN_2019_1777 |  | 83352586 20193656 | 609387C | AFUMEX CLASS 1KV RZ1-K (AS) 3G4MM2 | 12.62 | 12 | Vilanova | 14200.63MM+16021.70MM | CD | 75.7 | 13.1 | No | 2019-11-22 | D_s2_d2 | 1.88 | 30.9 | 45.4 | 1365 | 55.8 | D | 54.2 | 0.08 | s2 | n | y | d2
TN_2019_1778 |  | 72834 20307483 | 623480W | RZ1KZ1MZ1-K ATEX 2RH 1KV 3X2.5 | 18.31 | 8 | Vilanova | AISLAMIENTOXLPE+1602SEES+6010SEES+GFR380 | CD | 63.3 | 11.8 | No | 2019-11-25 | C_s1_d2 | 0.97 | 15.7 | 25.3 | 1362 | 27.1 | C | 11.3 | 0.03 | s1 | n | y | d2
TN_2019_1779 |  | 83352586 20193656 | 609365D | AFUMEX CLASS 1KV RZ1-K (AS) 3G4MM2 | 12.6 | 12 | Vilanova | 14200.66MM+16021.58MM | CD | 59.9 | 14.8 | No | 2019-11-25 | C_s1_d1 | 2 | 28.7 | 43.1 | 1065 | 64.6 | C | 20.8 | 0.05 | s1 | y | n | d1
TN_2019_1780 |  | 83352586 20193656 | 609387C | AFUMEX CLASS 1KV RZ1-K (AS) 3G4MM2 | 12.62 | 12 | Vilanova | 14200.63MM+16021.70MM | CD | 53.2 | 17.2 | No | 2019-11-25 | D_s1_d1 | 2.17 | 35.1 | 56.3 | 1368 | 58.3 | D | 17.5 | 0.03 | s1 | y | n | d1
TN_2019_1781 |  |  | Sample 90 | TEST SAMPLE 90 PBT-FR + GEL FR (AFO386 A) | 11.19 | 14 | Vilanova | AFUMEXCPR | CD | 71.3 | 14 | No | 2019-10-26 | D_s1_d2 | 1.99 | 30.8 | 47.7 | 900 | 97.1 | D | 31.3 | 0.04 | s1 | n | y | d2
TN_2019_1782 |  |  | Sample 91 | TEST SAMPLE 91 PBT-FR + GEL FR (AFO386 B) | 10.78 | 14 | Vilanova | AFUMEXCPR | CD | 63.8 | 16.8 | No | 2019-11-26 | D_s1_d1 | 2.87 | 47.9 | 69.5 | 792 | 153 | D | 32.5 | 0.05 | s1 | y | n | d1
TN_2019_1783 |  |  | Sample 92 | TEST SAMPLE 92 PBT-FR + GEL FR (AFO387 A) | 12.58 | 12 | Vilanova | AFUMEXCPR | CD | 54.8 | 19.5 | No | 2019-11-26 | C_s2_d2 | 1.89 | 29.7 | 48.6 | 816 | 107.1 | C | 57.1 | 0.1 | s2 | n | y | d2
TN_2019_1784 |  |  | Sample 93 | TEST SAMPLE 93 PBT-FR + GEL FR (AFO387 B) | 12.41 | 13 | Vilanova | AFUMEXCPR | CD | 55.8 | 16.1 | No | 2019-11-26 | D_s2_d2 | 1.91 | 33.3 | 53.7 | 834 | 116.7 | D | 63.7 | 0.11 | s2 | n | y | d2
TN_2019_1785 |  | 72835 20281142 | 619287N | RZ1KZ1MZ1-K ATEX 2RH 1KV 3X50 | 39.4 | 5 | Vilanova | AISLAMIENTOXLPE+1602SEES+6010SEES+GFR380 | CD | 47.7 | 17.7 | No | 2019-11-27 | B2_s1_d2 | 0.58 | 7.1 | 11.5 | 1497 | 24.6 | B2 | 10.1 | 0.02 | s1 | n | y | d2
TN_2019_1786 |  | 73777 | I26702 | FG16OR16 5G1.5 MM² - 0.6/1 KV | 11.33 | 14 | Vilanova | 05AM+54AB0.4+1.4 | CD | 44 | 19.3 | No | 2019-11-27 | C_s2_d1 | 1.43 | 17.6 | 36.7 | 882 | 96 | C | 300.8 | 0.67 | s2 | y | n | d1
TN_2019_1787 |  | 73779 | D46687 | FG16OR16 5G1.5 MM² - 0.6/1 KV | 11.36 | 14 | Vilanova | 05AM+20AH0.4+1.4 | CD | 40.6 | 20.4 | No | 2019-11-27 | D_s3_d2 | 3.3 | 68.3 | 175.9 | 1284 | 178.7 | D | 970.1 | 1.72 | s3 | n | y | d2
19110005 |  | 18102 | -- | K25 750V 1X1 -SH-NF F 55-625-255 | 3 | 165 | Paron | 16GASEES | -- | 45.5 | 22.2 | No | 2019-11-28 | B2_s1_d0 | 0.9 | 9.6 | 20.6 | 639 | 84 | B2 | 20 | 0.05 | s1 | n | n | d0
19110006 |  | 18116 | -- | RED ELEC RHZ1-RA-2OL (AS) 1X2000MM2 127/220KV +T375AL | 120.6 | 2 | Paron | XLPE+TUBEAL+60ACESNATUREL+SKINSC | -- | 42.9 | 23.2 | No | 2019-11-28 | B2_s1_d1 | 0.77 | 5.3 | 8.1 | 768 | 20 | B2 | 6 | 0.01 | s1 | y | n | d1
19110007 |  | 18102 | -- | K25 750V 1X1 -SH-NF F 55-625-255 | 2.9 | 165 | Paron | 16FASEES | -- | 45.4 | 22.3 | No | 2019-11-28 | B2_s1_d0 | 0.87 | 9.5 | 19.1 | 591 | 85 | B2 | 22 | 0.05 | s1 | n | n | d0
19110008 |  | 18102 | -- | K25 750V 1X1 -SH-NF F 55-625-255 | 3 | 165 | Paron | 1602SEES | -- | 45.5 | 23.2 | No | 2019-11-28 | B2_s1_d0 | 0.83 | 8.1 | 16.5 | 546 | 77 | B2 | 23 | 0.06 | s1 | n | n | d0
19110009 |  | 18116 | -- | RED ELEC RHZ1-RA-2OL (AS) 1X2000MM2 127/220KV +T375AL | 120.6 | 2 | Paron | XLPE+TUBEAL+60ACESNATUREL+SKINSC | -- | 37.1 | 22.2 | No | 2019-11-30 | B2_s1_d2 | 0.72 | 4.7 | 7.9 | 786 | 20 | B2 | 5 | 0.01 | s1 | y | y | d2
19110010 |  | 18011 | -- | PESS 1043 -01-1.2-NF F 55-623-PRYSMIAN 255 | 12.8 | 12 | Paron | IX1400FR+3000GV+5300SEIT | -- | 35.4 | 21.9 | No | 2019-11-30 | B2_s1_d2 | 0.67 | 9.4 | 18 | 918 | 35 | B2 | 11 | 0.03 | s1 | y | y | d2
19110011 |  | 18116 | -- | RED ELEC RHZ1-RA-2OL (AS) 1X2000MM2 127/220KV +T375AL | 120.6 | 2 | Paron | XLPE+TUBEAL+60ACESNATUREL+SKINSC | -- | 35.4 | 21.8 | No | 2019-11-30 | B2_s1_d2 | 0.62 | 7.6 | 10.8 | 756 | 31 | B2 | 7 | 0.01 | s1 | y | y | d2
TN_2019_1788 |  |  |  | NEXANS AL SECURE RZ1-K (AS) 1KV 5G1.5 | 11.41 | 14 | Vilanova | COMPETITORSAMPLE | CD | 50.7 | 18.3 | No | 2019-11-28 | E ou F_s2_d2 | 3.3 | 73.8 | 158 | 1263 | 165.5 | E ou F | 74.7 | 0.19 | s2 | n | y | d2
TN_2019_1789 |  | 83400283 20229626 | 601897L | AL-HEPRZ1(AS) 1X400MM2 18/30KV | 50.1 | 4 | Vilanova | 14202.5MM+16022.6MM | CD | 46.7 | 22 | No | 2019-11-28 | C_s1_d2 | 0.92 | 25.1 | 35.7 | 1266 | 42.4 | C | 9 | 0.03 | s1 | n | y | d2
TN_2019_1790 |  |  |  | NEXANS AL SECURE RZ1-K (AS) 1KV 1X150 | 23.16 | 7 | Vilanova | COMPETITORSAMPLE | CD | 43.8 | 21.4 | No | 2019-12-02 | B2_s1_d0 | 0.51 | 6.1 | 11.7 | 1500 | 28.9 | B2 | 3.1 | 0.01 | s1 | n | n | d0
TN_2019_1791 |  | 74561 20319530 | 530428C | ROZ1-K 500V 1X2X0.75 | 8.18 | 19 | Vilanova |  | CD | 71.2 | 13.1 | No | 2019-12-02 | D_s2_d2 | 3.3 | 65.4 | 178.7 | 999 | 255.7 | D | 75.3 | 0.11 | s2 | n | y | d2
TN_2019_1792 |  | 74562 20319529 | 591241D | ROZ1-K 500V 1X3X0.75 | 8.69 | 17 | Vilanova |  | CD | 69.6 | 14.2 | No | 2019-12-02 | E ou F_s1_d2 | 3.3 | 71.4 | 204.6 | 1053 | 271.6 | E ou F | 43.2 | 0.1 | s1 | n | y | d2
TN_2019_1793 |  | 71440 20226012 | 634822Z | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 41.06 | 5 | Vilanova | 14203.69MM+16023.41MM | CD | 59.5 | 16.7 | No | 2019-12-02 | D_s1_d2 | 1.72 | 44 | 78.6 | 1479 | 70.3 | D | 3.7 | 0.01 | s1 | n | y | d2
TN_2019_1794 |  |  | 609153Y | AL-HEPRZ1(AS) 1X240MM2 12/20KV | 43.41 | 5 | Vilanova | 14203.19MM+16023.19MM | CD | 65.3 | 10.9 | No | 2019-12-03 | D_s1_d2 | 1.4 | 32.1 | 53 | 1500 | 52.6 | D | 6.7 | 0.02 | s1 | n | y | d2
TN_2019_1795 |  | 83255629 |  | FG16OM16 7G1.5 MM² - 0.6/1 KV | 14.91 | 10 | Vilanova | IZ1000INSULATION.0300FDITFILLERAND5300SEITSHEATHING | CD | 64.1 | 10.9 | No | 2019-12-03 | B2_s1_d1 | 0.65 | 10.1 | 14.5 | 1149 | 31.1 | B2 | 10.8 | 0.02 | s1 | y | n | d1
TN_2019_1796 |  |  |  | NEXANS AL SECURE RZ1-K (AS) 1KV 3G2.5 | 11.17 | 14 | Vilanova | COMPETITORSAMPLE | CD | 63.3 | 11.7 | No | 2019-12-03 | E ou F_s1_d2 | 3.3 | 70.3 | 195.6 | 1425 | 176.8 | E ou F | 46.1 | 0.18 | s1 | n | y | d2
1912001 |  | 18116 | -- | RED ELEC RHZ1-RA-2OL (AS) 1X2000MM2 127/220KV +T375AL | 120.6 | 2 | Paron | XLPE+TUBEAL+60ACESNATUREL+SKINSC | -- | 34.9 | 21.3 | No | 2019-12-03 | B2_s1_d2 | 0.77 | 4.3 | 7.5 | 705 | 20 | B2 | 7 | 0.01 | s1 | y | y | d2
1912002 |  | 18113 | -- | GENERAL CABLE 7 CEBEC 1077 -XGB-CCA-S1B.D2.A1 0.6/1 KV 3G50 19.10.22 | 26.5 | 6 | Paron | SXLPE+BEDDING+LSOH | -- | 34.6 | 21 | No | 2019-12-03 | B2_s1_d0 | 0.47 | 3.1 | 4.7 | 651 | 15 | B2 | 6 | 0.01 | s1 | n | n | d0
1912003 |  | 18113 | -- | GENERAL CABLE 7 CEBEC 1077 -XGB-CCA-S1B.D2.A1 0.6/1 KV 3*70+1*35 19.10.22 | 35 | 5 | Paron | SXLPE+BEDDING+LSOH | -- | 33.9 | 20.6 | No | 2019-12-03 | C_s1_d2 | 0.77 | 9.7 | 30.2 | 1500 | 25 | C | 15 | 0.06 | s1 | y | y | d2
TN_2019_1797 |  | 72836 20281143 | 601915F | AFUMEX ATEX RZ1KZ1MZ1-K 2RH 1KV 3X150/70 UIC 895-O R | 61.29 | 3 | Vilanova | PENDINGTOCONFIRM | CD | 72.5 | 15.1 | No | 2019-12-04 | B2_s1_d0 | 0.6 | 4.7 | 6.3 | 642 | 20.4 | B2 | 8.7 | 0.01 | s1 | n | n | d0
TN_2019_1798 |  | 72835 20281142 | 619287N | AFUMEX ATEX RZ1KZ1MZ1-K 2RH 1KV 3X50/25 UIC 895-O R | 39.4 | 5 | Vilanova | AISLAMIENTOXLPE+1602SEES+6010SEES+GFR380 | CD | 74.8 | 15.1 | No | 2019-12-04 | B2_s1_d1 | 0.72 | 6.4 | 10.8 | 1500 | 26.3 | B2 | 5 | 0.01 | s1 | y | n | d1
TN_2019_1799 |  | 72834 20307483 | 623480W | RZ1KZ1MZ1-K ATEX 2RH 1KV 3X2.5 | 18.31 | 8 | Vilanova | AISLAMIENTOXLPE+1602SEES+6010SEES+GFR380 | CD | 75.5 | 14.8 | No | 2019-12-04 | C_s1_d2 | 1.24 | 19.2 | 31.4 | 1500 | 42.1 | C | 15.5 | 0.03 | s1 | n | y | d2
TN_2019_1800 |  | 73176 20295468 | 591996R | RHOZ1-K 500V 24X2X0.75MM2 | 26.9 | 6 | Vilanova | CUBIERTACPRDMZE | CD | 76.4 | 15.1 | No | 2019-12-04 | B2_s1_d0 | 0.78 | 13.4 | 29.2 | 1416 | 31.4 | B2 | 7.5 | 0.03 | s1 | n | n | d0
TN_2019_1801 |  | 73180 20089252 | 586797Y | RHOZ1-K 500V 2X2X0.75MM2 | 12.62 | 12 | Vilanova | CUBIERTACPRDMZE | CD | 76.5 | 15.2 | No | 2019-12-04 | C_s1_d0 | 1.41 | 21.4 | 36.6 | 921 | 80 | C | 28.1 | 0.05 | s1 | n | n | d0
TN_2019_1803 |  | 72834 20307483 | 623480W | AFUMEX ATEXRZ1KZ1MZ1-K 2RH 1KV 3X2.5/2.5 UIC 895-O R | 18.31 | 8 | Vilanova | AISLAMIENTOXLPE+1602SEES+6010SEES+GFR380 | CD | 78.3 | 14.2 | No | 2019-12-05 | C_s1_d1 | 1.24 | 19.4 | 36.8 | 1230 | 39.6 | C | 40.8 | 0.06 | s1 | y | n | d1
TN_2019_1804 |  | 73181 20259186 | 591256U | RHOZ1-K 500V 12X2X0.75MM2 | 20.14 | 8 | Vilanova | CUBIERTACPRDMZE | CD | 77.9 | 14.4 | No | 2019-12-05 | C_s1_d2 | 1.77 | 23.7 | 45.3 | 1500 | 66.9 | C | 22.5 | 0.05 | s1 | n | y | d2
TN_2019_1805 |  | 20316297 | 5096833 | H07Z1-K TYPE2 (AS) <HAR> AENOR 1X10 | 5.91 | 25 | Vilanova | 1602+TPR27 | CD | 75.6 | 15.1 | No | 2019-12-05 | B2_s1_d0 | 0.71 | 4 | 14 | 522 | 64.4 | B2 | 7.7 | 0.03 | s1 | n | n | d0
TN_2019_1806 |  | 20316300 | 5096835 | H07Z1-K TYPE2 (AS) <HAR> AENOR 1X25 | 8.56 | 17 | Vilanova | 1602+TPR27 | CD | 77.1 | 15.1 | No | 2019-12-05 | B2_s1_d0 | 0.41 | 2.9 | 7.4 | 588 | 36.1 | B2 | 3.1 | 0.01 | s1 | n | n | d0
19120004 |  | 18126 | -- | 750-1X35MM²-SH-NF F 55-625-255-ESS-923AA | 12 | 13 | Paron | ID3100FR/SV3300FR+SV3200FR | -- | 35.7 | 19 | No | 2019-12-06 | D_s2_d2 | 2.6 | 33.6 | 50.4 | 795 | 103 | D | 134 | 0.19 | s2 | y | y | d2
19120005 |  | 18126 | -- | 750-1X400MM²-SH-NF F 55-625-255-ESS-923AA | 33 | 6 | Paron | ID3100FR/SV3300FR+SV3200FR | -- | 38.1 | 18.2 | No | 2019-12-06 | B2_s1_d1 | 0.4 | 5 | 8.6 | 861 | 18 | B2 | 10 | 0.02 | s1 | y | n | d1
TN_2019_1807 |  | 20173170 83326179 | 499461T | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.53 | 3 | Vilanova |  | CD | 69.6 | 10.5 | No | 2019-12-08 | C_s1_d2 | 1.15 | 25.6 | 42.5 | 1497 | 40.4 | C | 8.6 | 0.01 | s1 | n | y | d2
TN_2019_1808 |  | 83266926 20194004 |  | AFUMEX CLASS 750V HO7Z1-K (AS) TYPE2 1X16 | 7 | 21 | Vilanova |  | CD | 55 | 14.4 | No | 2019-12-08 | B2_s1_d0 | 0.31 | 2.9 | 7.8 | 528 | 44 | B2 | 1.1 | 0 | s1 | n | n | d0
TN_2019_1809 |  | 83266861 20194000 |  | AFUMEX CLASS 750V HO7Z1-K (AS) TYPE2 1X10 | 6.07 | 25 | Vilanova |  | CD | 61.9 | 16.2 | No | 2019-12-08 | B2_s1_d0 | 0.57 | 5.4 | 12 | 558 | 66.9 | B2 | 1.3 | 0.01 | s1 | n | n | d0
TN_2019_1810 |  | 83339155 20193994 |  | AFUMEX CLASS 750V HO7Z1-K (AS) TYPE2 1X6 | 4.55 | 60 | Vilanova |  | CD | 60.2 | 12.3 | No | 2019-12-09 | B2_s1_d1 | 1.08 | 9 | 26.8 | 669 | 85.3 | B2 | 19.5 | 0.1 | s1 | y | n | d1
TN_2019_1811 |  | 83386693 20193682 | 625341U | AFUMEX CLASS RZ1-K (AS) 1KV 5G16 | 22.02 | 7 | Vilanova | 14200.63MM+16021.8MM | CD | 51.6 | 14.5 | No | 2019-12-09 | B2_s1_d0 | 0.77 | 9.3 | 20.6 | 1497 | 24.8 | B2 | 8.4 | 0.01 | s1 | n | n | d0
CEL-0201_20-1 |  | 83386693 20193682 | 625341U | AFUMEX CLASS RZ1-K (AS) 1KV 5G16 | 22.02 | 7 | CEIS | 14200.63MM+16021.8MM | CD | 70 | 18.39 | No | 2020-04-22 | B2_s1_d0 | 0.8 | 11 | 19.8 | 1500 | 31.3 | B2 | 14.7 | 0.03 | s1 | n | n | d0
TN_2019_1812 |  | 83336308 20193680 | 620551M | AFUMEX CLASS RZ1-K (AS) 1KV 5G6 | 16 | 9 | Vilanova | 14200.63MM+16021.61MM | CD | 47.6 | 17.5 | No | 2019-12-09 | C_s1_d2 | 0.93 | 17.9 | 31.6 | 1176 | 36.1 | C | 14.4 | 0.03 | s1 | n | y | d2
TN_2019_1813 |  | 83170703 20193655 | 578250H | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 | 11.34 | 14 | Vilanova | 14200.64MM+16021.64MM | CD | 42.5 | 19.2 | No | 2019-12-09 | D_s1_d2 | 2.53 | 44.9 | 64 | 1245 | 89.9 | D | 32.4 | 0.06 | s1 | n | y | d2
19120006 |  | 18112 | -- | AFUMEX TECNUC-PESS1097-PRYSMIAN-1P0.50MM²-CU CL.5-BLG-LSOH-0.3/0.5(0.6)- | 8.3 | 19 | Paron | IX2100FR+RUBANVERRE+SW3100FR | -- | 38.9 | 21.9 | No | 2019-12-09 | D_s2_d2 | 2.75 | 27 | 37.7 | 966 | 71 | D | 174 | 0.25 | s2 | y | y | d2
19120007 |  | 18112 | -- | AFUMEX TECNUC-PESS1097-PRYSMIAN-6P0.50MM²-CU CL.5-BLG-LSOH-0.3/0.5(0.6) | 15.6 | 9 | Paron | IX2100FR+RUBANVERRE+SW3100FR | -- | 39.6 | 22 | No | 2019-12-09 | B2_s1_d2 | 0.77 | 10.5 | 16.3 | 1050 | 23 | B2 | 44 | 0.09 | s1 | y | y | d2
19120008 |  | 18112 | -- | AFUMEX TECNUC-PESS1098-PRYSMIAN-12P0.50MM²-CU CL.5-BLG-LSOH-0.3/0.5(0.6) | 20.1 | 8 | Paron | IX2100FR+RUBANVERRE+SW3100FR | -- | 38.4 | 21.9 | No | 2019-12-09 | B2_s1_d2 | 0.57 | 8.7 | 25.8 | 1500 | 22 | B2 | 48 | 0.14 | s1 | y | y | d2
19120009 |  | 18112 | -- | AFUMEX TECNUC-PK3SG468-PRYSMIAN-48*0.50²-CU CL.2-BLG-LSOH-0.6/1 (1.2) | 26.5 | 6 | Paron | IX2100FR+RUBANVERRE+SW3100FR | -- | 38 | 22 | No | 2019-12-09 | B2_s1_d2 | 0.47 | 2.5 | 5.6 | 1464 | 5 | B2 | 13 | 0.04 | s1 | y | y | d2
TN_2019_1814 |  | 83379119 20193644 | 635549P | AFUMEX CLASS RZ1-K (AS) 1KV 1X185 | 23.74 | 7 | Vilanova | 14200.43MM+16021.61MM | CD | 58.7 | 10.8 | No | 2019-12-10 | B2_s1_d2 | 0.56 | 7.1 | 17.4 | 1500 | 27.1 | B2 | 5.3 | 0.01 | s1 | n | y | d2
TN_2019_1815 |  | 83333403 20193654 | 626795Z | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.6 | 14 | Vilanova | 14200.64MM+16021.58MM | CD | 54.6 | 13 | No | 2019-12-10 | D_s1_d1 | 3.3 | 44.3 | 58.7 | 1449 | 87.3 | D | 29.8 | 0.05 | s1 | y | n | d1
TN_2019_1816 |  | 83179919 20193643 | 555529L | AFUMEX CLASS RZ1-K (AS) 1KV 1X150 | 22.04 | 7 | Vilanova | 14200.31MM+16021.61MM | CD | 50.2 | 15.1 | No | 2019-12-10 | B2_s1_d0 | 0.55 | 9.2 | 17.7 | 1500 | 24.1 | B2 | 6.8 | 0.01 | s1 | n | n | d0
TN_2019_1817 |  | 83266555 20193641 | 610144A | AFUMEX CLASS RZ1-K (AS) 1KV 1X95 | 17.91 | 8 | Vilanova | 14200.31MM+16021.51MM | CD | 46.8 | 16.3 | No | 2019-12-10 | B2_s1_d0 | 0.25 | 8.2 | 11.3 | 1500 | 36.4 | B2 | 2.1 | 0 | s1 | n | n | d0
CEL-0200_20-1 |  | 83266555 20193641 | 610144A | AFUMEX CLASS RZ1-K (AS) 1KV 1X95 | 18 | 8 | CEIS | 14200.31MM+16021.51MM | CD | 70 | 17.92 | No | 2020-04-22 | C_s1_d2 | 1.1 | 20.2 | 33.8 | 1470 | 36.9 | C | 15.5 | 0.03 | s1 | n | y | d2
|  | 83335199 | --- | EXZH H07Z1-K (AS) 1X1.5 | 2.93 | 165 | Manlleu |  | -- | 27 | 22.5 | No | 2019-12-10 | C_s1_d2 | 1.78 | 18.3 | 35.9 | 795 | 86.2 | C | 31.4 | 0.1 | s1 | y | y | d2
|  | 83349227 | --- | AFUMEX 750V HO7Z1-K (AS) 1X2.5 | 3.66 | 105 | Manlleu |  | -- | 27 | 24.3 | No | 2019-12-10 | C_s1_d0 | 1.58 | 24.4 | 47.3 | 642 | 163.9 | C | 35 | 0.1 | s1 | n | n | d0
TN_2019_1818 |  | 83266564 20193645 | 619105R | AFUMEX CLASS 1KV RZ1-K (AS) 1X240MM2 | 27.3 | 6 | Vilanova | 14200.31MM+16021.51MM | -- | 65 | 10.9 | No | 2019-12-11 | B2_s1_d2 | 0.71 | 8.4 | 18.2 | 1493 | 24.1 | B2 | 3.7 | 0.01 | s1 | n | y | d2
TN_2019_1819 |  | 20173170 83326179 | 499461T | RED ELEC PRYSMIAN RHZ1-RA-2OL (AS) 66KV 1X1000K AL +H135 | 76.53 | 3 | Vilanova |  | CD | 61.6 | 12.2 | No | 2019-12-11 | C_s1_d2 | 1.19 | 26.9 | 54.9 | 1476 | 47.2 | C | 11.3 | 0.02 | s1 | n | y | d2
|  | 83388959 |  | AFUMEX 750V HO7Z1-K (AS) 1X1.5 | 2.97 | 165 | Manlleu |  |  | 26 | 20.5 | No | 2019-12-10 | C_s1_d0 | 1.78 | 21.4 | 50.6 | 651 | 179.7 | C | 37.9 | 0.13 | s1 | n | n | d0
|  | 83333170 |  | AFUMEX 750V HO7Z1-K (AS) 1X6 | 4.62 | 60 | Manlleu |  |  | 28 | 23.7 | No | 2019-12-10 | B2_s1_d0 | 1.2 | 10.5 | 29 | 687 | 91.9 | B2 | 29.8 | 0.17 | s1 | n | n | d0
|  | 83387103 |  | EXZH H07Z1-K (AS) 1X1.5 | 2.92 | 165 | Manlleu |  |  | 25 | 22.7 | No | 2019-12-10 | D_s1_d0 | 3.3 | 50.6 | 78 | 798 | 179.1 | D | 27.4 | 0.06 | s1 | n | n | d0
|  | 83452737 |  | EXZH H07Z1-K (AS) 1X2.5 | 3.47 | 120 | Manlleu |  |  | 28 | 23.4 | No | 2019-12-12 | D_s1_d0 | 3.3 | 46.4 | 70.1 | 864 | 150.9 | D | 38.9 | 0.09 | s1 | n | n | d0
|  | 83224342 |  | EXZH RZ1-K 1KV 1X240 COMPACT | 25.9 | 6 | Manlleu |  |  | 28 | 21.7 | No | 2019-12-12 | C_s1_d2 | 0.88 | 20 | 49.3 | 1500 | 41.1 | C | 4.9 | 0.02 | s1 | y | y | d2
|  | --- | 12T9357 | EXZH RZ1-K 1KV 3X2.5 COMPACT | 10.5 | 14 | Manlleu |  |  | 28 | 22.1 | No | 2019-12-12 | C_s1_d1 | 1.83 | 21 | 30.3 | 1242 | 48.4 | C | 15.4 | 0.04 | s1 | y | n | d1
TN_2019_1820 |  |  | 596750S | AFUMEX CLASS HAZ H07Z1-K (AS) 3G16+1X1.5 | 14.02 | 11 | Vilanova |  | CD | 52.7 | 15.1 | No | 2019-12-11 | B2_s1_d0 | 0.32 | 5.3 | 7 | 687 | 27.4 | B2 | 0.5 | 0 | s1 | n | n | d0
TN_2019_1821 |  | 83386713 20193680 | 635033D | AFUMEX CLASS 1KV RZ1-K (AS) 5G10 | 19.31 | 8 | Vilanova | 14200.45MM+16021.57MM | CD | 50.2 | 17 | No | 2019-12-11 | C_s1_d2 | 0.91 | 15.9 | 39.7 | 1500 | 34.7 | C | 10.6 | 0.02 | s1 | n | y | d2
19120010 | 20319461 | 18140 | -- | ARG18OM16NM16 3X16 804/125 | 31.3 | 6 | Paron | ID7600+0400FEIT+5300SEIT+GTI1230+GST+LANTOR+5300SEIT | -- | 32.2 | 21.8 | No | 2019-12-12 | B2_s1_d2 | 0.5 | 5.9 | 9.3 | 1257 | 11 | B2 | 7 | 0.01 | s1 | y | y | d2
19120011 | 20321226 | 18140 | -- | ARG18OM16NM16 3X16 804/125 | 30.5 | 6 | Paron | ID7600+SV55AA+GTI1230+GST+LANTOR+TPR37 | -- | 32.3 | 21.3 | No | 2019-12-12 | B2_s1_d2 | 0.7 | 12 | 23.5 | 1281 | 25 | B2 | 18 | 0.06 | s1 | y | y | d2
19120012 | 20319465 | 18140 | -- | ARG18OM16NM16 3X16 804/125 | 30.3 | 6 | Paron | ID7600+SV55AA+GTI1230+GST+LANTOR+TPR37 | -- | 32.3 | 22.3 | No | 2019-12-12 | B2_s1_d2 | 0.7 | 9.4 | 19.9 | 1500 | 18 | B2 | 14 | 0.05 | s1 | y | y | d2
19120013 | 20319466 | 18140 | -- | ARG18OM16NM16 3X16 804/125 | 31 | 6 | Paron | ID7600+SV55AA+GTI1230+GST+LANTOR+GFR380 | -- | 35.3 | 21.5 | No | 2019-12-12 | B2_s1_d1 | 0.67 | 6.8 | 19.9 | 1500 | 24 | B2 | 14 | 0.07 | s1 | y | n | d1
19120014 | 20321227 | 18140 | -- | ARG18OM16NM16 3X16 804/125 | 31 | 6 | Paron | ID7600+SV55AA+GTI1230+GST+GFR380 | -- | 35.1 | 21.2 | No | 2019-12-12 | C_s1_d2 | 0.79 | 10.5 | 31.2 | 1500 | 30 | C | 24 | 0.13 | s1 | y | y | d2
TN_2019_1822 |  | 71440 20226012 | 634822Z | AL-HEPRZ1(AS) 1X150MM2 12/20KV | 41.06 | 5 | Vilanova | 14203.69MM+16023.41MM | CD | 65.3 | 16.1 | No | 2019-12-13 | D_s1_d2 | 1.53 | 36.1 | 65.4 | 1500 | 58.9 | D | 21.4 | 0.03 | s1 | n | y | d2
TN_2019_1823 |  |  |  | FS17 BROWN 750V 1X1.5 MM2 | 2.81 | 180 | Vilanova | 28APGPIT | CD | 62.7 | 17.5 | No | 2019-12-13 | C_s2_d0 | 1.62 | 9.5 | 3.3 | 501 | 205.1 | C | 236.8 | 0.88 | s2 | n | n | d0
TN_2019_1824 |  | 72744 20227787 | 609153Y | AL-HEPRZ1(AS) 1X240MM2 12/20KV | 43.41 | 5 | Vilanova | 14203.19MM+16023.19MM | CD | 59.7 | 18.4 | No | 2019-12-13 | D_s1_d2 | 1.32 | 37.2 | 57.2 | 1482 | 59.7 | D | 4.7 | 0.02 | s1 | n | y | d2
TN_2019_1825 |  |  |  | FS17 BROWN 750V 1X1.5 MM2 | 2.81 | 180 | Vilanova | 28AMGPIT | CD | 55.5 | 19.5 | No | 2019-12-13 | C_s2_d0 | 1.49 | 9.1 | 30.9 | 483 | 248.5 | C | 220.1 | 0.98 | s2 | n | n | d0
TN_2019_1826 |  |  |  | FS17 GREY 750V 1X1.5 MM2 | 2.8 | 180 | Vilanova | 28ALGPIT | CD | 51 | 20.8 | No | 2019-12-13 | C_s2_d0 | 1.08 | 7 | 23.1 | 489 | 160.6 | C | 217.7 | 0.9 | s2 | n | n | d0
TN_2019_1827 |  |  | Sample 94 | TEST SAMPLE 94 PBT-FR + GEL FR | 11.29 | 14 | Vilanova | AFUMEXCPR | CD | 62.2 | 12.4 | No | 2019-12-15 | C_s1_d1 | 1.66 | 27.2 | 44.3 | 765 | 101.1 | C | 32.4 | 0.06 | s1 | y | n | d1
TN_2019_1828 |  | 83025678 20193636 | 567775X | AFUMEX CLASS RZ1-K (AS) 1KV 1X16 | 10.84 | 14 | Vilanova | 14200.7MM+16021.4MM | CD | 61.5 | 12.8 | No | 2019-12-15 | C_s1_d0 | 1.29 | 15.1 | 22.2 | 819 | 43.1 | C | 37.1 | 0.11 | s1 | n | n | d0
TN_2019_1829 |  | 83021626 20193677 | 566630C | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11.92 | 13 | Vilanova | 14200.5MM+16021.5MM | CD | 57.8 | 15.3 | No | 2019-12-15 | E ou F_s2_d2 | 3.3 | 98.2 | 226.5 | 1464 | 208.4 | E ou F | 54.5 | 0.24 | s2 | n | y | d2
TN_2019_1830 |  | 831777240 | 5096894 | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.39 | 15 | Vilanova | 14200.6MM+16021.6MM | CD | 48.3 | 18.6 | No | 2019-12-15 | D_s1_d2 | 3.3 | 66.2 | 168 | 1476 | 142.8 | D | 38.9 | 0.15 | s1 | n | y | d2
19120015 |  | 18149 | EBM198736 | 750-3G1.5-SH-NF F 55-625-255 | 10.7 | 14 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 46.5 | 20.8 | No | 2019-12-17 | B2_s1_d1 | 1.07 | 14.5 | 28.1 | 1014 | 40 | B2 | 25 | 0.05 | s1 | y | n | d1
19120016 |  | 18125 | -- | 750-3G2.5-SH-NF F 55-625-255 | 11 | 14 | Paron | IX1100FR+0400FEIT+5300SEIT | -- | 44.8 | 22 | No | 2019-12-17 | B2_s1_d2 | 0.77 | 11.3 | 17.4 | 813 | 47 | B2 | 18 | 0.03 | s1 | y | y | d2
19120017 |  | 18125 | -- | 1000-1X35MM²-SH-NF F55-625-255 | 14 | 11 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 44.3 | 23.1 | No | 2019-12-17 | B2_s1_d2 | 0.57 | 5.4 | 10.5 | 1110 | 17 | B2 | 17 | 0.03 | s1 | y | y | d2
TN_2019_1832 |  | 74883 | 614000S | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.24 | 8 | Vilanova | LE0592+XLPE4201+LE0492+RELLENOCPR1420SEES+COBERTACPR1602SEES | CD | 74.5 | 14.2 | No | 2019-12-19 | C_s1_d2 | 1.28 | 22.3 | 45.6 | 1500 | 39.3 | C | 22.6 | 0.05 | s1 | n | y | d2
19120018 |  | 18153 | I28430 | PRYSMIAN FG16M16 1 KV 1X16 | 10.4 | 15 | Paron | SXLPE+0300FDIT+5300SEIT | -- | 45.5 | 20.6 | No | 2019-12-19 | B2_s1_d1 | 0.83 | 8.5 | 16.4 | 1056 | 29 | B2 | 21 | 0.06 | s1 | y | n | d1
19120019 |  | 18153 | H21395 | PRYSMIAN FG16M16 1 KV 1X240 | 28.7 | 6 | Paron | SXLPE+0300FDIT+5300SEIT | -- | 46.8 | 22.8 | No | 2019-12-19 | B2_s1_d0 | 0.47 | 3.5 | 5.3 | 762 | 12 | B2 | 3 | 0.01 | s1 | n | n | d0
19120020 |  | 18153 | I25770 | PRYSMIAN FG16M16 1 KV 5G1.5 | 13.2 | 12 | Paron | SXLPE+0300FDIT+5300SEIT | -- | 47.6 | 21.9 | No | 2019-12-19 | B2_s1_d2 | 0.8 | 12.6 | 20.8 | 1122 | 26 | B2 | 25 | 0.04 | s1 | y | y | d2
19120021 |  | 18153 | I30866 | PRYSMIAN FG16M16 1 KV 1X16 | 10.4 | 15 | Paron | SXLPE+0300FDIT+5310SEIT | -- | 26.6 | 21.3 | No | 2019-12-21 | B2_s1_d1 | 0.8 | 8.4 | 15.8 | 930 | 39 | B2 | 23 | 0.05 | s1 | y | n | d1
19120022 |  | 18153 | I31029 | PRYSMIAN FG16M16 1 KV 5G1.5 | 13 | 12 | Paron | SXLPE+0300FDIT+5310SEIT | -- | 38.8 | 20.8 | No | 2019-12-21 | C_s1_d1 | 1.07 | 17.1 | 30.3 | 1197 | 35 | C | 31 | 0.11 | s1 | y | n | d1
19120023 |  | 18153 | H8663 | PRYSMIAN AGR16R16 1 KV 1X16 | 9.4 | 17 | Paron | SXLPE+05AMFPIT+20AHSPIT | -- | 40 | 21 | No | 2019-12-21 | B2_s2_d1 | 0.57 | 7.7 | 19.9 | 609 | 66 | B2 | 172 | 0.5 | s2 | y | n | d1
19120024 |  | 18153 | H53104 | PRYSMIAN AGR16R16 1 KV 1X400 | 33.3 | 6 | Paron | SXLPE+05AMFPIT+20AHSPIT | -- | 41.6 | 20.9 | No | 2019-12-21 | C_s3_d2 | 1 | 11.9 | 40.8 | 1494 | 64 | C | 433 | 0.87 | s3 | y | y | d2
20010001 |  | 18152 | EBM 212498 | 750-5G1.5-SH-NF F 55-625-255 | 14.6 | 10 | Paron | IX1400FR+07AAFEIT+5300SEIT | -- | 45.3 | 23.8 | No | 2020-01-09 | B2_s1_d1 | 0.67 | 9.9 | 13.2 | 1287 | 23 | B2 | 13 | 0.02 | s1 | y | n | d1
20010002 |  | 18152 | EBM 212498 | 750-5G1.5-SH-NF F 55-625-255 | 14.6 | 10 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 45.2 | 23.2 | No | 2020-01-09 | B2_s1_d1 | 0.67 | 9 | 15.1 | 1203 | 21 | B2 | 14 | 0.03 | s1 | y | n | d1
20010003 |  | 18152 | EBM 180110 | 750-5G1.5-SH-NF F 55-625-255 | 14.6 | 10 | Paron | IX1400FR+04ANFEIT+5300SEIT | -- | 43.9 | 24 | No | 2020-01-09 | B2_s1_d1 | 0.57 | 6.4 | 9 | 1137 | 23 | B2 | 10 | 0.02 | s1 | y | n | d1
20010004 | 20319466 | 18140 | -- | ARG18OM16NM16 3X16 804/125 | 31 | 6 | Paron | ID7600+SV55AA+GTI1230+GST+LANTOR+GFR380 | -- | 41.4 | 21.9 | No | 2019-01-13 | B2_s1_d1 | 0.67 | 10.7 | 23.2 | 1488 | 27 | B2 | 24 | 0.08 | s1 | y | n | d1
20010005 |  | 18157 | CE3713B | FR-N1X1G1 1X25MM² | 14 | 11 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 41.2 | 21.8 | No | 2020-01-13 | B2_s1_d2 | 0.57 | 5.6 | 8.4 | 1035 | 24 | B2 | 5 | 0.01 | s1 | n | y | d2
20010006 | 20321227 | 18140 | -- | ARG18OM16NM16 3X16 804/125 | 31 | 6 | Paron | ID7600+SV55AA+GTI1230+GST+GFR380 | -- | 41.5 | 21.6 | No | 2020-01-13 | C_s1_d2 | 1.1 | 13.2 | 37.9 | 1497 | 36 | C | 41 | 0.17 | s1 | y | y | d2
20010007 |  | 18157 | -- | FR-N1X1G1 1X25MM² | 11 | 14 | Paron | IX1400FR+TPR-37 | -- | 46.6 | 20.7 | No | 2020-01-13 | D_s2_d2 | 2.4 | 37.4 | 52.9 | 1383 | 80 | D | 80 | 0.14 | s2 | y | y | d2
20010008 |  | 18157 | -- | FR-N1X1G1 1X25MM² | 12.7 | 12 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 45.5 | 21.8 | No | 2020-01-13 | B2_s1_d1 | 0.57 | 5.5 | 10.8 | 978 | 20 | B2 | 8 | 0.01 | s1 | y | n | d1
TN_2019_1833 |  | 73429 | 466475N | RHZ1-RA+2OL (AS) 76/132 KV 1X1600MAL + H135 | 101.7 | 2 | Vilanova | TPO03SKIN:70%LE0563+30%1602SEESOVERLAPREARTHEFLAME | CD | 50.8 | 9.4 | No | 2020-01-14 | B2_s1_d0 | 0.78 | 10.8 | 17.7 | 870 | 31 | B2 | 4.9 | 0.01 | s1 | n | n | d0
TN_2019_1834 |  | 72746 | 581064S | HEPRZ1(AS) 20KV 1X150 | 41.84 | 5 | Vilanova | 14202.1MM+60002.9MM | CD | 75.6 | 13.1 | No | 2019-12-19 | D_s1_d2 | 1.38 | 40.9 | 67.5 | 1500 | 66.5 | D | 12.9 | 0.03 | s1 | n | y | d2
TN_2020_1835 |  | 74883 | 614000S | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.24 | 8 | Vilanova | LE0592+XLPE4201+LE0492+RELLENOCPR1420SEES+COBERTACPR1602SEES | CD | 75.1 | 7.9 | No | 2020-01-13 | C_s1_d2 | 1.19 | 22.6 | 50.9 | 1473 | 43.5 | C | 21.6 | 0.05 | s1 | n | y | d2
TN_2020_1836 |  | 74605 20319196 | 545824M | RHZ1(AS) 10KV 1X400 | 48.43 | 4 | Vilanova | 14203.3MM+16023.3MM | CD | 55.5 | 8.2 | No | 2020-01-13 | B2_s1_d0 | 0.46 | 4 | 5.4 | 678 | 14.3 | B2 | 4.1 | 0.01 | s1 | n | n | d0
TN_2020_1837 |  | 83443562 20319195 | 642913U | RHZ1(AS) 10KV 1X95 | 32.58 | 6 | Vilanova | 14202.6MM+16022.7MM | CD | 53.2 | 10.3 | No | 2020-01-13 | B2_s1_d0 | 0.51 | 4.3 | 5.8 | 1011 | 11.7 | B2 | 0.3 | 0 | s1 | n | n | d0
TN_2020_1838 |  | 74562 20319529 | 639303V | ROZ1-K 500V 1X3X0.75 | 8.18 | 19 | Vilanova | GFR380 | CD | 47.2 | 12.7 | No | 2020-01-13 | E ou F_s2_d1 | 3.3 | 72.1 | 149.4 | 1317 | 146.9 | E ou F | 84.1 | 0.17 | s2 | y | n | d1
TN_2020_1839 |  | 74561 20319530 | 639305X | ROZ1-K 500V 1X2X0.75 | 8.26 | 19 | Vilanova | GFR380 | CD | 43 | 15.2 | No | 2020-01-13 | D_s1_d0 | 2.2 | 22.9 | 29.1 | 711 | 73.5 | D | 31.8 | 0.05 | s1 | n | n | d0
TN_2020_1840 |  |  | 555464R | AFUMEX CLASS HAZ H07Z1-K (AS) 2X25+G16+1.5 | 16.5 | 9 | Vilanova | 1602SEES | CD | 51.9 | 12.7 | No | 2020-01-14 | B2_s1_d0 | 0.48 | 4 | 5.7 | 615 | 18.5 | B2 | 0 | 0 | s1 | n | n | d0
TN_2020_1841 |  |  | 593875S | AFUMEX CLASS HAZ H07Z1-K (AS) 3G25+1X1.5 | 17.5 | 9 | Vilanova | 1602SEES | CD | 46.8 | 14.4 | No | 2020-01-14 | B2_s1_d0 | 0.46 | 3 | 5.2 | 630 | 15.9 | B2 | 2 | 0 | s1 | n | n | d0
TN_2020_1842 |  |  | 641944R | AFUMEX CLASS HAZ H07Z1-K (AS) 2X35+G16+1.5 | 19 | 8 | Vilanova | 1602SEES | CD | 68.6 | 7.9 | No | 2020-01-15 | B2_s1_d0 | 0.29 | 3.8 | 5.6 | 768 | 17.1 | B2 | 6.1 | 0.01 | s1 | n | n | d0
TN_2020_1843 |  | 83266889 20193990 |  | AFUMEX CLASS 750V HO7Z1-K (AS) TYPE2 1X4 | 4.03 | 90 | Vilanova | 1602SEES | CD | 67.1 | 9.7 | No | 2020-01-15 | B2_s1_d0 | 0.69 | 5.3 | 16.6 | 618 | 64.1 | B2 | 5.3 | 0.03 | s1 | n | n | d0
TN_2020_1845 |  | 83179220 20193683 | 624507M | AFUMEX CLASS RZ1-K (AS) 1KV 5G25 | 26.5 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 62.6 | 11.2 | No | 2020-01-15 | B2_s1_d0 | 0.53 | 6 | 15.4 | 555 | 59.3 | B2 | 1.7 | 0 | s1 | n | n | d0
TN_2020_1846 |  | 83333527 20193639 | 633558A | AFUMEX CLASS RZ1-K (AS) 1KV 1X50 | 14.56 | 10 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 55.5 | 14.6 | No | 2020-01-15 | B2_s1_d2 | 0.97 | 12.5 | 21.3 | 1074 | 27.5 | B2 | 9.3 | 0.02 | s1 | n | y | d2
20010009 |  | 18157 | -- | FR-N1X1G1 1X150MM² | 22 | 7 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 32.4 | 23.2 | No | 2020-01-16 | B2_s1_d0 | 0.47 | 3.6 | 6.3 | 1497 | 12 | B2 | 5 | 0.01 | s1 | n | n | d0
20010010 |  | 18153 | H83939 | PRYSMIAN FG16M16 1 KV 1X240 | 28.6 | 6 | Paron | SXLPE+0300FDIT+5310SEIT | -- | 33 | 22.8 | No | 2020-01-16 | B2_s1_d0 | 0.42 | 4.5 | 5.9 | 756 | 16 | B2 | 4 | 0.01 | s1 | n | n | d0
20010011 |  | 18158 | -- | PRYSMIAN GROUP 20191*2*0.5 DCA-S2D2A2 MOVISTAR OF74841 | 3.8 | 90 | Paron | TPR-32 | -- | 43.3 | 20.3 | No | 2020-01-16 | D_s2_d2 | 3.3 | 62.2 | 260.3 | 759 | 575 | D | 151 | 0.37 | s2 | y | y | d2
TN_2020_1847 |  | 73193 20310305 | 562797L | RHZ1-2OL (AS) 1X240MM AL-VOLTALENE 12_20KV | 43.8 | 5 | Vilanova | TPR492.0MM+60002.8MM | CD | 44.5 | 13 | No | 2020-01-20 | D_s1_d2 | 1.48 | 33.3 | 43.7 | 1500 | 64.9 | D | 14.3 | 0.05 | s1 | n | y | d2
TN_2020_1848 |  | 83352586 20193656 | 641965N | AFUMEX CLASS 1KV RZ1-K (AS) 3G4MM2 | 12.28 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 76.2 | 12 | No | 2020-01-17 | C_s1_d2 | 1.38 | 24.1 | 32.5 | 1179 | 49.9 | C | 26 | 0.07 | s1 | n | y | d2
TN_2020_1849 |  | 83333528 | 632053P | AFUMEX CLASS 1KV RZ1-K (AS) 1X70MM2 | 16.61 | 9 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 74.2 | 11.9 | No | 2020-01-17 | B2_s1_d1 | 0.49 | 6.3 | 19.3 | 1500 | 16.1 | B2 | 9.5 | 0.01 | s1 | y | n | d1
TN_2020_1850 |  | 83389551 20193684 | 641964M | AFUMEX CLASS 1KV RZ1-K (AS) 5G35MM2 | 30.48 | 6 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 74.6 | 13.4 | No | 2020-01-17 | B2_s1_d0 | 0.41 | 4.4 | 6.1 | 1026 | 12.7 | B2 | 3.6 | 0.01 | s1 | n | n | d0
TN_2020_1851 |  | 83258843 20193637 | 578166S | AFUMEX CLASS 1KV RZ1-K (AS) 1X25MM2 | 12.14 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 67.7 | 15.1 | No | 2020-01-17 | C_s1_d2 | 1.8 | 25 | 50.6 | 1500 | 51.9 | C | 13.7 | 0.04 | s1 | n | y | d2
TN_2020_1852 |  | 83333252 20193677 | 641943P | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11.6 | 13 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 37.3 | 12.7 | No | 2020-01-20 | E ou F_s2_d2 | 3.3 | 95.7 | 227.9 | 1329 | 221.5 | E ou F | 75.7 | 0.27 | s2 | n | y | d2
TN_2020_1853 |  | 83400283 20229626 | 601897L | AL-HEPRZ1(AS) 1X400MM2 18/30KV | 50.1 | 4 | Vilanova | 14202.5MM+16022.6MM | CD | 42.1 | 12.8 | No | 2020-01-20 | D_s1_d2 | 0.9 | 33 | 47.7 | 1416 | 55.2 | D | 8.1 | 0.03 | s1 | n | y | d2
20010012 |  | 18165 | -- | L1081-1 RÉF. CEC 2019-059 | 3 | 165 | Paron | 1700SEES | -- | 31.1 | 19.8 | No | 2020-01-20 | C_s1_d1 | 1.27 | 12.7 | 30.5 | 639 | 107 | C | 38 | 0.09 | s1 | y | n | d1
20010013 |  | 18125 | -- | FR-N1X1G1 4G1.5MM² | 12 | 13 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 30.8 | 19.8 | No | 2020-01-20 | B2_s1_d2 | 0.67 | 8.6 | 11.7 | 936 | 29 | B2 | 17 | 0.03 | s1 | y | y | d2
20010014 |  | 18125 | -- | FR-N1X1G1 5G1.5MM² | 13 | 12 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 32.2 | 19.9 | No | 2020-01-20 | B2_s1_d2 | 0.67 | 7.2 | 12.5 | 1128 | 28 | B2 | 13 | 0.02 | s1 | y | y | d2
TN_2020_1854 |  | 83443562 20319195 | 642913U | RHZ1(AS) 10KV 1X95 | 32.58 | 6 | Vilanova | 14202.6MM+16022.7MM | CD | 79.1 | 13 | No | 2020-01-22 | B2_s1_d0 | 0.41 | 5.1 | 7.3 | 1245 | 11.3 | B2 | 17.6 | 0.02 | s1 | n | n | d0
TN_2020_1855 |  | 74605 20319196 | 545824M | RHZ1(AS) 10KV 1X400 | 48.43 | 4 | Vilanova | 14203.3MM+16023.3MM | CD | 83 | 14.7 | No | 2020-01-22 | B2_s1_d0 | 0.26 | 4.5 | 5.7 | 981 | 14.4 | B2 | 1.8 | 0.01 | s1 | n | n | d0
TN_2020_1856 |  | 83349414 20268963 | 656522L | PRYSMIAN AFUMEX RHZ1MZ1 (AS) 10KV 3X70 | 59,,46 | 4 | Vilanova | XLPE+1602 | CD | 83.8 | 15.3 | No | 2020-01-22 | B2_s1_d2 | 0.5 | 6 | 9.4 | 891 | 18.5 | B2 | 6.2 | 0.01 | s1 | n | y | d2
TN_2020_1857 |  | 83441778 20313823 | 602095B | PRYSMIAN EPROTENAX DHVMV 2RH 3X120 10KV | 64.2 | 3 | Vilanova | ID7140IT+2400+2400 | CD | 82.7 | 15.6 | No | 2020-01-22 | B2_s3_d0 | 0.49 | 7.6 | 9.5 | 690 | 34.5 | B2 | 1028.3 | 1.71 | s3 | n | n | d0
20010014 |  | 18125 | -- | FR-N1X1G1 5G1.5MM² | 13 | 12 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 32.2 | 19.9 | No | 2020-01-20 | B2_s1_d2 | 0.67 | 7.2 | 12.5 | 1128 | 28 | B2 | 13 | 0.02 | s1 | y | y | d2
20010015 |  | 18154 | -- | 1800-S-1X240MM²-SH-NF F 55-625-255 | 30 | 6 | Paron | IX1400FR+5300SEIT | -- | 28.3 | 18 | No | 2020-01-22 | B2_s1_d2 | 0.67 | 10 | 17.8 | 1485 | 21 | B2 | 5 | 0.01 | s1 | y | y | d2
20010016 |  | 18154 | -- | 1800-S-1X240MM²-SH-NF F 55-625-255 | 32.5 | 6 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 31.3 | 18 | No | 2020-01-22 | B2_s1_d0 | 0.6 | 6.6 | 8.2 | 1074 | 17 | B2 | 5 | 0.01 | s1 | n | n | d0
20010017 |  | 18146 | -- | K25 750V 1X1 -SH-NF F 55-625-255 ( IRRADIÉ) | 3 | 165 | Paron | 1602SEES | -- | 28.5 | 18.2 | No | 2020-01-23 | C_s2_d0 | 1.27 | 18.4 | 36.3 | 588 | 141 | C | 71 | 0.2 | s2 | n | n | d0
20010018 |  | 18159 | -- | OMERIN PVRISOL 500 EN 3G1.5MM² | 7.4 | 21 | Paron | LSOH | -- | 29.1 | 18.5 | No | 2020-01-23 | D_s2_d1 | 3.3 | 25.1 | 65.5 | 564 | 262 | D | 258 | 0.64 | s2 | y | n | d1
20010019 |  | 18159 | -- | OMERIN PVRISOL 500 EN 2*1.5MM² | 6.9 | 21 | Paron | LSOH | -- | 29.9 | 19 | No | 2020-01-23 | D_s2_d1 | 3.3 | 25.1 | 63.1 | 699 | 176 | D | 219 | 0.52 | s2 | y | n | d1
20010020 |  | -- | -- | PRYSMIAN 255-2P0.60MM²-C1-SH-AF-10-2019 | 11 | 11 | Paron | ME6032+3000GVFR+SW3800FR | -- | 31.3 | 19 | No | 2020-01-25 | B2_s1_d1 | 0.67 | 11.5 | 25.6 | 696 | 67 | B2 | 33 | 0.08 | s1 | y | n | d1
TN_2020_1858 |  |  | PG 150718 DBM | HN 33534 4X10MM² | 21.54 | 7 | Vilanova | 4400IPFR+TWOTWISTEDPETYARNS1100DTEX+1200FPFR+1000GPFR+2800SPFR | CD | 79.4 | 11.9 | No | 2020-01-23 | C_s3_d0 | 0.97 | 17.9 | 27.8 | 807 | 67.3 | C | 646.6 | 1.1 | s3 | n | n | d0
TN_2020_1859 |  | 73779 | D46687 | FG16OR16 5G1.5 MM² - 0.6/1 KV | 11.36 | 14 | Vilanova | 05AM+20AH0.4+1.4 | CD | 82.3 | 13.1 | No | 2020-01-23 | C_s2_d2 | 1.62 | 23.5 | 41.4 | 732 | 107.2 | C | 332.2 | 0.63 | s2 | n | y | d2
TN_2020_1860 |  | 73777 | I26702 | FG16OR16 5G1.5 MM² - 0.6/1 KV | 11.33 | 14 | Vilanova | 05AM+54AB0.4+1.4 | CD | 77.5 | 14.8 | No | 2020-01-23 | C_s2_d1 | 1.29 | 20.1 | 47.2 | 804 | 98.1 | C | 394.2 | 0.87 | s2 | y | n | d1
TN_2020_1862 |  | 20319871 | 639946U | RZ1F3Z1-K 1KV 2X25MM² + 2FO | 16.5 | 9 | Vilanova | 1602SEES+TPR55 | CD | 69.7 | 12.6 | No | 2020-01-29 | B2_s1_d1 | 0.43 | 10.9 | 16.7 | 1074 | 36 | B2 | 17.2 | 0.03 | s1 | y | n | d1
TN_2020_1863 |  | 20319872 | 623471L | RZ1F3Z1-K 1KV 2X25MM² + 2FO | 16.15 | 9 | Vilanova | TPR55+TPR55 | CD | 69.6 | 12.8 | No | 2020-01-29 | B2_s1_d1 | 0.58 | 10.2 | 14.2 | 870 | 34.4 | B2 | 17.1 | 0.04 | s1 | y | n | d1
TN_2020_1864 |  |  | 5096818 | FS17 ICEL 1X1.5 NEGRO | 2.81 | 180 | Vilanova | COMPETITORSAMPLE | CD | 66.9 | 15.1 | No | 2020-01-29 | B2_s2_d0 | 0.7 | 6.6 | 17.7 | 447 | 125.3 | B2 | 218.2 | 0.95 | s2 | n | n | d0
TN_2020_1865 |  |  | 5096819 | FS17 REPERO 1X1.5 AZUL | 2.81 | 180 | Vilanova | COMPETITORSAMPLE | CD | 65 | 16 | No | 2020-01-29 | C_s2_d0 | 1.1 | 8.6 | 24.5 | 492 | 163.8 | C | 218.7 | 0.86 | s2 | n | n | d0
TN_2020_1866 |  |  | 635440W | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.16 | 17 | Vilanova | XLPE+SKINIGNÍFUG+TPR49+TPR541.572G/CM3 | CD | 63.2 | 16.3 | No | 2020-01-29 | D_s1_d1 | 3.3 | 41.7 | 70.1 | 1497 | 75.2 | D | 32.2 | 0.08 | s1 | y | n | d1
TN_2020_1867 |  | 83269089 20303005 | 590078P | EXZHELLENT SOLAR ABRERA 1X4 MM2 | 5.49 | 30 | Vilanova | TPR-20+TPS02 | CD | 67.6 | 13.1 | No | 2020-01-31 | D_s2_d2 | 3.3 | 57.8 | 382.1 | 666 | 1056.9 | D | 89.8 | 0.34 | s2 | n | y | d2
TN_2020_1869 |  | 73429 | 466475N | RHZ1-RA+2OL (AS) 76/132 KV 1X1600MAL + H135 | 101.7 | 2 | Vilanova | TPO03SKIN:70%LE0563+30%1602SEESOVERLAPINFRONTOFTHEFLAME | CD | 60.8 | 17.2 | No | 2020-01-31 | B2_s1_d0 | 0.86 | 12.1 | 18.1 | 1497 | 24.8 | B2 | 11.8 | 0.02 | s1 | n | n | d0
TN_2020_1870 |  | 83436927 20154478 | 652788C | PRYSUN SPM 1X4 MM2 | 5.82 | 25 | Vilanova | SV4120ES | CD | 73.1 | 15.7 | No | 2020-02-03 | D_s2_d2 | 3.3 | 51.3 | 262.2 | 624 | 937.2 | D | 76.9 | 0.2 | s2 | n | y | d2
TN_2020_1871 |  | 831168717 20221312 | 573062U | PRYSUN SPM 1X6 MM2 | 6 | 25 | Vilanova | SV4120ES | CD | 70.9 | 16.5 | No | 2020-02-03 | D_s2_d2 | 3.3 | 45.5 | 264.8 | 573 | 988.2 | D | 57.4 | 0.15 | s2 | n | y | d2
TN_2020_1872 |  | 74181 20317072 | 633758T | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.38 | 17 | Vilanova | XLPE+MEGOLOND308 | CD | 66.6 | 18.1 | No | 2020-02-03 | B2_s1_d1 | 0.55 | 10.3 | 23.2 | 573 | 85.5 | B2 | 6.4 | 0.03 | s1 | y | n | d1
TN_2020_1873 |  | 74184 20317076 | 633829V | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 10.62 | 14 | Vilanova | XLPE+MEGOLOND19.434 | CD | 62 | 20 | No | 2020-02-03 | E ou F_s2_d2 | 3.3 | 71.6 | 233.2 | 1500 | 194.3 | E ou F | 125.1 | 0.35 | s2 | n | y | d2
TN_2020_1874 |  | 74180 20317062 | 633828U | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.58 | 15 | Vilanova | XLPE+CPR+MEGOLOND30812 | CD | 55.1 | 17.6 | No | 2020-02-04 | B2_s1_d2 | 0.78 | 11.8 | 18.6 | 690 | 63.7 | B2 | 7.2 | 0.04 | s1 | n | y | d2
TN_2020_1875 |  | 74185 20317075 | 633757S | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11.1 | 14 | Vilanova | XLPE+MEGOLOND19.434 | CD | 50 | 18.3 | No | 2020-02-04 | C_s2_d2 | 1.84 | 29.6 | 47.7 | 1494 | 64.5 | C | 55.7 | 0.14 | s2 | n | y | d2
TN_2020_1876 |  | 74180 20317062 | 633740Y | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.53 | 15 | Vilanova | XLPE+CPR+MEGOLOND19434 | CD | 51 | 18.6 | No | 2020-02-04 | B2_s1_d1 | 0.42 | 8.8 | 16 | 540 | 76.3 | B2 | 18.6 | 0.03 | s1 | y | n | d1
TN_2020_1877 |  | 74186 20317073 | 633755P | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11.15 | 14 | Vilanova | XLPE+MEGOLOND30812 | CD | 49.4 | 19.8 | No | 2020-02-04 | D_s2_d2 | 1.98 | 33.5 | 50.3 | 1500 | 69 | D | 61.7 | 0.13 | s2 | n | y | d2
TN_2020_1878 |  | 74633 20319996 | 274765H | HEPRZ1(AS) 20KV 1X120 | 38.28 | 5 | Vilanova | 14202.8MM+60003.0MM | CD | 61.1 | 10.1 | No | 2020-02-06 | D_s1_d2 | 1.51 | 45.1 | 71.9 | 1389 | 77.1 | D | 7.7 | 0.03 | s1 | n | y | d2
TN_2020_1879 |  | 74183 20317074 | 633756R | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 10.44 | 15 | Vilanova | XLPE+MEGOLOND30812 | CD | 78.4 | 15.2 | No | 2020-02-06 | E ou F_s2_d2 | 3.3 | 96.4 | 331.7 | 1338 | 319.6 | E ou F | 182.5 | 0.48 | s2 | n | y | d2
TN_2020_1880 |  | 74182 20317077 | 633831X | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.24 | 17 | Vilanova | XLPE+MEGOLOND19.434 | CD | 57.3 | 18.6 | No | 2020-02-06 | C_s1_d0 | 0.49 | 15.1 | 26.2 | 591 | 98.8 | C | 21.2 | 0.08 | s1 | n | n | d0
TN_2020_1882 |  | 83350210 20193655 | 613365B | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 (TORN MATÍ) | 11.63 | 13 | Vilanova | 14200.5MM+16021.7MM | CD | 72.2 | 11 | No | 2020-02-07 | C_s1_d2 | 1.11 | 18 | 28.8 | 780 | 60 | C | 10.6 | 0.05 | s1 | n | y | d2
TN_2020_1883 |  | 83350210 20193655 | 613364A | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 (TORN TARDA) | 11.51 | 13 | Vilanova | 14200.7MM+16021.5MM | CD | 69 | 12.4 | No | 2020-02-07 | C_s1_d2 | 1.53 | 20.4 | 28.3 | 756 | 62.1 | C | 21 | 0.09 | s1 | n | y | d2
TN_2020_1884 |  | 83350210 20193655 | 615742K | AFUMEX CLASS RZ1-K (AS) 1KV 3G2.5 (TORN NIT) | 11.41 | 14 | Vilanova | 14200.6MM+16021.6MM | CD | 62.7 | 16.5 | No | 2020-02-07 | C_s1_d0 | 1.37 | 22.7 | 33.4 | 867 | 64 | C | 38.6 | 0.14 | s1 | n | n | d0
TN_2020_1885 |  | 72661 | T7-F89184 | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 PROTOYPE 2 | 12.23 | 13 | Vilanova | SXLPE+0300FEIT+16AASEIT | CD | 69.9 | 13.8 | No | 2020-02-10 | C_s1_d1 | 0.46 | 16.1 | 27.2 | 825 | 51.8 | C | 24.3 | 0.09 | s1 | y | n | d1
TN_2020_1886 |  | 72661 | T7-F89185 | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 PROTOYPE 3 | 12.27 | 13 | Vilanova | SXLPE+0300FEIT+16AASEES | CD | 67.9 | 14.2 | No | 2020-02-10 | C_s2_d1 | 1.46 | 29.4 | 39.9 | 1137 | 68.4 | C | 54.8 | 0.13 | s2 | y | n | d1
TN_2020_1887 |  | 72661 | T7-F89187 | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 PROTOYPE 1 | 12.22 | 13 | Vilanova | SXLPE+0300FEIT+16AASEIT | CD | 64.6 | 16.9 | No | 2020-02-10 | C_s1_d1 | 0.67 | 16 | 29.9 | 804 | 59.8 | C | 31.8 | 0.08 | s1 | y | n | d1
TN_2020_1888 |  |  |  | ASCABLE-RECAEL RZ1-K (AS) 1KV 1X150 | 21.98 | 7 | Vilanova | COMPETITORSAMPLE | CD | 76.3 | 14.8 | No | 2020-02-12 | C_s1_d2 | 0.89 | 18.8 | 29.8 | 951 | 45.9 | C | 11.4 | 0.02 | s1 | n | y | d2
TN_2020_1889 |  |  |  | ASCABLE-RECAEL HO7Z1-K (AS) TYPE2 AENOR (HAR) 1X4 MM2 | 4.11 | 75 | Vilanova | COMPETITORSAMPLE | CD | 74.8 | 15 | No | 2020-02-12 | B2_s1_d1 | 1.18 | 11.8 | 22.6 | 702 | 88.3 | B2 | 21 | 0.07 | s1 | y | n | d1
TN_2020_1890 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 75.9 | 15.6 | No | 2020-02-12 | C_s1_d0 | 1.31 | 21.7 | 32.1 | 849 | 85.6 | C | 39.8 | 0.09 | s1 | n | n | d0
TN_2020_1891 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 74.3 | 15.9 | No | 2020-02-12 | C_s1_d0 | 0.84 | 16.4 | 26.4 | 696 | 82 | C | 23.8 | 0.06 | s1 | n | n | d0
TN_2020_1892 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 71.3 | 16.3 | No | 2020-02-12 | C_s1_d0 | 0.9 | 16.9 | 26.6 | 924 | 70.6 | C | 29.5 | 0.06 | s1 | n | n | d0
TN_2020_1893 |  | 83451495 20194862 | 5096559 | ES05Z1-K 500V 1X1MM² | 2.4 | 270 | Manlleu |  | CD | 36 | 21.2 | No | 2020-02-17 | B2_s1_d0 | 1.5 | 12.8 | 27.6 | 723 | 90.2 | B2 | 21.6 | 0.07 | s1 | n | n | d0
CEL_2020_20-1 |  | 83451495 20194862 | 5096559 | ES05Z1-K 500V 1X1MM² | 2.4 | 270 | CEIS |  | CD | 37 | 21.07 | No | 2020-05-05 | C_s2_d0 | 0.9 | 13.4 | 33.7 | 648 | 106 | C | 56.1 | 0.15 | s2 | n | n | d0
TN_2020_1894 |  | 20302818 | 5096567 | 750V HO7Z1-K (AS) TYPE2 1X2.5 AZUL | 3.5 | 120 | Manlleu |  | CD | 36 | 21 | No | 2020-02-13 | D_s1_d0 | 2.66 | 21.9 | 46.3 | 777 | 108.3 | D | 33.5 | 0.06 | s1 | n | n | d0
TN_2020_1895 |  |  | T8-G67892 | AFUMEX CLASS RZ1-K (AS) 1KV 3X25 | 21.78 | 7 | Vilanova | 1420+1500 | CD | 73.3 | 13.2 | No | 2020-02-14 | B2_s1_d0 | 0.44 | 7.3 | 21 | 1500 | 18.9 | B2 | 6.1 | 0.02 | s1 | n | n | d0
TN_2020_1896 |  |  | 5096847 | ECOCLASS RZ1-K (AS) 1 KV 1X10 | 9.45 | 17 | Vilanova | COMPETITORSAMPLE | CD | 72.2 | 13.2 | No | 2020-02-14 | C_s2_d0 | 1.15 | 17.9 | 29.6 | 855 | 76.5 | C | 52.3 | 0.17 | s2 | n | n | d0
TN_2020_1897 |  |  | 5096849 | ECOCLASS RZ1-K (AS) 1 KV 3G2.5 | 10.9 | 14 | Vilanova | COMPETITORSAMPLE | CD | 70.1 | 15.2 | No | 2020-02-14 | D_s1_d0 | 1.69 | 30.6 | 42.1 | 990 | 80.4 | D | 45 | 0.08 | s1 | n | n | d0
TN_2020_1898 |  |  | 5096848 | ECOCLASS RZ1-K (AS) 1 KV 4G1.5 | 10.91 | 14 | Vilanova | COMPETITORSAMPLE | CD | 66.6 | 17.1 | No | 2020-02-14 | D_s2_d1 | 1.99 | 40.2 | 53 | 1143 | 96.6 | D | 52.1 | 0.1 | s2 | y | n | d1
TN_2020_1899 |  |  | 5096555 | ASCABLE RECAEL RZ1-K (AS) 1 KV 4G1.5 | 12.08 | 13 | Vilanova | COMPETITORSAMPLE | CD | 67.7 | 17.7 | No | 2020-02-14 | B2_s1_d0 | 0.73 | 15 | 23.4 | 831 | 46.6 | B2 | 37.4 | 0.06 | s1 | n | n | d0
TN_2020_1900 |  |  | 5096846 | ECOCLASS H07Z1-K (AS) 4 MM2 | 4.21 | 75 | Vilanova | COMPETITORSAMPLE | CD | 74 | 14.9 | No | 2020-02-17 | B2_s1_d1 | 0.82 | 10.7 | 29.8 | 765 | 64 | B2 | 15.6 | 0.05 | s1 | y | n | d1
TN_2020_1901 |  | 74788 2032983 | 661656S | SEGURFOC SZ-K 1KV PH120 (AS) 3G2.5 | 11.21 | 14 | Vilanova | SILICONA+TPR-49+TPR-55 | CD | 73.5 | 15.3 | No | 2020-02-17 | B2_s1_d2 | 0.85 | 15 | 27.9 | 831 | 80.7 | B2 | 10.6 | 0.03 | s1 | n | y | d2
TN_2020_1902 |  |  | 5096845 | ECOCLASS RZ1-K (AS) 1 KV 1X150 | 23.16 | 7 | Vilanova | COMPETITORSAMPLE | CD | 77.9 | 16 | No | 2020-02-17 | B2_s1_d1 | 0.42 | 8.2 | 13.8 | 1500 | 21.6 | B2 | 2.3 | 0 | s1 | y | n | d1
TN_2020_1903 |  |  | 5096557 | ASCABLE RECAEL RZ1-K (AS) 1 KV 1X10 | 10.71 | 14 | Vilanova | COMPETITORSAMPLE | CD | 77.5 | 16.4 | No | 2020-02-17 | B2_s1_d1 | 0.72 | 13.5 | 22.5 | 762 | 66.1 | B2 | 15.6 | 0.03 | s1 | y | n | d1
TN_2020_1904 |  |  | 5096556 | ASCABLE RECAEL RZ1-K (AS) 1 KV 3G2.5 | 11.87 | 13 | Vilanova | COMPETITORSAMPLE | CD | 65.7 | 18.7 | No | 2020-02-17 | B2_s1_d0 | 0.47 | 10.9 | 22.7 | 798 | 44.6 | B2 | 3.4 | 0.01 | s1 | n | n | d0
TN_2020_1905 |  | 74536 20318516 | 664967R | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11 | 14 | Manlleu | XLPE+25%19AA--56AC0.28MM+1602SEES1.12 | CD | 35 | 18.4 | No | 2020-02-11 | D_s2_d2 | 3.3 | 47.8 | 78.8 | 1221 | 121.3 | D | 69.5 | 0.15 | s2 | n | y | d2
TN_2020_1906 |  | 74536 20318516 | 658060H | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.16 | 13 | Manlleu | XLPE+25%19AA--0400FEIT0.5MM+1602SEES1.4MM | CD | 37 | 18.6 | No | 2020-02-13 | D_s1_d2 | 3.3 | 43.7 | 63.7 | 1182 | 109 | D | 39.6 | 0.16 | s1 | n | y | d2
TN_2020_1907 |  | 75136 20326367 | 665007J | AFUMEX CLASS RZ1-K (AS) 1KV 2X16 | 17.23 | 9 | Manlleu | XLPE--0400FEIT0.5MM+1602SEES1.4MM | CD | 35 | 20.7 | No | 2020-02-11 | B2_s1_d0 | 0.7 | 6.4 | 9.4 | 1419 | 23.9 | B2 | 2.7 | 0.01 | s1 | n | n | d0
TN_2020_1908 |  | 75134 20326365 | 634729Y | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11.97 | 13 | Manlleu | XLPE--0400FEIT0.5MM+1602SEES1.4MM | CD | 34 | 19.8 | No | 2020-02-26 | D_s1_d2 | 3.3 | 50.6 | 72.5 | 978 | 107.6 | D | 6.2 | 0.02 | s1 | n | y | d2
TN_2020_1909 |  | 74534 20318514 | 662497F | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 10.91 | 14 | Manlleu | XLPE+15%19AA--56AC0.28MM+1602SEES1.12 | CD | 35 | 17 | No | 2020-02-19 | D_s2_d2 | 3.3 | 57.4 | 117 | 1080 | 150 | D | 77.6 | 0.28 | s2 | n | y | d2
TN_2020_1910 |  | 74533 20318513 | 664957E | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.46 | 17 | Manlleu | XLPE+15%19AA--56AC0.28MM+1602SEES1.12 | CD | 36 | 21 | No | 2020-02-14 | D_s1_d2 | 3.3 | 58.8 | 118.5 | 1011 | 169.3 | D | 37.9 | 0.12 | s1 | n | y | d2
TN_2020_1911 |  | 74535 20318515 | 664995W | AFUMEX CLASS RZ1-K (AS) 1KV 35G1.5 | 8.56 | 15 | Manlleu | XLPE+25%19AA--56AC0.28MM+1602SEES1.12 | CD | 37 | 19 | No | 2020-02-18 | D_s1_d2 | 3.3 | 46.2 | 78.6 | 1080 | 130.6 | D | 35.8 | 0.08 | s1 | n | y | d2
TN_2020_1912 |  | 20302814 | 5096568 | 750V HO7Z1-K (AS) TYPE2 1X1.5 NEGRO | 2.87 | 165 | Manlleu |  | CD | 34 | 19.2 | No | 2020-02-18 | D_s1_d0 | 3.3 | 25.7 | 48.2 | 819 | 95.5 | D | 35.9 | 0.07 | s1 | n | n | d0
20020009 |  | 18153 | I30866 | PRYSMIAN FG16M16 1 KV 1X16 | 10.4 | 15 | Paron | SXLPE+0300FDIT+5300SEIT | -- | 30 | 21.6 | No | 2020-02-19 | B2_s1_d1 | 0.8 | 9.3 | 16.5 | 867 | 45.5 | B2 | 21.3 | 0.06 | s1 | y | n | d1
20020011 |  | 18153 | I25770 | PRYSMIAN FG16M16 1 KV 5G1.5 | 13.2 | 12 | Paron | SXLPE+0300FDIT+5300SEIT | -- | 31.3 | 24 | No | 2020-02-20 | C_s1_d1 | 0.83 | 15.7 | 20.2 | 1269 | 39.4 | C | 22.8 | 0.03 | s1 | y | n | d1
20020012 |  | 18153 | I25770 | PRYSMIAN FG16M16 1 KV 5G1.5 | 13.2 | 15 | Paron | SXLPE+0300FDIT+5300SEIT | -- | 31.6 | 21.5 | No | 2020-02-20 | C_s1_d2 | 1.03 | 20.3 | 32 | 1047 | 44.5 | C | 31.9 | 0.07 | s1 | y | y | d2
20020005 |  | 18200 | -- | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Paron | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | -- | 27.9 | 21.4 | No | 2020-02-18 | C_s2_d0 | 1.33 | 21.3 | 37.5 | 924 | 64.8 | C | 64.1 | 0.14 | s2 | n | n | d0
20020006 |  | 18200 | -- | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Paron | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | -- | 29.1 | 21.7 | No | 2020-02-18 | C_s2_d0 | 1.37 | 20.8 | 32.8 | 930 | 67.2 | C | 57 | 0.13 | s2 | n | n | d0
20020007 |  | 18200 | -- | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Paron | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | -- | 28.8 | 21.9 | No | 2020-02-18 | C_s2_d0 | 1.39 | 22.3 | 40.5 | 855 | 75.1 | C | 57.3 | 0.13 | s2 | n | n | d0
\20020010 |  | 18185 | -- | PRYSMIAN 255- HPTE- 525KVDC- 1X3500AL- 2020- 9984/- GTSO | 156.5 | 2 | Paron | XLPE+TUBEAL+65AC+SKINSC | -- | 33.7 | 21.7 | No | 2020-02-20 | C_s1_d0 | 1.63 | 26.3 | 34.1 | 1257 | 52 | C | 19.8 | 0.05 | s1 | n | n | d0
TN_2020_1913 |  | 74965 20316993 | 667287M | EXZHELLENT RZ1-K (AS) 1 KV 5G1.5 | 11.97 | 13 | Manlleu | SXLPE+0400FEIT+1602SEES | -- | 36 | 18 | No | 2020-02-18 | B2_s1_d1 | 1.1 | 0 | 0 | 0 | 0 | B2 | 0 | 0 | s1 | y | n | d1
TN_2020_1914 |  | 75007 20316994 | 667325D | EXZHELLENT RZ1-K (AS) 1 KV 5G16 | 20.07 | 8 | Manlleu | 0400FEIT | CD | 35 | 17.2 | No | 2020-02-26 | B2_s1_d0 | 0.4 | 5.6 | 7.6 | 1500 | 22.7 | B2 | 0 | 0 | s1 | n | n | d0
TN_2020_1915 |  | 75005 20316992 | 667288N | EXZHELLENT RZ1-K (AS) 1 KV 2X16 | 15.63 | 9 | Manlleu | 0400FEIT | CD | 35 | 18.4 | No | 2020-02-19 | B2_s1_d1 | 0.8 | 10.6 | 15 | 1389 | 33 | B2 | 1.3 | 0 | s1 | y | n | d1
TN_2020_1916 |  | 75268 | 647427A | H07Z1-K 1X240 | 24.69 | 7 | Vilanova | PENDINGTOCONFIRM | CD | 61.1 | 11.8 | No | 2020-02-21 | B2_s1_d2 | 0.56 | 7.4 | 10.7 | 801 | 22.8 | B2 | 9.5 | 0.02 | s1 | n | y | d2
TN_2020_1917 |  | 706222 20303007 | 576652W | EXZHELLENT SOLAR ABRERA 1X6 MM2 | 5.67 | 25 | Vilanova | TPR-20+TPS02 | CD | 58.9 | 12.7 | No | 2020-02-21 | E ou F_s2_d2 | 3.3 | 64 | 425.1 | 732 | 984.1 | E ou F | 98.1 | 0.32 | s2 | n | y | d2
TN_2020_1918 |  | 20302889 | 632243W | EXZHELCOMPACT RZ1-K (AS) 1KV 1X185 | 24.01 | 7 | Vilanova | PENDINGTOCONFIRM | CD | 56.7 | 14 | No | 2020-02-21 | B2_s1_d2 | 0.38 | 4 | 8.2 | 1470 | 14.4 | B2 | 5.4 | 0.01 | s1 | n | y | d2
TN_2020_1919 |  | 83269089 20303005 | 590078P | EXZHELLENT SOLAR ABRERA 1X4 MM2 | 5.49 | 30 | Vilanova | TPR-20+TPS02 | CD | 50.1 | 17.3 | No | 2020-02-21 | E ou F_s2_d2 | 3.3 | 62.8 | 405.3 | 711 | 986 | E ou F | 83.2 | 0.26 | s2 | n | y | d2
TN_2020_1920 |  | 83436927 20154478 | 652788C | PRYSUN SPM 1X4 MM2 | 5.82 | 25 | Vilanova | SV4120ES | CD | 46.7 | 13.6 | No | 2020-02-21 | D_s1_d2 | 3.3 | 54.2 | 271.6 | 681 | 722.2 | D | 46.5 | 0.15 | s1 | n | y | d2
TN_2020_1925 |  | 75962 20319996 | 676984C | HEPRZ1(AS) 12/20 KV 1X120 | 37.6 | 5 | Vilanova | 14202.5MM+61AA2.7MM | CD | 62.6 | 14.1 | No | 2020-02-24 | B2_s1_d1 | 0.71 | 11.9 | 14.5 | 909 | 36.8 | B2 | 8.9 | 0.04 | s1 | y | n | d1
TN_2020_1926 |  | 83497482 20184154 | 552289P | LXHIOZ1 1X240 15KV | 39.14 | 5 | Vilanova | 1420+6000 | CD | 61.7 | 14.3 | No | 2020-02-24 | D_s1_d2 | 1.77 | 45 | 62.2 | 1413 | 79.1 | D | 28.8 | 0.16 | s1 | n | y | d2
TN_2020_1927 |  | 831168717 20221312 | 573062U | PRYSUN SPM 1X6 MM2 | 6 | 25 | Vilanova | SV4120ES | CD | 57.1 | 16.7 | No | 2020-02-24 | D_s1_d2 | 3.3 | 42.9 | 252.8 | 618 | 798.4 | D | 48.6 | 0.12 | s1 | n | y | d2
CEL-0078 |  | 74883 | 614000S | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.56 | 8 | CEIS | LE0592+XLPE4201+LE0492+RELLENOCPR1420SEES+COBERTACPR1602SEES | CD | 85 | 14.26 | No | 2020-02-17 | C_s1_d2 | 1.15 | 25.2 | 49.8 | 1500 | 44.9 | C | 27.5 | 0.06 | s1 | n | y | d2
20020013 |  | 18216 | I66481 | ARG18OM16NM16 3X16 804/130 | 30 | 6 | Paron | SV55AAUNDERJACKET–WBTAPE–GALVANIZEDSTEELTAPE70%OVERLAP-CFR13TAPE50%OVERLAP-5300SEIT | -- | 37.4 | 22.3 | No | 2020-02-24 | B2_s2_d2 | 0.68 | 14.4 | 29.1 | 1500 | 41.7 | B2 | 50.2 | 0.15 | s2 | y | y | d2
20020014 |  | 18216 | I66481 | ARG18OM16NM16 3X16 804/130 | 30 | 6 | Paron | SV55AAUNDERJACKET–WBTAPE–GALVANIZEDSTEELTAPE70%OVERLAP-CFR13TAPE50%OVERLAP-5300SEIT | -- | 38.1 | 21.9 | No | 2020-02-24 | B2_s1_d2 | 0.6 | 9.9 | 19.8 | 1500 | 31.9 | B2 | 29.1 | 0.11 | s1 | y | y | d2
TN_2020_1929 |  | 74590 20319871 | 639946U | RZ1F3Z1-K 1KV 2X25MM² + 2FO | 16.5 | 9 | Vilanova | 1602SEES+TPR55 | CD | 56.9 | 16.1 | No | 2020-02-25 | B2_s1_d1 | 0.42 | 11.5 | 21.5 | 849 | 39.2 | B2 | 8.2 | 0.02 | s1 | y | n | d1
TN_2020_1930 |  | 72661 | T7-F89184 | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.23 | 13 | Vilanova | SXLPE+0300FEIT+16AASEIT | CD | 56.1 | 17 | No | 2020-02-25 | C_s1_d2 | 0.9 | 23.3 | 32.6 | 930 | 58.1 | C | 18.4 | 0.04 | s1 | n | y | d2
TN_2020_1932 |  | 75962 20319996 | 676984C | HEPRZ1(AS) 12/20 KV 1X120 | 37.6 | 5 | Vilanova | 14202.5MM+61AA2.7MM | CD | 54.5 | 18.5 | No | 2020-02-25 | B2_s1_d1 | 0.72 | 14 | 16.2 | 925 | 46.9 | B2 | 7.4 | 0.02 | s1 | y | n | d1
TN_2020_1931 |  |  | T8-G67892 | AFUMEX CLASS RZ1-K (AS) 1KV 3X25 | 21.78 | 7 | Vilanova | SXLPE+1420FEES+1500SEES | CD | 44.1 | 15.9 | No | 2020-02-26 | B2_s1_d0 | 0.56 | 4.7 | 12.2 | 1500 | 12 | B2 | 4.4 | 0.01 | s1 | n | n | d0
20020016 |  | 18216 | I66484 | ARG18OM16NM16 3X16 804/130 | 30 | 6 | Paron | SV55AAUNDERJACKET–WBTAPE–GALVANIZEDSTEELTAPE70%OVERLAP-CFR13TAPE50%OVERLAP-56ACSEIT | -- | 34.1 | 22.6 | No | 2020-02-24 | B2_s1_d2 | 0.65 | 12.6 | 18.8 | 1500 | 35.3 | B2 | 11.7 | 0.04 | s1 | y | y | d2
20020017 |  | 18216 | I66484 | ARG18OM16NM16 3X16 804/130 | 30 | 6 | Paron | SV55AAUNDERJACKET–WBTAPE–GALVANIZEDSTEELTAPE70%OVERLAP-CFR13TAPE50%OVERLAP-56ACSEIT | -- | 34.5 | 21.9 | No | 2020-02-24 | B2_s1_d2 | 0.7 | 11.6 | 21.3 | 1317 | 36.6 | B2 | 23.9 | 0.09 | s1 | y | y | d2
TN_2020_1934 |  | 74440 | 544247Y | HEPRHZ1-2OL 1X150 MM2 10 KV | 36.76 | 5 | Vilanova | 14202.14MM+60001.93MM | CD | 41 | 12.5 | No | 2020-03-03 | C_s1_d2 | 1.23 | 22.7 | 38.7 | 1272 | 51.5 | C | 22 | 0.07 | s1 | n | y | d2
TN_2020_1935 |  | 74441 | 671398F | HEPRHZ1-2OL 1X300 MM2 10 KV | 43.67 | 5 | Vilanova | 14201.66MM+60001.99MM | CD | 40.6 | 13.1 | No | 2020-03-03 | D_s1_d2 | 1.33 | 32.4 | 40.5 | 897 | 107.7 | D | 29.1 | 0.06 | s1 | n | y | d2
TN_2020_1936 |  | 20326301 | 520636J | RHZ1(AS) 25 KV 3X70 AL-AFUMEX RD+GR FULLY | 64.32 | 3 | Vilanova | 14203.1MM+60003.0MM | CD | 41.6 | 14.9 | No | 2020-03-03 | C_s1_d2 | 0.65 | 16.2 | 27.7 | 1095 | 34.9 | C | 3.5 | 0.01 | s1 | n | y | d2
TN_2020_1937 |  | 74533 20318513 | 644781Z | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.27 | 17 | Manlleu | XLPE+56AC1.40MM | -- | 32 | 20.3 | No | 2020-02-28 | D_s2_d2 | 3.3 | 51.4 | 199.4 | 876 | 347.3 | D | 76 | 0.34 | s2 | n | y | d2
TN_2020_1938 |  | 74535 20318515 | 509550J | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.2 | 17 | Manlleu | XLPE+TPR-351.40MM | -- | 30 | 20.3 | No | 28/02/20 | C_s1_d0 | 1.65 | 13.6 | 18.4 | 636 | 57.3 | C | 19.8 | 0.06 | s1 | n | n | d0
TN_2020_1939 |  | 74184 20317076 | 522919R | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 10.89 | 14 | Manlleu | XLPE+56AC1.40MM | -- | 34 | 17.7 | No | 2020-02-28 | D_s2_d2 | 3.3 | 5.1 | 20.2 | 1011 | 28.4 | D | 108.8 | 0.45 | s2 | n | y | d2
TN_2020_1940 |  | 74184 20317076 | 644778W | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 10.71 | 14 | Manlleu | XLPE+TPR-351.40MM | -- | 33 | 20.4 | No | 28/02/20 | C_s1_d1 | 1.75 | 24.4 | 38.1 | 1500 | 63.8 | C | 19.4 | 0.06 | s1 | y | n | d1
TN_2020_1944 |  | 60084091 | 5096573 | LT TKEST 48F B2CA-S1B.D1.A1 | 15.51 | 9 | Vilanova | TPR-37 | CD | 72.8 | 13.8 | No | 2020-03-05 | C_s1_d0 | 0.56 | 16.2 | 35.1 | 780 | 73.4 | C | 13.8 | 0.02 | s1 | n | n | d0
TN_2020_1945 |  | AFO-357 60075217 | 5096572 | LT TVT CCA-S1B.D1.A1 | 14.4 | 11 | Vilanova | MEGOLONS548 | CD | 69.1 | 16.3 | No | 2020-03-05 | C_s1_d0 | 0.79 | 25.2 | 28.8 | 1275 | 73.9 | C | 27.7 | 0.05 | s1 | n | n | d0
TN_2020_1946 |  | 60061646 | 5096571 | 32 FXT VT B2CA-S1A.D2.A1 | 10.21 | 15 | Vilanova | CYGSA | CD | 57.7 | 19.7 | No | 2020-03-05 | C_s1_d2 | 1.71 | 21.6 | 39.3 | 579 | 226.8 | C | 23.7 | 0.04 | s1 | n | y | d2
20020005 |  | 17903 | -- | 750 NE -SH-70MM²-CT 442-PRYSMIAN | -- | -- | Efectis | ID3100FR/SV3300FR+SV3200FR | -- | 35.3 | 9.89 | No | 2020-02-28 | C_s1_d2 | 1.4 | 18.7 | 33.3 | 1185 | 38.2 | C | 40.5 | 0.09 | s1 | y | y | d2
2003005 |  | 18217 | 544365B | PROT XGB CCA-S1B.D2.A1 0.6/1KV 3G240MM² | 51.8 | 4 | Paron | SXLPE+1400FEIT+1602SEES | -- | 44.7 | 18.8 | No | 2020-03-05 | B2_s1_d0 | 0.55 | 8 | 8.9 | 1425 | 27.4 | B2 | 12.8 | 0.02 | s1 | n | n | d0
20020006 |  | 18189 | FBM 194806 | 28 P ZPFU | 32.6 | 5 | Paron | 3000GVFR+SW3800FR | -- | 43 | 20.2 | No | 2020-03-05 | B2_s1_d0 | 0.35 | 8.2 | 10.1 | 1497 | 34.3 | B2 | 13.3 | 0.03 | s1 | n | n | d0
20020007 |  | 18189 | GBL 1861569 | 28 P ZPAU | 34.5 | 5 | Paron | TPR248+TPS290 | -- | 45.7 | 20.6 | No | 2020-03-05 | B2_s1_d0 | 0.3 | 7.5 | 8.9 | 1143 | 20.2 | B2 | 5.8 | 0.01 | s1 | n | n | d0
20020008 |  | 18189 | GBL 183439 | 28 P ZPFU | 32.6 | 6 | Paron | TPR248+TPS290 | -- | 41 | 21.2 | No | 2020-03-05 | B2_s1_d2 | 0.4 | 13.1 | 17.9 | 1203 | 28.2 | B2 | 13 | 0.03 | s1 | y | y | d2
20020015 |  | 18153 | I31029 | PRYSMIAN FG16M16 1 KV 5G1.5 | 13.2 | 12 | Paron | SXLPE+0300FDIT+5310SEIT | -- | 37.1 | 22 | No | 2020-02-24 | C_s1_d2 | 0.95 | 16.6 | 29.5 | 1050 | 39.4 | C | 24.8 | 0.05 | s1 | y | y | d2
20020018 |  | 18153 | I31029 | PRYSMIAN FG16M16 1 KV 5G1.5 | 13.2 | 12 | Paron | SXLPE+0300FDIT+5310SEIT | -- | 29 | 22.8 | No | 2020-02-25 | C_s1_d2 | 0.78 | 15.2 | 24.3 | 1089 | 35.7 | C | 19.4 | 0.05 | s1 | y | y | d2
20020019 |  | 18153 | H21395 | PRYSMIAN FG16M16 1 KV 1X240 | 28.7 | 6 | Paron | SXLPE+0300FDIT+5300SEIT | -- | 26.5 | 20.8 | No | 2020-02-26 | B2_s1_d0 | 0.27 | 5.5 | 7 | 1500 | 17 | B2 | 5 | 0.01 | s1 | n | n | d0
20020020 |  | 18153 | H21395 | PRYSMIAN FG16M16 1 KV 1X240 | 28.7 | 6 | Paron | SXLPE+0300FDIT+5300SEIT | -- | 28 | 19.8 | No | 2020-02-26 | B2_s1_d0 | 0.33 | 5.3 | 7.1 | 1500 | 16.2 | B2 | 6.9 | 0.01 | s1 | n | n | d0
20020021 |  | 18153 | I28430 | PRYSMIAN FG16M16 1 KV 1X16 | 10.4 | 15 | Paron | SXLPE+0300FDIT+5300SEIT | -- | 29.6 | 19.6 | No | 2020-02-26 | C_s1_d1 | 0.95 | 15 | 31 | 969 | 48.2 | C | 37.3 | 0.09 | s1 | y | n | d1
20020022 |  | 18153 | I28430 | PRYSMIAN FG16M16 1 KV 1X16 | 10.4 | 15 | Paron | SXLPE+0300FDIT+5300SEIT | -- | 26.6 | 20.2 | No | 2020-02-28 | C_s1_d1 | 1 | 18.6 | 33.1 | 906 | 58.8 | C | 34 | 0.1 | s1 | y | n | d1
20020023 |  | 18153 | H83939 | PRYSMIAN FG16M16 1 KV 1X240 | 28.7 | 6 | Paron | SXLPE+0300FDIT+5310SEIT | -- | 29.4 | 19.7 | No | 2020-02-28 | B2_s1_d0 | 0.27 | 7.8 | 9.2 | 726 | 28.9 | B2 | 6.7 | 0.01 | s1 | n | n | d0
20020024 |  | 18153 | H83939 | PRYSMIAN FG16M16 1 KV 1X240 | 28.7 | 6 | Paron | SXLPE+0300FDIT+5310SEIT | -- | 29.4 | 20 | No | 2020-02-28 | B2_s1_d0 | 0.3 | 7.7 | 9.4 | 1476 | 22.1 | B2 | 7 | 0.01 | s1 | n | n | d0
20030001 |  | 18153 | H8633 | PRYSMIAN AGR16R16 1 KV 1X16 | 9.4 | 17 | Paron | SXLPE+05AMFPIT+20AHSPIT | -- | 34.8 | 20.9 | No | 2020-03-02 | B2_s2_d1 | 1 | 13 | 26.1 | 660 | 110.2 | B2 | 299.1 | 0.69 | s2 | y | n | d1
20030002 |  | 18153 | H8663 | PRYSMIAN AGR16R16 1 KV 1X16 | 9.4 | 17 | Paron | SXLPE+05AMFPIT+20AHSPIT | -- | 35.8 | 20.7 | No | 2020-03-02 | B2_s2_d1 | 1 | 11.5 | 25.9 | 696 | 80.5 | B2 | 250.2 | 0.57 | s2 | y | n | d1
20030003 |  | 18153 | H53104 | PRYSMIAN AGR16R16 1 KV 1X400 | 33.3 | 6 | Paron | SXLPE+05AMFPIT+20AHSPIT | -- | 30.4 | 20 | No | 2020-03-03 | D_s3_d2 | 1.35 | 17.1 | 60.9 | 1500 | 50.9 | D | 501.4 | 1.17 | s3 | y | y | d2
20030004 |  | 18153 | H53104 | PRYSMIAN AGR16R16 1 KV 1X400 | 33.3 | 6 | Paron | SXLPE+05AMFPIT+20AHSPIT | -- | 28.1 | 19.8 | No | 2020-03-03 | C_s3_d2 | 1.25 | 18.9 | 44.1 | 1455 | 47.6 | C | 421.8 | 0.7 | s3 | y | y | d2
TN_2020_1950 |  |  | 5096570 | PRYSMINA 2F G657 A1 INDOOR OUTDOOR DROP CABLE 2019 | 4.53 | 60 | Vilanova | PENDINGTOCONFIRM | CD | 50.2 | 15.6 | No | 2020-03-09 | D_s1_d1 | 2.12 | 30.3 | 42.5 | 663 | 117.9 | D | 22.7 | 0.05 | s1 | y | n | d1
TN_2020_1953 |  | 74441 | 671398F | HEPRHZ1-2OL 1X300 MM2 10 KV | 43.67 | 5 | Vilanova | 14201.66MM+60001.99MM | CD | 65.2 | 12.9 | No | 2020-03-11 | D_s1_d2 | 1.62 | 34.5 | 60.4 | 1155 | 70.6 | D | 21.5 | 0.07 | s1 | n | y | d2
TN_2020_1954 |  | 74440 | 544247Y | HEPRHZ1-2OL 1X150 MM2 10 KV | 36.76 | 5 | Vilanova | 14202.14MM+60001.93MM | CD | 63.6 | 13.5 | No | 2020-03-11 | C_s1_d2 | 1.56 | 28.2 | 32.2 | 1311 | 72.9 | C | 28.7 | 0.1 | s1 | n | y | d2
TN_2020_1955 |  | 74184 20317076 | 644778W | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 10.71 | 14 | Vilanova | XLPE+TPR-351.40MM | CD | 57.4 | 16.2 | No | 2020-03-11 | D_s2_d2 | 3.3 | 69.1 | 220.1 | 1500 | 183.4 | D | 84.4 | 0.21 | s2 | n | y | d2
TN_2020_1956 |  | 83505003 20308921 | 5096850 | RHZ1-RA+2OL (AS) 76/132 KV 1X1200 AL | 97.36 | 2 | Vilanova | TPO04 | CD | 53.4 | 19 | No | 2020-03-11 | D_s1_d2 | 0.93 | 31.1 | 57.7 | 1380 | 53.4 | D | 13.3 | 0.03 | s1 | n | y | d2
TN_2020_1957 |  | 74535 20318515 | 509550J | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.2 | 17 | Vilanova | XLPE+TPR-351.40MM | CD | 54 | 20.4 | No | 2020-03-11 | D_s1_d2 | 3.3 | 37.9 | 75.1 | 1500 | 67.2 | D | 47.6 | 0.1 | s1 | n | y | d2
TN_2020_1908 rep |  | 75134 20326365 | 634729Y | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11.97 | 13 | Manlleu | XLPE--0400FEIT0.5MM+1602SEES1.4MM | -- | 31 | 20.6 | No | 2020-03-06 | D_s1_d2 | 2.3 | 39.7 | 56.9 | 1041 | 85.3 | D | 23.9 | 0.06 | s1 | n | y | d2
TN_2020_1964 |  | 5096820 5096821 |  | FS 17 LA TRIVENETA | 2.75 | 180 | Manlleu | COMPETITORSAMPLE | -- | 31 | 17.3 | No | 2020-03-06 | B2_s2_d0 | 0.82 | 6.6 | 16.1 | 453 | 131.4 | B2 | 314.5 | 1.41 | s2 | n | n | d0
TN_2020_1965 |  | 83550377 20302936 | 5096826 | EXZHELLENT COMPACT RZ1-K 1KV 3G1.5 | 9.6 | 15 | Manlleu | TPR-49+TPR-54 | -- | 30 | 18 | No | 2020-03-06 | B2_s1_d0 | 1.1 | 13.4 | 21.5 | 669 | 59.3 | B2 | 23.7 | 0.07 | s1 | n | n | d0
TN_2020_1967 |  | 83553261 20302900 | 671723J | EXZHELLENT COMPACT RZ1-K 1KV 3G2.5 | 10.51 | 14 | Manlleu | TPR-49+TPR-54 | -- | 34 | 20 | No | 2020-03-12 | B2_s1_d0 | 0.85 | 12.9 | 19 | 771 | 47.6 | B2 | 10.7 | 0.03 | s1 | n | n | d0
TN_2020_1966 |  | 75431 20329226 | 661459C | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.38 | 15 | Manlleu | 0400+1600 | -- | 33 | 16.8 | No | 2020-03-06 | D_s1_d2 | 2.15 | 33.3 | 50.6 | 512 | 88.4 | D | 32.7 | 0.09 | s1 | n | y | d2
TN_2020_1959 |  | 75265 20328349 | 672473Z | AFUMEX ROZ1-K 12X3X0.75 MM | 23.02 | 7 | Vilanova | 1420+1602 | CD | 72 | 14.1 | No | 2020-03-13 | C_s1_d1 | 0.82 | 18.6 | 37.7 | 1500 | 44.2 | C | 21.4 | 0.05 | s1 | y | n | d1
TN_2020_1960 |  | 75141 20395470 | 643951X | AFUMEX ROZ1-K 12X3X0.75 MM | 22.19 | 7 | Vilanova |  | CD | 72.8 | 15.2 | No | 2020-03-13 | C_s1_d2 | 0.65 | 17.2 | 35.7 | 1500 | 55.8 | C | 16.7 | 0.05 | s1 | n | y | d2
TN_2020_1961 |  | 20215475 | I25158 | FG16OR16 24G1.5 MM² - 0.6/1 KV | 23.32 | 7 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 73.1 | 16.8 | No | 2020-03-13 | D_s2_d2 | 1.23 | 32.5 | 56.9 | 1266 | 624 | D | 399.1 | 0.77 | s2 | n | y | d2
TN_2020_1962 |  | 20215184 | H92277 | FG16R16 1X240MM² - 0.6/1 KV | 28.6 | 6 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 67.7 | 18.2 | No | 2020-03-13 | D_s2_d2 | 1.66 | 39.4 | 85 | 1365 | 322.2 | D | 377.2 | 0.97 | s2 | n | y | d2
TN_2020_1963 |  | 20215159 | F89154 | FG16R16 1X16MM² - 0.6/1 KV | 9.98 | 15 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 61.5 | 20.4 | No | 2020-03-13 | D_s2_d1 | 0.65 | 15.7 | 43.6 | 366 | 697.4 | D | 66.6 | 0.2 | s2 | y | n | d1
TN_2020_1968 |  |  |  | EXZHELLENT ES05Z1-K 1X1 AZUL | 2.44 | 249 | Manlleu | PENDINGTOCONFIRM | -- | 34 | 19.3 | No | 2020-03-12 | C_s2_d1 | 1.86 | 22.2 | 37.9 | 843 | 81.7 | C | 54.9 | 0.16 | s2 | y | n | d1
20030009 |  | 18152 | CE6707 | 750-5G1.5-SH-NF F 55-625-255 | 14.6 | 10 | Paron | IX1400FR+07AAFEIT+5300SEIT | -- | 31.6 | 20 | No | 2020-03-06 | C_s1_d2 | 0.95 | 17.9 | 26.6 | 1497 | 39 | C | 25 | 0.04 | s1 | y | y | d2
20030013 |  | 18152 | CE 6706 | 750-5G1.5-SH-NF F 55-625-255 | 14.6 | 10 | Paron | IX1400FR+07ANFEIT+5300SEIT | -- | 40.4 | 22.7 | No | 2020-03-10 | B2_s1_d2 | 0.75 | 12.9 | 20.6 | 1182 | 28.3 | B2 | 22.1 | 0.05 | s1 | y | y | d2
20030018 |  | 18218 | GL0ME8S | 1A641211RJ 1X300MM² CU 12/20KV ISH 25M | 40.6 | 5 | Paron | TPS246–GAINERISHILOFABRIQUÉEÀMTCÀMONTEREAU+CATALYSEUR+COLORANT | -- | 35.1 | 22.2 | No | 2020-03-16 | B2_s1_d1 | 0.33 | 6.8 | 10.3 | 1455 | 17.7 | B2 | 9.9 | 0.02 | s1 | y | n | d1
20030019 |  | 18239 | DV144FS | K209 À 12 FIBRES | 13.1 | 12 | Paron | TPS246+TPR248+ECCOH6151 | -- | 36.2 | 22.2 | No | 2020-03-16 | B2_s1_d0 | 0.27 | 5.2 | 9 | 666 | 31.8 | B2 | 9.6 | 0.02 | s1 | n | n | d0
20020008 |  | 18153 | I30866 | PRYSMIAN FG16M16 1 KV 1X16 | 10.4 | 15 | Paron | SXLPE+0300FDIT+5310SEIT | -- | 29 | 21 | No | 2020-02-19 | B2_s1_d2 | 0.9 | 12.2 | 24 | 861 | 32 | B2 | 32 | 0.07 | s1 | y | y | d2
TN_2020_1970 |  | 83550377 20302936 | 5096826 | EXZHELLENT COMPACT RZ1-K 1KV 3G1.5 | 9.6 | 15 | Vilanova | TPR-49+TPR-54 | CD | 69.8 | 14.2 | No | 2020-03-18 | C_s1_d0 | 1.56 | 21.7 | 36.6 | 1257 | 45.8 | C | 49.2 | 0.1 | s1 | n | n | d0
TN_2020_1971 |  | 76284 20316601 |  | HEPRHZ1-2OL 6/10 KV 1X300 + H50 B2CAS1AD1A1 | 44.21 | 5 | Vilanova | 0400FEIT+TPR37 | CD | 70 | 14.3 | No | 2020-03-18 | B2_s2_d0 | 0.42 | 4.3 | 14.8 | 1485 | 17.9 | B2 | 50.8 | 0.07 | s2 | n | n | d0
TN_2020_1972 |  | 83505003 20308921 | 5096850 | RHZ1-RA+2OL (AS) 76/132 KV 1X1200 AL | 97.36 | 2 | Vilanova | TPO04 | CD | 68.1 | 15.4 | No | 2020-03-18 | B2_s1_d2 | 0.59 | 14.4 | 25.3 | 1371 | 31.8 | B2 | 6.4 | 0.01 | s1 | n | y | d2
TN_2020_1973 |  |  | 5096580 | 32 FXT VT B2CA-S1A.D2.A1 | 10.05 | 15 | Vilanova | CYGSA | CD | 64.6 | 16.6 | No | 2020-03-18 | D_s1_d2 | 1.35 | 19.5 | 47.4 | 453 | 309.5 | D | 22.5 | 0.04 | s1 | n | y | d2
TN_2020_1974 |  |  | 5096579 | LT TKEST 48F B2CA-S1B.D1.A1 | 15.39 | 10 | Vilanova | TPR-37 | CD | 58.1 | 18.1 | No | 2020-03-18 | C_s1_d0 | 0.65 | 19.2 | 34.9 | 867 | 61.5 | C | 29.9 | 0.05 | s1 | n | n | d0
|  | 74536 20318516 | 676892C | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 11.04 | 14 | Manlleu | XLPE+25%19AA+56AC+5300SEIT | -- | 42 | 19.8 | No | 2020-03-17 | D_s2_d2 | 3.3 | 58.1 | 93.7 | 927 | 177.7 | D | 60 | 0.13 | s2 | n | y | d2
|  | 74535 20318515 | 669175P | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.34 | 17 | Manlleu | XLPE+25%19AA+56AC+5300SEIT | -- | 37 | 19.1 | No | 2020-03-17 | D_s1_d2 | 2.02 | 33.6 | 61.6 | 774 | 134.9 | D | 18.3 | 0.04 | s1 | n | y | d2
|  | 74533 20326368 | 676890A | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.1 | 13 | Manlleu | XLPE+0400+5300INOEX0.036 | -- | 42 | 20.1 | No | 2020-03-17 | C_s1_d2 | 1.6 | 26.8 | 54.5 | 960 | 82.9 | C | 6.2 | 0.02 | s1 | n | y | d2
|  | 74533 20326368 | 676895F | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.3 | 13 | Manlleu | XLPE+0400+5300INOEX0.054 | -- | 44 | 18.8 | No | 2020-03-17 | C_s1_d2 | 1.22 | 16.6 | 33.5 | 1023 | 49.3 | C | 3.4 | 0.01 | s1 | n | y | d2
|  | 74533 20326366 | 676920H | AFUMEX CLASS RZ1-K (AS) 1KV 2X16 | 17.45 | 9 | Manlleu | SXLPE+0400FEIT+5300SEIT | -- | 41 | 20.6 | No | 2020-03-17 | B2_s1_d2 | 0.8 | 13.2 | 21.8 | 1341 | 29.5 | B2 | 0.8 | 0.01 | s1 | n | y | d2
20030021 |  | 18218 | GL0K6WS | GENERAL CABLE 6 HERSATENE 2018 NFC33226- 240² AL- 6/10(12)KV EC0.1- C1 ISH | 33.5 | 5 | Paron | TPS246–GAINERISHILOFABRIQUÉEÀMTCÀMONTEREAU+CATALYSEUR+COLORANT | -- | 43 | 21.4 | No | 2020-03-18 | B2_s1_d2 | 0.35 | 9.2 | 15.1 | 1497 | 18.4 | B2 | 18.7 | 0.05 | s1 | y | y | d2
20030022 |  | 18190 | XCP06198134 | PK26-001-COAX-VS8 K20 75 | 10.2 | 15 | Paron | AXELERONCC3485NTCPD+SW3800FR | -- | 42.7 | 21.8 | No | 2020-03-18 | C_s2_d2 | 1.3 | 15.9 | 46.4 | 672 | 132.2 | C | 84.6 | 0.2 | s2 | y | y | d2
20030023 |  | 18190 | VCP02173895 | PK26-002-COAX-VS6 K20 75 | 6.1 | 25 | Paron | AXELERONCC3485NTCPD+SW3800FR | -- | 39.8 | 21.4 | No | 2020-03-18 | D_s2_d2 | 3.1 | 28.2 | 64.4 | 696 | 240.4 | D | 150.3 | 0.28 | s2 | y | y | d2
20030024 |  | 17903 | -- | 750 NE -SH-70MM²-CT 442-PRYSMIAN | 18.7 | 8 | Paron | ID3100FR/SV3300FR+SV3200FR | -- | 33.3 | 22.8 | No | 2020-03-18 | B2_s1_d2 | 0.8 | 11.4 | 24.6 | 1500 | 21.6 | B2 | 39.3 | 0.11 | s1 | y | y | d2
20030016 |  | 17903 | -- | 750 NE -SH-70MM²-CT 442-PRYSMIAN | 17.8 | 9 | Paron | ID3100FR/SV3300FR+SV3200FR | -- | 43.8 | 23.4 | No | 2020-03-18 | D_s2_d2 | 1.75 | 33.6 | 64.4 | 33.6 | 63.2 | D | 85.1 | 0.022 | s2 | y | y | d2
TN_2020_1975 |  | 76284 20316601 |  | HEPRHZ1-2OL 6/10 KV 1X300 + H50 B2CAS1AD1A1 | 44.21 | 5 | Vilanova | HEPR+0400FEIT+TPR37 | CD | 70.9 | 12.2 | No | 2020-03-19 | B2_s1_d0 | 0.3 | 4.2 | 6.6 | 588 | 22.8 | B2 | 5.3 | 0.01 | s1 | n | n | d0
TN_2020_1976 |  | 74965 20316993 | 667287M | EXZHELLENT RZ1-K (AS) 1 KV 5G1.5 | 11.97 | 13 | Vilanova | SXLPE+0400FEIT+1602SEES | CD | 71.9 | 12.5 | No | 2020-03-19 | C_s1_d0 | 0.67 | 14.2 | 36.1 | 990 | 52.4 | C | 15.6 | 0.06 | s1 | n | n | d0
TN_2020_1977 |  | 74533 20326368 | 676890A | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.1 | 13 | Vilanova | SXLPE+0400FEIT+5300SEITINOEX0.036 | CD | 69.1 | 15.6 | No | 2020-03-19 | C_s1_d1 | 0.38 | 13.8 | 35.8 | 684 | 93.2 | C | 4.7 | 0.01 | s1 | y | n | d1
20030025 |  | 17903 | -- | 750 NE -SH-70MM²-CT 442-PRYSMIAN | 18.7 | 8 | Paron | ID3100FR/SV3300FR+SV3200FR | -- | 34.2 | 23.8 | No | 2020-03-20 | C_s2_d2 | 1.1 | 20.3 | 42.1 | 1314 | 42 | C | 62 | 0.16 | s2 | y | y | d2
20030026 |  | 18250 | EBM 217155 | 750-5G10-SH-NF F 55-625-255 | 20.6 | 7 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 32.8 | 23.7 | No | 2020-03-20 | B2_s1_d0 | 0.35 | 6.3 | 7.8 | 717 | 27 | B2 | 8 | 0.01 | s1 | n | n | d0
20030020 |  | 18102 | -- | K25 750V 1X1.5 -SH-NF F 55-625-255 ( IRRADIÉ) | 3.3 | 135 | Paron | 1602SEES | -- | 36.9 | 22 | No | 2020-03-16 | B2_s2_d1 | 1.15 | 14 | 29.3 | 759 | 100.2 | B2 | 67.1 | 0.17 | s2 | y | n | d1
TN_2020_1980 |  | 20215475 | I25158 | FG16OR16 24G1.5 MM² - 0.6/1 KV | 23.32 | 7 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 76.6 | 15.28 | No | 2020-03-23 | C_s3_d0 | 1.17 | 23.5 | 45.1 | 1149 | 53.4 | C | 583.5 | 0.94 | s3 | n | n | d0
TN_2020_1987 |  |  | 5096566 | FG16OR16 5G1.5 MM² - 0.6/1 KV | 11.53 | 13 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 64 | 12.87 | No | 2020-03-24 | B2_s2_d1 | 0.64 | 8 | 23.8 | 630 | 72.7 | B2 | 185.3 | 0.58 | s2 | y | n | d1
TN_2020_1988 |  |  | 5096560 | FG16OR16 3G1.5 MM² - 0.6/1 KV | 9.78 | 15 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 63.6 | 13.59 | No | 2020-03-24 | B2_s2_d0 | 0.65 | 9.7 | 17.8 | 528 | 80.1 | B2 | 148.9 | 0.55 | s2 | n | n | d0
TN_2020_1989 |  | 74535 20318515 | 509550J | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.2 | 17 | Vilanova | XLPE+TPR-351.40MM | CD | 56.9 | 17.36 | No | 2020-03-24 | B2_s1_d0 | 0.43 | 7.8 | 14.3 | 627 | 48.3 | B2 | 8 | 0.03 | s1 | n | n | d0
TN_2020_1990 |  | 83551994 20193654 | 635403F | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.65 | 14 | Vilanova | XLPE+1420+1602 | CD | 50.7 | 18.04 | No | 2020-03-24 | C_s1_d1 | 1.73 | 22.7 | 32.1 | 984 | 68.6 | C | 17.1 | 0.05 | s1 | y | n | d1
TN_2020_1991 |  | 83553261 20302900 | 671723J | EXZHELLENT COMPACT RZ1-K 1KV 3G2.5 | 10.51 | 14 | Vilanova | TPR-49+TPR-54 | CD | 48.1 | 17.36 | No | 2020-03-24 | B2_s1_d0 | 1.07 | 11.7 | 18.8 | 768 | 40.1 | B2 | 21.1 | 0.08 | s1 | n | n | d0
TN_2020_1992 |  | 74533 20326368 | 676890A | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.1 | 13 | Vilanova | SXLPE+0400FEIT+5300SEITINOEX0.036 | CD | 45.4 | 11.95 | No | 2020-03-25 | C_s1_d2 | 1 | 15.3 | 25.5 | 750 | 56.7 | C | 21.5 | 0.04 | s1 | n | y | d2
TN_2020_1994 |  | 74533 20326368 | 676895F | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.3 | 13 | Vilanova | XLPE+0400+5300INOEX0.054 | CD | 50.6 | 12.93 | No | 2020-03-25 | B2_s1_d2 | 0.37 | 9.8 | 17.8 | 813 | 35.7 | B2 | 15.8 | 0.03 | s1 | n | y | d2
20030027 |  | 18102 | -- | K25 750V 1X1 -SH-NF F 55-625-255 ( IRRADIÉ) | 3 | 165 | Paron | 16FASEES | -- | 21 | 19.7 | No | 2019-03-26 | C_s2_d1 | 1.5 | 23.4 | 41.5 | 726 | 140 | C | 93 | 0.24 | s2 | y | n | d1
20030028 |  | 18102 | -- | K25 750V 1X1 -SH-NF F 55-625-255 ( IRRADIÉ) | 3 | 165 | Paron | 16GASEES | -- | 22.8 | 20 | No | 2019-03-26 | D_s2_d0 | 3.3 | 54.4 | 79.5 | 807 | 182 | D | 132 | 0.21 | s2 | n | n | d0
20030029 |  | 18224 | -- | GENERAL CABLE 6 HERSATENE 334 2018 NFC33226 50AL 12/20(24)KV EC0.15 C1 ISH | 28.8 | 6 | Paron | TPS246–GAINERISHILOFABRIQUÉEÀMTCÀMONTEREAU+CATALYSEUR+COLORANT | -- | 25.1 | 23.4 | No | 2020-03-27 | C_s1_d2 | 1.75 | 17.7 | 43.5 | 1500 | 36.2 | C | 33.9 | 0.08 | s1 | y | y | d2
CEL-0242/20-1 |  | 75141 20395470 | 643951X | AFUMEX ROZ1-K 12X3X0.75 MM | 22.19 | 7 | CEIS |  | -- | 44 | 9.83 | No | 2020-03-30 | C_s1_d0 | 0.94 | 16.2 | 40.4 | 1401 | 36.8 | C | 18.2 | 0.06 | s1 | n | n | d0
CEL-0249/20-1 |  | 74965 20316993 | 667287M | EXZHELLENT RZ1-K (AS) 1 KV 5G1.5 | 11.97 | 13 | CEIS | SXLPE+0400FEIT+1602SEES | -- | 44 | 10.09 | No | 2020-03-30 | C_s1_d1 | 0.98 | 21 | 33.5 | 858 | 61 | C | 35.7 | 0.06 | s1 | y | n | d1
CEL-0251/20-1 |  | 75005 20316992 | 667288N | EXZHELLENT RZ1-K (AS) 1 KV 2X16 | 15.63 | 9 | CEIS | SXLPE+0400FEIT+1602SEES | -- | 46 | 9.49 | No | 2020-03-30 | C_s1_d0 | 0.73 | 15.5 | 23.9 | 1269 | 26.8 | C | 12.5 | 0.03 | s1 | n | n | d0
TN_2020_1995 |  | 20215159 | F89154 | FG16R16 1X16MM² - 0.6/1 KV | 9.98 | 15 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 58.1 | 7.6 | No | 2020-03-27 | B2_s2_d0 | 0.5 | 4.2 | 10.9 | 561 | 50.1 | B2 | 67.7 | 0.38 | s2 | n | n | d0
TN_2020_1996 |  | 20215159 | F89154 | FG16R16 1X16MM² - 0.6/1 KV | 9.98 | 15 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 57.3 | 8.03 | No | 2020-03-27 | B2_s2_d0 | 0.45 | 4.5 | 11.4 | 561 | 48.2 | B2 | 74.6 | 0.33 | s2 | n | n | d0
TN_2020_1997 |  |  | 5096566 | FG16OR16 5G1.5 MM² - 0.6/1 KV | 11.53 | 13 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 73.7 | 16.74 | No | 2020-04-14 | B2_s2_d1 | 1.12 | 12.7 | 27 | 606 | 88.2 | B2 | 226.5 | 0.66 | s2 | y | n | d1
TN_2020_1998 |  | 74811 20320760 | 627468F | RHZ1MZ1 (AS) 3X185MM2 10KV | 70.77 | 3 | Vilanova | XLPE+1602+1602 | CD | 66.8 | 20.61 | No | 2020-04-14 | B2_s1_d0 | 0.39 | 4 | 5.2 | 1440 | 14.6 | B2 | 0 | 0 | s1 | n | n | d0
TN_2020_1999 |  | 75521 / 83588410 20327919 | 552309L | RHZ1-OL(AS) 20KV 1X400 | 49.77 | 4 | Vilanova | XLPE+1420+6000 | CD | 59.7 | 19.94 | No | 2020-04-14 | C_s1_d2 | 0.95 | 24.6 | 34.6 | 1347 | 42.9 | C | 13.3 | 0.04 | s1 | n | y | d2
TN_2020_2000 |  | 74184 20317076 | 644778W | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 10.71 | 14 | Vilanova | XLPE+TPR-351.40MM | CD | 70.9 | 16.63 | No | 2020-04-16 | D_s2_d2 | 3.3 | 52.1 | 121.5 | 1476 | 103.4 | D | 82.8 | 0.31 | s2 | n | y | d2
TN_2020_2001 |  |  | 5096585 | LT TKEST 48F B2CA-S1B.D1.A1 | 15.43 | 10 | Vilanova | TPR-37 | CD | 67.7 | 16.75 | No | 2020-04-16 | B2_s1_d0 | 0.71 | 10 | 15.9 | 1077 | 30 | B2 | 21 | 0.05 | s1 | n | n | d0
TN_2020_2002 |  |  | 5096584 | 32 FXT VT B2CA-S1A.D2.A1 | 10.01 | 15 | Vilanova | CYGSA | CD | 61.1 | 18.74 | No | 2020-04-16 | C_s1_d2 | 1.3 | 27.9 | 34.6 | 645 | 138.1 | C | 14 | 0.05 | s1 | n | y | d2
TN_2020_2003 |  | 75195 20327982 | 680282M | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.37 | 8 | Vilanova | LE0592+XLPE4201+LE0492+CINTACU25%+RELLENOCPR1420SEES+COBERTACPR1602SEES | CD | 61 | 19.88 | No | 2020-04-16 | D_s2_d2 | 1.75 | 51.6 | 91.7 | 1494 | 107.6 | D | 98.6 | 0.25 | s2 | n | y | d2
TN_2020_2004 |  | 75191 20327590 | 680336W | AL AFUMEX CLASS 1KV RZ1 (AS) 1X16 MM² | 9.93 | 15 | Vilanova | XLPE+TPR55 | CD | 81.5 | 16.98 | No | 2020-04-20 | C_s1_d1 | 0.36 | 26 | 35.2 | 1458 | 67.4 | C | 5.7 | 0.01 | s1 | y | n | d1
TN_2020_2005 |  | 75192 20327589 | 687784S | AL AFUMEX CLASS 1KV RZ1 (AS) 1X300 MM² | 28.4 | 6 | Vilanova | XLPE+TPR55 | CD | 81.3 | 17.61 | No | 2020-04-20 | B2_s1_d1 | 0.38 | 7.3 | 9.3 | 1464 | 24.4 | B2 | 12.4 | 0.02 | s1 | y | n | d1
TN_2020_2006 |  |  | 5096560 | FG16OR16 3G1.5 MM² - 0.6/1 KV | 9.78 | 15 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 74.3 | 15.78 | No | 2020-04-17 | B2_s2_d0 | 0.8 | 9 | 22.6 | 528 | 101.2 | B2 | 232.6 | 0.66 | s2 | n | n | d0
TN_2020_2007 |  | 75195 20327982 | 680281L | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.29 | 8 | Vilanova | LE0592+XLPE4201+LE0492+CINTACU50%+RELLENOCPR1420SEES+COBERTACPR1602SEES | CD | 73.1 | 15.65 | No | 2020-04-17 | D_s2_d2 | 1.68 | 41.4 | 102.5 | 1500 | 87.5 | D | 87.2 | 0.24 | s2 | n | y | d2
TN_2020_2008 |  | 83553276 20302925 | 667997J | EXZHELLENT COMPACT RZ1-K 1KV 5G10 | 17.47 | 9 | Vilanova | INS:PRS-03SKINTPR53;SHEATH:TPR49SKINTPR54 | CD | 69.3 | 19.25 | No | 2020-04-17 | B2_s1_d0 | 0.32 | 4.4 | 5.7 | 1494 | 23.3 | B2 | 0 | 0 | s1 | n | n | d0
TN_2020_2009 |  | 83447738 20302865 | 667525W | EXZHELLENT CLASS H07Z1-K (AS) 1KV 1X35 | 10.26 | 15 | Vilanova | TPR-27 | CD | 67.1 | 18.99 | No | 2020-04-17 | B2_s1_d0 | 0.29 | 2.7 | 6.9 | 495 | 40 | B2 | 1.8 | 0.01 | s1 | n | n | d0
TN_2020_2010 |  | 75530 20317801 | 5096569 | H07Z1-K 750V 1X1.5 | 2.92 | 165 | Vilanova | TPR-56AFUMEXVILANOVA1602 | CD | 81 | 17.16 | No | 2020-04-20 | B2_s2_d0 | 1.19 | 11.3 | 27.2 | 687 | 91.7 | B2 | 61.1 | 0.19 | s2 | n | n | d0
TN_2020_2011 |  | 83505003 20308921 | 5096850 | RHZ1-RA+2OL (AS) 76/132 KV 1X1200 AL | 97.36 | 2 | Vilanova | TPO04 | CD | 81.4 | 16.64 | No | 2020-04-20 | B2_s1_d2 | 0.57 | 6.5 | 14.3 | 1491 | 15.8 | B2 | 7.5 | 0.01 | s1 | n | y | d2
TN_2020_2012 |  | 75137 20218519 | 656552U | AFUMEX CLASS FIRS MRZ1-K 1X2.5 | 8.25 | 19 | Vilanova | CU+MICA+XLPE+1420+1602 | CD | 81.8 | 18.17 | No | 2020-04-20 | C_s1_d0 | 1.29 | 18.5 | 26.3 | 783 | 79.1 | C | 38.9 | 0.08 | s1 | n | n | d0
TN_2020_2013 |  | 75138 20218533 | 680332S | AFUMEX CLASS FIRS MRZ1-K 1X240 | 28.64 | 6 | Vilanova | CU+MICA+XLPE+1420+1602 | CD | 82.1 | 15.89 | No | 2020-04-21 | B2_s1_d2 | 0.7 | 11.2 | 25 | 1230 | 26.9 | B2 | 10.6 | 0.03 | s1 | n | y | d2
TN_2020_2014 |  | 75139 20218508 | 671138Y | AFUMEX CLASS FIRS MRZ1-K 5X1.5 | 14.01 | 11 | Vilanova | CU+MICA+XLPE+1420+1602 | CD | 85.5 | 16.23 | No | 2020-04-21 | C_s1_d2 | 0.89 | 16.2 | 28.2 | 1011 | 40.3 | C | 18.4 | 0.04 | s1 | n | y | d2
TN_2020_2015 |  | 75268 20328397 | 627074C | H07Z1-K 750V 1X240 | 24.89 | 7 | Vilanova | TPR-56AFUMEXVILANOVA1602 | CD | 84.5 | 16.42 | No | 2020-04-21 | C_s1_d2 | 0.45 | 22.6 | 33.7 | 1407 | 47.8 | C | 5.1 | 0.01 | s1 | n | y | d2
TN_2020_2016 |  | 75200 20327985 | 678620F | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.54 | 8 | Vilanova | LE0592+XLPE4201+LE0492+CU25+MICA+LANTOR+RELLENOCPR1420SEES+COBERTACPR1602SEES | CD | 82.6 | 16.82 | No | 2020-04-21 | C_s1_d2 | 1.07 | 24.5 | 50.3 | 1359 | 48 | C | 32 | 0.09 | s1 | n | y | d2
TN_2020_2018 |  | 76250 20307072 | 682005K | EXZHELLENT XXI H07Z1-R TYPE 2 (AS) 1X70 PT | 12.79 | 12 | Vilanova | TPR-32 | CD | 61.1 | 21.17 | No | 2020-04-24 | B2_s1_d1 | 0.27 | 6 | 9 | 1500 | 43.6 | B2 | 3.8 | 0 | s1 | y | n | d1
TN_2020_2019 |  | 75191 20327590 | 680337X | AL AFUMEX CLASS 1KV RZ1(AS) 1X16 MM2 | 9.97 | 15 | Vilanova | XLPE+TPR-37 | CD | 72.9 | 15.19 | No | 2020-04-24 | B2_s1_d2 | 0.51 | 6.8 | 13.3 | 762 | 33.3 | B2 | 8.1 | 0.02 | s1 | n | y | d2
TN_2020_2020 |  | 83505003 20308921 | 5096850 | RHZ1-RA+2OL (AS) 76/132 KV 1X1200 AL | 97.36 | 2 | Vilanova | TPO04 | CD | 81.4 | 16.64 | No | 2020-04-23 | B2_s1_d2 | 0.57 | 6.8 | 14.8 | 1491 | 15.8 | B2 | 7.6 | 0.01 | s1 | n | y | d2
TN_2020_2021 |  | 75521 / 83588410 20327919 | 552309L | RHZ1-OL(AS) 20KV 1X400 | 49.77 | 4 | Vilanova | XLPE+1420+6000 | CD | 66 | 22.84 | No | 2020-04-23 | C_s1_d2 | 1.03 | 24.3 | 32.3 | 1245 | 45.5 | C | 10.1 | 0.03 | s1 | n | y | d2
TN_2020_2022 |  | 74811 20320760 | 627468F | RHZ1MZ1 (AS) 3X185MM2 10KV | 70.77 | 3 | Vilanova | XLPE+1602+1602 | CD | 54.5 | 23.28 | No | 2020-04-23 | B2_s1_d0 | 0.52 | 4 | 5.1 | 549 | 19.8 | B2 | 2 | 0 | s1 | n | n | d0
|  | 75530 20317801 | 5096569 | H07Z1-K 750V 1X1.5 | 2.92 | 165 | Manlleu | TPR-56AFUMEXVILANOVA1602 | -- | 60 | 19.1 | No | 2020-04-21 | C_s1_d0 | 1.34 | 13.5 | 33.3 | 639 | 103.7 | C | 46.4 | 0.18 | s1 | n | n | d0
|  | 83595713 20302921 | 661594Z | EXZHELLENT COMPACT RZ1-K 5G1.5 | 11.7 | 13 | Manlleu | TPR-49+TPR-54 | -- | 54 | 19.7 | No | 2020-04-21 | D_s1_d0 | 2.48 | 35.3 | 43.1 | 1362 | 77.9 | D | 15.7 | 0.05 | s1 | n | n | d0
|  | 74535 20318515 | 509550J | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 9.2 | 17 | Manlleu | XLPE+TPR-351.40MM | -- | 54 | 19.9 | No | 2020-04-21 | D_s1_d2 | 3.3 | 41 | 52.2 | 1128 | 77.9 | D | 22.5 | 0.04 | s1 | n | y | d2
|  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Manlleu | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | -- | 58 | 19.6 | No | 2020-04-21 | C_s1_d0 | 1.37 | 24.9 | 39.5 | 894 | 70.3 | C | 31.9 | 0.09 | s1 | n | n | d0
|  | 83651900 20302890 | 708671V | RZ1-K 1X240 | 26.05 | 6 | Manlleu | PRS-03+TPR-54 | -- | 54 | 19.9 | No | 2020-04-21 | B2_s1_d2 | 0.81 | 9 | 17.9 | 1470 | 18.5 | B2 | 1.6 | 0.01 | s1 | n | y | d2
|  | 76080 20302894 | 706516C | SZ1-K (AS+) 3G4 | 13.2 | 12 | Manlleu | TPR-49+TPR-37 | -- | 54 | 19.6 | No | 2020-04-21 | B2_s1_d0 | 0.74 | 9 | 14.1 | 972 | 36.7 | B2 | 2.1 | 0.01 | s1 | n | n | d0
TN_2020_2023 |  | 75196 20327983 | 678622H | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.45 | 8 | Vilanova | LE0592+XLPE4201+LE0492+CU+LANTOR+RELLENOCPR1420SEES+COBERTACPR1602SEES | CD | 72 | 15.12 | No | 2020-04-24 | C_s2_d2 | 1.23 | 26.6 | 59.7 | 1491 | 54.7 | C | 57.8 | 0.18 | s2 | n | y | d2
TN_2020_2024 |  | 83612820 | 680541U | AL AFUMEX CLASS 1KV RZ1 (AS) 1X240MM² | 28.45 | 7 | Vilanova | PENDINGTOCONFIRM | CD | 67.3 | 18.82 | No | 2020-04-24 | B2_s1_d2 | 0.3 | 3.9 | 6.2 | 1500 | 19.9 | B2 | 4.7 | 0.01 | s1 | n | y | d2
TN_2020_2025 |  | 75192 20327589 | 687786U | AL AFUMEX CLASS 1KV RZ1 (AS) 1X300MM² | 28.5 | 6 | Vilanova | XLPE+TPR-37 | CD | 65.2 | 20.24 | No | 2020-04-24 | C_s1_d2 | 0.87 | 16.3 | 36.2 | 1452 | 32.3 | C | 12.2 | 0.05 | s1 | n | y | d2
20050001 |  | 18269 | -- | 750 NE -SH-70MM²-CT 442-PRYSMIAN | 18.8 | 8 | Paron | ID3800FR/SV3200FR+SV3200FR | -- | 33.5 | 23.4 | No | 2020-05-12 | B2_s1_d1 | 0.4 | 5.5 | 9.5 | 1095 | 23.1 | B2 | 8.5 | 0.02 | s1 | y | n | d1
20050002 |  | 18274 | -- | FR-N1X1G1 5G1.5MM² | 14.4 | 11 | Paron | IX1400FR+MEGOLONS670 | -- | 30.3 | 21.9 | No | 2020-05-12 | D_s2_d2 | 2.85 | 66.8 | 125.2 | 1458 | 116.6 | D | 91.4 | 0.19 | s2 | y | y | d2
TN_2020_2028 |  |  | 5096584 | 32 FXT VT B2CA-S1A.D2.A1 | 10.01 | 15 | Vilanova | CYGSA | CD | 66.6 | 14.6 | No | 2020-04-29 | B2_s1_d0 | 0.55 | 4.9 | 15.3 | 606 | 86.6 | B2 | 6.9 | 0.02 | s1 | n | n | d0
TN_2020_2029 |  | 74533 20326368 | 676895F | AFUMEX CLASS RZ1-K (AS) 1KV 5G1.5 | 12.3 | 13 | Vilanova | XLPE+0400+5300INOEX0.054 | CD | 67.9 | 14.98 | No | 2020-04-29 | B2_s1_d2 | 0.65 | 7.1 | 14.9 | 813 | 31.2 | B2 | 15.6 | 0.03 | s1 | n | y | d2
TN_2020_2030 |  | 75139 20218508 | 671138Y | AFUMEX CLASS FIRS MRZ1-K 5X1.5 | 14.01 | 11 | Vilanova | CU+MICA+XLPE+1420+1602 | CD | 69.9 | 18.03 | No | 2020-04-29 | D_s1_d2 | 1.71 | 38.8 | 58.2 | 1251 | 68.1 | D | 23.8 | 0.05 | s1 | n | y | d2
TN_2020_2031 |  | 75138 20218533 | 680332S | AFUMEX CLASS FIRS MRZ1-K 1X240 | 28.64 | 6 | Vilanova | CU+MICA+XLPE+1420+1602 | CD | 63.6 | 19.68 | No | 2020-04-29 | B2_s1_d2 | 0.7 | 14.4 | 29.4 | 1203 | 33.3 | B2 | 14.4 | 0.03 | s1 | n | y | d2
TN_2020_2032 |  | 83670928 20302972 | 689907Z | SEGURFOC CLASS RZ1-K-M 1KV 1X70 NJ | 17.34 | 9 | Vilanova | TPR-49B-600EVA+TPR-37NARANJA | CD | 57.3 | 17.4 | No | 2020-04-30 | B2_s1_d1 | 0.77 | 11.7 | 19.7 | 1500 | 24 | B2 | 13.8 | 0.03 | s1 | y | n | d1
TN_2020_2033 |  | 83670920 20302975 | 702882C | SEGURFOC CLASS RZ1-K-M 1KV 1X150 NJ | 20 | 7 | Vilanova | TPR-49B-600EVA+TPR-37NARANJA | CD | 55.7 | 17.68 | No | 2020-04-30 | C_s1_d0 | 0.39 | 15.2 | 24.1 | 1497 | 47.3 | C | 3 | 0 | s1 | n | n | d0
TN_2020_2034 |  | 83611447 20302936 | 5096589 | EXZHELLENT COMPACT RZ1-K 3G1.5 | 9.85 | 15 | Vilanova | INS:PE+TPR-53BEDDING:TPR-49SHEATH:TPR-54 | CD | 47.5 | 22.65 | No | 2020-04-30 | B2_s1_d0 | 0.43 | 6.3 | 15.7 | 681 | 42.6 | B2 | 5.5 | 0.01 | s1 | n | n | d0
TN_2020_2035 |  | 83640132 20302900 | 708008Z | EXZHELLENT COMPACT RZ1-K 3G2.5 | 10.27 | 15 | Vilanova | INS:PE+TPR-53BEDDING:TPR-49SHEATH:TPR-54 | CD | 41.4 | 24.65 | No | 2020-04-30 | B2_s1_d0 | 0.47 | 8.5 | 15.2 | 744 | 42.6 | B2 | 10 | 0.03 | s1 | n | n | d0
TN_2020_2036 |  | 75258 20327889 | 680322F | RHOZ1MZ1 500V 4X2X0.5 2RH | 16.5 | 9 | Vilanova | XLPE+GFR380+SWSA+GFR380 | CD | 53.4 | 23.26 | No | 2020-05-07 | B2_s1_d1 | 0.34 | 5 | 9.2 | 951 | 19.2 | B2 | 11.9 | 0.02 | s1 | y | n | d1
TN_2020_2037 |  | 83551994 20193654 | 672596H | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.61 | 14 | Vilanova | XLPE+1420+1602 | CD | 64.2 | 18.36 | No | 2020-05-07 | C_s1_d2 | 1.52 | 19.7 | 28.7 | 774 | 61.2 | C | 46.7 | 0.14 | s1 | n | y | d2
TN_2020_2038 |  | 83551994 20193654 | 675882E | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.62 | 14 | Vilanova | XLPE+1420+1602 | CD | 61.8 | 18.69 | No | 2020-05-07 | C_s1_d2 | 1.33 | 15.4 | 22.4 | 825 | 43.3 | C | 29.2 | 0.09 | s1 | n | y | d2
TN_2020_2039 |  | 83551994 20193654 | 609882R | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10.78 | 14 | Vilanova | XLPE+1420+1602 | CD | 57.9 | 22.15 | No | 2020-05-07 | B2_s1_d1 | 1.04 | 12.4 | 20.5 | 744 | 46.1 | B2 | 21.4 | 0.05 | s1 | y | n | d1
TN_2020_2040 |  | 75199 20327984 | 717091X | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 15.23 | 8 | Vilanova | LE0592+4201+LE0594/CUTAPE25%+MICATAPE/1420+1602SEES | CD | 48.3 | 24.8 | No | 2020-05-07 | C_s1_d2 | 1.05 | 26.7 | 53.2 | 1500 | 45.2 | C | 37.7 | 0.08 | s1 | n | y | d2
TN_2020_2042 |  |  | 5096773 | EXZHELLENT XXI RZ1-K (AS) 1 KV 3G1.5 | 9.69 | 15 | Vilanova | INTERCOMPARISON | CD | 45.3 | 24.22 | No | 2020-05-27 | B2_s1_d2 | 0.68 | 9.2 | 18.9 | 714 | 46.1 | B2 | 17.7 | 0.03 | s1 | n | y | d2
TN_2020_2044 |  | 60083270 | 712003S | KEMFLAM LT-M1G0M1 72FO | 16.2 | 9 | Vilanova | 1602+6010 | CD | 53.9 | 24.29 | No | 2020-05-20 | E ou F_s1_d2 | 3.3 | 133.3 | 217.4 | 1125 | 283.5 | E ou F | 41.3 | 0.07 | s1 | n | y | d2
TN_2020_2045 |  | 75543 20329100 | 662984K | CNE TSL1(F) 145 KV 1X400 | 77.21 | 3 | Vilanova | 60AC+SKINLE0563 | CD | 62.3 | 20.45 | No | 2020-05-20 | D_s1_d2 | 1.36 | 39.7 | 61.4 | 1431 | 63.8 | D | 20.8 | 0.03 | s1 | n | y | d2
TN_2020_2046 |  | 75543 20329100 | 662984K | CNE TSL1(F) 145 KV 1X400 | 77.21 | 3 | Vilanova | 60AC+SKINLE0563 | CD | 61.7 | 21.09 | No | 2020-05-22 | D_s1_d2 | 1.04 | 30.7 | 45.5 | 1149 | 53.6 | D | 26.5 | 0.05 | s1 | n | y | d2
TN_2020_2047 |  |  | 5096582 | FS17 1X1.5 | 2.86 | 165 | Vilanova | 28AM | CD | 60.1 | 26.08 | No | 2020-05-22 | C_s2_d0 | 1.08 | 6.3 | 25.9 | 450 | 195.4 | C | 183.3 | 0.88 | s2 | n | n | d0
TN_2020_2048 |  |  | TW-H21739 | ARG16R16 1X240 | 25.83 | 6 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 53.4 | 27.19 | No | 2020-05-22 | C_s2_d2 | 1.01 | 16.2 | 42.8 | 1467 | 36.7 | C | 195.8 | 0.41 | s2 | n | y | d2
TN_2020_2049 |  |  | T8-I90889 | FG16OR16 24X1.5 | 20.67 | 7 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 49.5 | 28.57 | No | 2020-05-22 | D_s3_d2 | 2.5 | 37.4 | 78.1 | 1497 | 75.5 | D | 647.3 | 1.41 | s3 | n | y | d2
TN_2020_2050 |  |  | TW-H97127 | ARG16R16 1X240 | 25.85 | 6 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 41.7 | 26.64 | No | 2020-05-22 | C_s2_d2 | 0.97 | 14.9 | 34.1 | 1248 | 36.1 | C | 203.9 | 0.39 | s2 | n | y | d2
TN_2020_2051 |  |  | T8-I90881 | FG16OR16 24X1.5 | 19.24 | 8 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 44.7 | 28.65 | No | 2020-05-22 | D_s3_d2 | 3.3 | 53.7 | 149.7 | 1422 | 133.4 | D | 973.9 | 2.95 | s3 | n | y | d2
TN_2020_2054 |  | 75190 20327645 | 688005G | AFUMEX CLASS FIRS RZ1-K 4X120 | 46.34 | 4 | Vilanova | MICA+XLPE+1420+1602 | CD | 58.4 | 20.77 | No | 2020-05-27 | B2_s1_d0 | 0.57 | 5.7 | 7.3 | 1467 | 16.8 | B2 | 3.8 | 0.01 | s1 | n | n | d0
TN_2020_2055 |  | 75530 20317801 | 5096592 | H07Z1-K 750V 1X1.5 | 2.89 | 165 | Vilanova | 1610+1510 | CD | 55.6 | 21.95 | No | 2020-05-27 | B2_s1_d1 | 1.3 | 12.7 | 29.8 | 687 | 101.2 | B2 | 35.6 | 0.14 | s1 | y | n | d1
TN_2020_2056 |  |  | 07 - I31553 | FG16R16 1.5 | 6.26 | 25 | Vilanova | SXLPE+05AMFPIT+20AHSPIT | CD | 40.6 | 25.54 | No | 2020-05-27 | B2_s2_d1 | 0.54 | 3.1 | 13 | 444 | 97.2 | B2 | 75.6 | 0.41 | s2 | y | n | d1
TN_2020_2057 |  | 75456 20282517 | 716998W | RHOZ1MZ1 500V 6X3X0.5 2RH | 21.17 | 7 | Vilanova | XLPE+GFR380+SWSA+GFR380 | CD | 66.2 | 19.58 | No | 2020-05-28 | B2_s1_d2 | 0.7 | 11.2 | 19.9 | 1455 | 20.7 | B2 | 18.8 | 0.04 | s1 | n | y | d2
TN_2020_2058 |  | 75458 20314925 | 710912F | RHOZ1MZ1 500V 24X2X0.5 2RH | 33.55 | 5 | Vilanova | XLPE+GFR380+SWSA+GFR380 | CD | 67.1 | 20.9 | No | 2020-05-28 | B2_s1_d1 | 0.45 | 3.6 | 6.6 | 1467 | 18.6 | B2 | 2.9 | 0.01 | s1 | y | n | d1
TN_2020_2059 |  | 75457 20315022 | 717019U | RHOZ1MZ1 500V 2X2X0.5 2RH | 14.52 | 10 | Vilanova | XLPE+GFR380+SWSA+GFR380 | CD | 65.1 | 23.07 | No | 2020-05-28 | B2_s1_d1 | 0.48 | 4.6 | 8.5 | 867 | 26 | B2 | 4.6 | 0.01 | s1 | y | n | d1
TN_2020_2060 |  | 75460 20270394 | 719890P | ROZ1MZ1 500V 1X2X2.5 2RH | 14.19 | 11 | Vilanova | XLPE+GFR380+SWSA+GFR380 | CD | 64.3 | 23.8 | No | 2020-05-28 | B2_s1_d1 | 0.41 | 8.3 | 14.5 | 873 | 28.7 | B2 | 9.5 | 0.04 | s1 | y | n | d1
TN_2020_2061 |  |  | 5096597 | TEST SAMPLE #90 PBT-FR + GEL FR (AFO415-1) | 16.05 | 9 | Vilanova | AFUMEXCPR+AFUMEXCPR | CD | 62.3 | 24.02 | No | 2020-05-28 | B2_s1_d0 | 0.66 | 14.1 | 22.6 | 927 | 45.1 | B2 | 43.6 | 0.08 | s1 | n | n | d0
TN_2020_2064 |  |  | 5096593 | TEST SAMPLE #94 PBT-FR + GEL FR (AFO417-2) | 14.59 | 10 | Vilanova | AFUMEXCPR | CD | 73.7 | 19.8 | No | 2020-06-01 | C_s2_d0 | 0.85 | 17.4 | 29.1 | 882 | 62.7 | C | 53.1 | 0.09 | s2 | n | n | d0
TN_2020_2065 |  |  | 5096599 | TEST SAMPLE #91 PBT-FR + GEL FR (AFO415-2) | 15.66 | 9 | Vilanova | AFUMEXCPR+AFUMEXCPR | CD | 73.3 | 20.79 | No | 2020-06-01 | C_s2_d1 | 1.09 | 21.8 | 33.3 | 990 | 59.6 | C | 80.5 | 0.16 | s2 | y | n | d1
TN_2020_2066 |  |  | 5096595 | TEST SAMPLE #93 PBT-FR + GEL FR (AFO417-1) | 14.03 | 11 | Vilanova | AFUMEXCPR | CD | 67.6 | 22.94 | No | 2020-06-01 | C_s2_d0 | 1.55 | 22.1 | 40.1 | 771 | 95.1 | C | 92.87 | 0.16 | s2 | n | n | d0
TN_2020_2067 |  | 20314610 | OF155 | HEPRZ1 (AS) 1X800MM2 36/66KV | 73.68 | 3 | Vilanova | 60ACSEES | CD | 63.8 | 24.4 | No | 2020-06-01 | C_s1_d2 | 0.75 | 21.1 | 41.3 | 1500 | 34.4 | C | 7.6 | 0.01 | s1 | n | y | d2
TN_2020_2068 |  |  | 646164C | RHZ1FA3Z1-2OL(AS) RR 30KV 1X400/16 AL AFUMEX | 56.41 | 4 | Vilanova | TPR28+TPR37 | CD | 66.2 | 20.46 | No | 2020-06-04 | B2_s1_d0 | 0.35 | 5.9 | 7.3 | 1326 | 15.8 | B2 | 5.4 | 0.02 | s1 | n | n | d0
TN_2020_2069 |  |  | 5096596 | TEST SAMPLE #95 PBT-FR + GEL FR (AFO417-3) | 15.02 | 10 | Vilanova | AFUMEXCPR | CD | 71.6 | 23.98 | No | 2020-06-03 | C_s2_d0 | 1.22 | 20.6 | 34.7 | 879 | 66.6 | C | 76.6 | 0.14 | s2 | n | n | d0
TN_2020_2070 |  |  | 5096594 | 32F FXT VT | 9.87 | 15 | Vilanova | PENDINGTOCONFIRM | CD | 63.1 | 26.45 | No | 2020-06-03 | C_s1_d2 | 1.78 | 13 | 27.7 | 705 | 85 | C | 18.8 | 0.04 | s1 | n | y | d2
TN_2020_2071 |  |  | 5096598 | TEST SAMPLE #92 PBT-FR + GEL FR (AFO415-3) | 16.69 | 9 | Vilanova | AFUMEXCPR+AFUMEXCPR | CD | 60.7 | 26.71 | No | 2020-06-03 | C_s2_d0 | 1.06 | 20.7 | 29.4 | 978 | 53.4 | C | 50.9 | 0.09 | s2 | n | n | d0
TN_2020_2072 |  | 83566120 20302899 | 711677M | EXZHELLENT COMPACT RZI-K 3G1.5 | 9.58 | 15 | Vilanova | TPR-49+TPR-54 | CD | 79.7 | 19.57 | No | 2020-06-04 | C_s1_d1 | 1.78 | 20.3 | 30.5 | 762 | 61.9 | C | 30.4 | 0.06 | s1 | y | n | d1
TN_2020_2073 |  | 75456 20282517 | 716998W | RHOZ1MZ1 500V 6X3X0.5 2RH | 21.17 | 7 | Vilanova | XLPE+GFR380+SWSA+GFR380 | CD | 78.4 | 19.99 | No | 2020-06-04 | B2_s1_d1 | 0.69 | 9 | 18.7 | 1500 | 26.3 | B2 | 18 | 0.04 | s1 | y | n | d1
TN_2020_2074 |  | 83638170 20302916 | 701648C | EXZHELLENT COMPACT RZI-K 4X10 | 16.46 | 9 | Vilanova | TPR-49+TPR-54 | CD | 72.6 | 19.64 | No | 2020-06-04 | B2_s1_d2 | 0.66 | 9.1 | 21.2 | 1491 | 18.1 | B2 | 7.5 | 0.02 | s1 | n | y | d2
TN_2020_2075 |  | 83595713 20302921 | 716520B | EXZHELLENT COMPACT RZI-K 5G1.5 | 12.07 | 13 | Vilanova | TPR-49+TPR-54 | CD | 67.6 | 21.02 | No | 2020-06-04 | C_s1_d0 | 1.46 | 18.3 | 23.9 | 1209 | 72.3 | C | 9 | 0.07 | s1 | n | n | d0
TN_2020_2076 |  | 83719177 20302822 | 5096591 | EXZHELLENT CLASS H07Z1-K 1X2.5 | 3.51 | 120 | Vilanova | 1602SEESSKIN:TPR-53 | CD | 57.5 | 17.77 | No | 2020-06-05 | D_s1_d1 | 3.3 | 54.4 | 81.8 | 1140 | 143.2 | D | 47.6 | 0.08 | s1 | y | n | d1
TN_2020_2077 |  | 83634955 20193980 | 5096590 | AFUMEX CLASS H07Z1-K 750V 1X1.5 NEGRE | 2.89 | 165 | Vilanova | 1602SEESSKIN:TPR-53 | CD | 56 | 18.16 | No | 2020-06-05 | C_s2_d0 | 1.63 | 12 | 28.6 | 645 | 99.8 | C | 61.1 | 0.15 | s2 | n | n | d0
TN_2020_2078 |  | 76679 20335082 | 722632V | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.19 | 14 | Vilanova | 0400FEIT+1602SEES | CD | 52.1 | 20.5 | No | 2020-06-05 | C_s1_d2 | 1.98 | 28.4 | 40.3 | 1050 | 72.4 | C | 41.1 | 0.12 | s1 | n | y | d2
TN_2020_2079 |  | 83636274 20193689 | 5096601 | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.55 | 14 | Vilanova | 1420+1602 | CD | 43.8 | 24.07 | No | 2020-06-05 | D_s1_d2 | 2.2 | 29.1 | 42.3 | 1455 | 59.7 | D | 22.8 | 0.05 | s1 | n | y | d2
TN_2020_2080 |  | 76679 20335082 | 722632V | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.19 | 14 | Vilanova | 0400FEIT+1602SEES | CD | 67.8 | 15.99 | No | 2020-06-08 | D_s1_d2 | 1.98 | 31.8 | 51 | 1047 | 73.9 | D | 33.5 | 0.1 | s1 | t | n | d2
TN_2020_2081 |  | 76981 203336609 | 592620C | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.84 | 13 | Vilanova | XLPE/PAPER/1420+160210%1420 | CD | 63.5 | 17.15 | No | 2020-06-08 | D_s1_d2 | 3.3 | 46.5 | 98.5 | 1500 | 82.1 | D | 30.6 | 0.1 | s1 | n | y | d2
TN_2020_2082 |  | 76981 203336609 | 592624G | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.61 | 13 | Vilanova | XLPE+PA/1420+1602 | CD | 57.2 | 18.67 | No | 2020-06-08 | D_s1_d2 | 1.84 | 31.4 | 51 | 1278 | 64.5 | D | 34.6 | 0.07 | s1 | n | y | d2
TN_2020_2083 |  | 76981 203336609 | 707633S | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.9 | 13 | Vilanova | XLPE/PAPER/1420+16HA+ADD291 | CD | 53.6 | 20.87 | No | 2020-06-08 | C_s1_d2 | 1.35 | 20.7 | 27.3 | 1155 | 46.1 | C | 6.6 | 0.02 | s1 | n | y | d2
TN_2020_2084 |  | 76981 203336609 | 671138Y | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.58 | 13 | Vilanova | XLPE+PA/1420+160210%1420 | CD | 57.1 | 21.25 | No | 2020-06-08 | D_s1_d2 | 2.13 | 31.9 | 49.5 | 1272 | 59 | D | 22.2 | 0.04 | s1 | n | y | d2
TN_2020_2085 |  | 77319 20337630 | 717043V | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.08 | 13 | Vilanova | XLPE/PAPER/1420+16HAINDEX0.04 | CD | 67.4 | 16.25 | No | 2020-06-09 | C_s1_d2 | 1.69 | 24.7 | 38.5 | 984 | 68.6 | C | 23.1 | 0.04 | s1 | n | y | d2
TN_2020_2086 |  | 77320 20337631 | 718096P | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.66 | 12 | Vilanova | XLPE/PAPER/1420+16HAINDEX0.06 | CD | 64.7 | 17.02 | No | 2020-06-09 | C_s1_d2 | 1.39 | 22.5 | 34.7 | 1113 | 59.3 | C | 36.6 | 0.05 | s1 | n | y | d2
TN_2020_2087 |  | 77318 20337632 | 727648X | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 10.95 | 14 | Vilanova | XLPE/PAPER/16HA | CD | 72.7 | 16.32 | No | 2020-06-10 | D_s2_d2 | 3.3 | 10.5 | 153.5 | 1446 | 134 | D | 114.1 | 0.37 | s2 | n | y | d2
TN_2020_2088 |  | 77319 20337630 | 718098S | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.52 | 13 | Vilanova | XLPE/PAPER/1420+16HAINDEX0.02 | CD | 56.2 | 22.34 | No | 2020-06-09 | C_s1_d2 | 1.8 | 26.8 | 40.3 | 912 | 74.5 | C | 24.1 | 0.05 | s1 | n | y | d2
TN_2020_2089 |  | 76981 203336609 | 518514C | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.75 | 11.75 | Vilanova | XLPE/PAPER/1420+16HA+ADD290 | CD | 48.6 | 24.28 | No | 2020-06-09 | C_s1_d2 | 1.63 | 20.3 | 29.4 | 1077 | 53 | C | 18.2 | 0.04 | s1 | n | y | d2
TN_2020_2090 |  | 74180 20317062 | 718089G | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 10.88 | 14 | Vilanova | XLPE+INTUMESCENCE/PAPEL/1602SEES | CD | 67.6 | 17.65 | No | 2020-06-10 | D_s2_d2 | 3.3 | 55.7 | 78.4 | 1263 | 162.3 | D | 129 | 0.25 | s2 | n | y | d2
TN_2020_2091 |  | 76679 20335082 | 734372F | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.07 | 14 | Vilanova | 0400FEIT+1602SEES | CD | 61.9 | 19.97 | No | 2020-06-10 | C_s1_d1 | 1.48 | 20.1 | 29.3 | 942 | 66.1 | C | 48.5 | 0.12 | s1 | y | n | d1
TN_2020_2092 |  | 76981 20336609 | 708259X | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.72 | 13 | Vilanova | XLPE+PA/1420+16HA+ADD290 | CD | 54.9 | 21.98 | No | 2020-06-10 | E ou F_s2_d2 | 3.3 | 74.3 | 180.7 | 1398 | 164.9 | E ou F | 63 | 0.18 | s2 | n | y | d2
TN_2020_2093 |  | 76679 20335082 | 734372F | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.07 | 14 | Vilanova | 0400FEIT+1602SEES | CD | 50.6 | 23.28 | No | 2020-06-10 | D_s1_d2 | 3.3 | 64.9 | 168.4 | 1440 | 148 | D | 18.2 | 0.09 | s1 | n | y | d2
TN_2020_2094 |  | 76742 20335321 | 732624F | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.91 | 13 | Vilanova | RELLENOAFUMEXCPR-TPR54 | CD | 69.7 | 19.07 | No | 2020-06-11 | B2_s1_d1 | 0.67 | 11.1 | 17.4 | 903 | 29.6 | B2 | 23.3 | 0.07 | s1 | y | n | d1
TN_2020_2095 |  | 76915 20336395 | 732625G | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.14 | 14 | Vilanova | TPR+PAPER+TPR54 | CD | 69.5 | 19.62 | No | 2020-06-11 | C_s1_d2 | 1.33 | 15.8 | 10 | 843 | 42.2 | C | 26.7 | 0.04 | s1 | n | y | d2
TN_2020_2096 |  | 76913 20336393 | 732628K | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.08 | 14 | Vilanova | TPR+PAPER+TPR35 | CD | 68.2 | 20.94 | No | 2020-06-11 | C_s1_d1 | 1.45 | 20.2 | 27.7 | 1320 | 42.5 | C | 30 | 0.07 | s1 | y | n | d1
TN_2020_2097 |  | 76743 20335322 | 734365Y | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.12 | 13 | Vilanova | 0400FEIT+TPR54 | CD | 67.4 | 22.46 | No | 2020-06-11 | C_s1_d1 | 1.25 | 16.3 | 24.2 | 873 | 42.5 | C | 16.3 | 0.04 | s1 | y | n | d1
TN_2020_2098 |  |  | 5096611 | TEST SAMPLE 97 PBT-FR+GEL FR (AFO414-2) | 12.54 | 13 | Vilanova | AFUMEXCPR+AFUMEXCPR | CD | 64.4 | 22.98 | No | 2020-06-11 | C_s1_d0 | 1.07 | 15.6 | 26.2 | 750 | 73.2 | C | 20.1 | 0.04 | s1 | n | n | d0
TN_2020_2099 |  | 77319 20337630 | 717043V | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.08 | 13 | Vilanova | XLPE/PAPER/1420+16HAINDEX0.04 | CD | 79.4 | 19.87 | No | 2020-06-12 | D_s1_d2 | 1.99 | 32.7 | 55.6 | 1029 | 76.6 | D | 23.6 | 0.05 | s1 | n | y | d2
TN_2020_2100 |  |  | 5096608 | TEST SAMPLE 100 PBT-FR+GEL FR (AFO416-2) | 11.26 | 14 | Vilanova | AFUMEXCPR | CD | 75 | 20.2 | No | 2020-06-12 | B2_s1_d0 | 1.09 | 15 | 28.8 | 777 | 81 | B2 | 29.4 | 0.07 | s1 | n | n | d0
TN_2020_2101 |  |  | 5096613 | TEST SAMPLE 96 PBT-FR+GEL FR (AFO414-1) | 12.72 | 12 | Vilanova | AFUMEXCPR+AFUMEXCPR | CD | 62.6 | 22.41 | No | 2020-06-12 | C_s1_d0 | 1.15 | 23.4 | 33.3 | 999 | 75.7 | C | 32.7 | 0.08 | s1 | n | n | d0
TN_2020_2102 |  |  | 5096612 | TEST SAMPLE #99 PBT-FR+GEL FR (AFO416-1) | 10.56 | 14 | Vilanova | AFUMEXCPR | CD | 47.1 | 25.93 | No | 2020-06-12 | B2_s1_d0 | 1.28 | 13.3 | 29.3 | 708 | 84.2 | B2 | 26.3 | 0.07 | s1 | n | n | d0
20050004 |  | 18281 | -- | 1800-S-1*16-SH-NF F 55-625-255 | 14.4 | 10 | Paron | ID3100FR/SV3300FR+SV3200FR | -- | 32.3 | 20.4 | No | 2020-05-15 | B2_s1_d2 | 0.85 | 12 | 20.6 | 1155 | 36.5 | B2 | 23.6 | 0.05 | s1 | y | y | d2
20050005 |  | 18281 | -- | 1800-S-1*16-SH-NF F 55-625-255 | 15.3 | 10 | Paron | IX1400FR+0400FEIT+5300SEIT | -- | 31 | 21.4 | No | 2020-05-15 | B2_s1_d2 | 0.8 | 13.9 | 23.2 | 1200 | 33.8 | B2 | 18.6 | 0.03 | s1 | y | y | d2
20060001 |  | 18316 | -- | ZPUF-SH-14P1MM²-CT445-PRYSMIAN 255 | 24.9 | 7 | Paron | PEHD+3000GV+SW3800FR | -- | 57.6 | 23.8 | No | 2020-06-12 | B2_s1_d2 | 0.83 | 14.1 | 29.7 | 1500 | 32.5 | B2 | 42.7 | 0.1 | s1 | y | y | d2
20060002 |  | 18316 | -- | ZPFU- SH- 2P1MM²- CT445- PRYSMIAN 255 | 12.6 | 12 | Paron | PEHD+3000GV+SW3800FR | -- | 56.6 | 24.1 | No | 2020-06-12 | B2_s1_d2 | 0.9 | 14.5 | 29.2 | 744 | 67.9 | B2 | 42.2 | 0.12 | s1 | y | y | d2
TN_2020_2103 |  | OF339 | 466477R | RHZ1-RA+2OL (AS) 76/132 KV 1X1000 | 95.2 | 2 | Vilanova | 60AC+SKIN30%DMZ-E+70%LE0563 | CD | 68.6 | 18.37 | No | 2020-06-17 | C_s1_d2 | 0.86 | 25.2 | 51.7 | 1464 | 44.7 | C | 5.7 | 0.01 | s1 | y | y | d2
TN_2020_2104 |  | 76475 | 705952P | CCTSST FR 0.3 10X4X1.4 | 36.79 | 5 | Vilanova | RELLENOAFUMEXCPR+TPR55 | CD | 58.9 | 26.43 | No | 2020-06-16 | B2_s1_d0 | 0.21 | 4.2 | 6.4 | 627 | 19.7 | B2 | 4.4 | 0.01 | s1 | n | n | d0
TN_2020_2105 |  | 76474 | 687920P | CCTSST FR 0.3 48X1.4 | 28.74 | 6 | Vilanova | RELLENOAFUMEXCPR+TPR55 | CD | 58.9 | 26.68 | No | 2020-06-16 | B2_s1_d1 | 0.17 | 3.3 | 5.2 | 552 | 19.4 | B2 | 4.8 | 0.01 | s1 | y | n | d1
TN_2020_2106 |  | 76915 20336395 | 732625G | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.14 | 14 | Vilanova | TPR+PAPER+TPR54 | CD | 60.5 | 26.92 | No | 2020-06-16 | B2_s1_d0 | 0.96 | 12 | 14.7 | 1347 | 33.6 | B2 | 9.1 | 0.03 | s1 | n | n | d0
TN_2020_2107 |  | 76742 20335321 | 732624F | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.91 | 13 | Vilanova | RELLENOAFUMEXCPR-TPR54 | CD | 60.7 | 26.55 | No | 2020-06-16 | B2_s1_d1 | 0.66 | 8.6 | 13.1 | 813 | 30.6 | B2 | 12.5 | 0.03 | s1 | y | n | d1
TN_2020_2108 |  | 76913 20336393 | 732628K | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.08 | 14 | Vilanova | TPR+PAPER+TPR35 | CD | 60.4 | 26.76 | No | 2020-06-16 | D_s1_d2 | 2.5 | 34.8 | 64.8 | 1488 | 55.7 | D | 42.9 | 0.12 | s1 | n | y | d2
20060003 |  | 18316 | -- | ZPFU- SH- 2P1MM²- CT445- PRYSMIAN 255 | 12.6 | 12 | Paron | PEHD+3000GV+SW3800FR | -- | 57.2 | 24.3 | No | 2020-06-16 | B2_s1_d2 | 0.8 | 12.7 | 24.2 | 840 | 49 | B2 | 48 | 0.1 | s1 | y | y | d2
20060004 |  | 18316 | -- | ZPUF-SH-14P1MM²-CT445-PRYSMIAN 255 | 24.8 | 7 | Paron | PEHD+3000GV+SW3800FR | -- | 54 | 23.8 | No | 2020-06-16 | B2_s1_d0 | 0.67 | 6.1 | 20.5 | -- | 17 | B2 | 29 | 0.11 | s1 | n | n | d0
TN_2020_2109 |  | 75866 | 599575M | CCTSST (X) FR 0.1 1X4X1.4 1Z93149U8P | 16.46 | 9 | Vilanova | RELLENOAFUMEXCPR+TPR55 | CD | 68.6 | 20.04 | No | 2020-06-16 | B2_s1_d2 | 0.37 | 8.1 | 11.9 | 1380 | 19.6 | B2 | 6.9 | 0.01 | s1 | n | y | d2
TN_2020_2110 |  | 76391 | 687922S | CCTSST (X) FR 0.3 5X4X1.4 | 27.57 | 6 | Vilanova | RELLENOAFUMEXCPR+TPR55 | CD | 70.3 | 19.12 | No | 2020-06-16 | B2_s1_d1 | 0.33 | 5.1 | 7.8 | 1497 | 24.4 | B2 | 3.5 | 0.02 | s1 | y | n | d1
TN_2020_2111 |  | 76390 | 544582M | CCTSST (H) FR 0.3 4X1.4 | 28.33 | 6 | Vilanova | RELLENOAFUMEXCPR+TPR55 | CD | 66.1 | 21.82 | No | 2020-06-16 | B2_s1_d0 | 0.36 | 5 | 6.5 | 606 | 25.7 | B2 | 2.3 | 0 | s1 | n | n | d0
TN_2020_2114 |  | 74801 20292827 | 729239B | AL ROZ1-K DCA TELEMANDO SEC 1KV 2X25 | 20.07 | 8 | Vilanova | XLPE+PET+CINTAAL/PET+1602SEES | CD | 72.2 | 18.8 | No | 2020-06-18 | C_s1_d2 | 0.7 | 18.8 | 31.6 | 882 | 54.3 | C | 39.4 | 0.07 | s1 | n | y | d2
CEL-0533_20-1 |  | 74801 20292827 | 729239B | AL ROZ1-K DCA TELEMANDO SEC 1KV 2X25 | 20 | 8 | CEIS | XLPE+PET+CINTAAL/PET+1602SEES | CD | 35 | 30.19 | No | 2020-07-23 | C_s1_d2 | 1.1 | 22.6 | 45.5 | 1290 | 49.2 | C | 30.2 | 0.08 | s1 | n | y | d2
TN_2020_2115 |  | 74921 20321141 | 729235X | AL ROZ1-K DCA TELEMANDO SEC 1KV 2X50 | 25.24 | 7 | Vilanova | XLPE+PET+CINTAAL/PET+1602SEES | CD | 74 | 18.66 | No | 2020-06-18 | C_s1_d2 | 1.2 | 24.7 | 46.4 | 1404 | 42.1 | C | 39.9 | 0.07 | s1 | n | y | d2
CEL-0534_20-1 |  | 74921 20321141 | 729235X | AL ROZ1-K DCA TELEMANDO SEC 1KV 2X50 | 26 | 7 | CEIS | XLPE+PET+CINTAAL/PET+1602SEES | CD | 37 | 27.95 | No | 2020-07-23 | D_s1_d2 | 1.1 | 26.8 | 61.8 | 1455 | 54 | D | 23.5 | 0.1 | s1 | n | y | d2
TN_2020_2116 |  | 76746 20302983 | 732619A | SEGURFOC CLASS - 331 (AS+) 1KV 3G2.5 NJ | 12.35 | 13 | Vilanova | TPR37 | CD | 75.3 | 18.49 | No | 2020-06-18 | B2_s1_d0 | 0.4 | 8.9 | 11.2 | 810 | 34.9 | B2 | 14.6 | 0.03 | s1 | n | n | d0
20060005 |  | 18323 | -- | SNCF RESEAU TFO .072B.L04 GENERAL CABLE 6 | 15.8 | 9 | Paron | TPR248+TPS246 | -- | 23.5 | 53.1 | No | 2020-06-19 | C_s2_d1 | 1.47 | 22.4 | 41.5 | 1035 | 59 | C | 95 | 0.34 | s2 | y | n | d1
TN_2020_2118 |  | 76115 | 423079U | RHZ1-RA+2OL (AS) 66KV 1X1000K AL+H135 | 76.1 | 3 | Vilanova | 61ABSEES+SKIN70%LE0563N+30%DMZ-E | CD | 73.4 | 19.37 | No | 2020-06-20 | B2_s1_d0 | 0.77 | 12.1 | 15.8 | 930 | 38.2 | B2 | 21.5 | 0.04 | s1 | n | n | d0
TN_2020_2119 |  | 76115 | 423074N | RHZ1-RA+2OL (AS) 66KV 1X1000K AL+H135 | 76.09 | 3 | Vilanova | 61AASEES+SKIN70%LE0563N+30%DMZ-E | CD | 73.7 | 21.08 | No | 2020-06-20 | B2_s1_d2 | 0.84 | 15 | 21.4 | 1092 | 37.4 | B2 | 21.8 | 0.07 | s1 | n | y | d2
TN_2020_2120 |  | 76779 20302968 | 732604J | SEGURFOC CLASS - 331 (AS+) 1KV 1X16 NJ | 11.78 | 13 | Vilanova | TPR37 | CD | 69.4 | 23.31 | No | 2020-06-20 | B2_s1_d1 | 0.4 | 5 | 12.8 | 477 | 63 | B2 | 7.7 | 0.02 | s1 | y | n | d1
TN_2020_2121 |  |  | 5096622 | TEST SAMPLE 102 PBT-FR+GEL FR (AFO420) | 13.93 | 11 | Vilanova | AFUMEXCPR+AFUMEXCPR | CD | 67.8 | 24.58 | No | 2020-06-20 | C_s1_d1 | 1.12 | 22.1 | 38.7 | 834 | 79.4 | C | 45.5 | 0.1 | s1 | y | n | d1
TN_2020_2122 |  | 76115 | 423079U | RHZ1-RA+2OL (AS) 66KV 1X1000K AL+H135 | 76.1 | 3 | Vilanova | 61ABSEES+SKIN70%LE0563N+30%DMZ-E | CD | 76.8 | 20.94 | No | 2020-06-22 | B2_s1_d0 | 0.75 | 13 | 16.4 | 1014 | 37.2 | B2 | 16 | 0.03 | s1 | n | n | d0
TN_2020_2123 |  |  | 5096623 | TEST SAMPLE 103 PBT-FR+GEL FR (AFO421) | 11.71 | 13 | Vilanova | AFUMEXCPR | CD | 76 | 23.27 | No | 2020-06-22 | D_s2_d0 | 2.14 | 32.9 | 53.6 | 771 | 131.3 | D | 117.2 | 0.22 | s2 | n | n | d0
TN_2020_2124 |  | 77436 60087613 | 5096604 | ACOMETIDA INTERIOR 1X2X0.5 | 3.74 | 105 | Vilanova | TPR32+SKINTPR-53 | CD | 66.2 | 25.91 | No | 2020-06-22 | E ou F_s2_d2 | 3.3 | 88.1 | 254.5 | 972 | 379.9 | E ou F | 73.4 | 0.23 | s2 | n | y | d2
TN_2020_2125 |  | 76115 | 423074N | RHZ1-RA+2OL (AS) 66KV 1X1000K AL+H135 | 76.09 | 3 | Vilanova | 61AASEES+SKIN70%LE0563N+30%DMZ-E | CD | 60.8 | 27.35 | No | 2020-06-22 | C_s1_d2 | 0.89 | 20.7 | 25.9 | 1230 | 45.9 | C | 11.3 | 0.04 | s1 | n | y | d2
TN_2020_2127 |  |  | 5096623 | TEST SAMPLE 103 PBT-FR+GEL FR (AFO421) | 11.71 | 13 | Vilanova | AFUMEXCPR | CD | 75.6 | 21.27 | No | 2020-06-23 | D_s2_d0 | 2.21 | 35.5 | 57.8 | 789 | 137.5 | D | 132 | 0.21 | s2 | n | n | d0
TN_2020_2128 |  | 76914 20336394 | 732875D | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 CU5 TPR-54 | 10.86 | 14 | Vilanova | TPR54 | CD | 76.8 | 22.89 | No | 2020-06-23 | E ou F_s2_d2 | 3.3 | 73.3 | 210.6 | 1494 | 176.4 | E ou F | 78.7 | 0.4 | s2 | n | y | d2
TN_2020_2129 |  | 76741 20335319 | 732878G | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 1420 LE200308 | 11.64 | 13 | Vilanova | TPR54 | CD | 72 | 25.32 | No | 2020-06-23 | D_s1_d1 | 2.51 | 40.5 | 68.7 | 1500 | 67.3 | D | 30 | 0.06 | s1 | y | n | d1
TN_2020_2130 |  | 76740 20335320 | 732874C | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 PP+1420 LE200308 | 11.51 | 13 | Vilanova | TPR54 | CD | 67.5 | 27.24 | No | 2020-06-23 | E ou F_s2_d2 | 3.3 | 86.1 | 217.2 | 1470 | 190.5 | E ou F | 88.9 | 0.47 | s2 | n | y | d2
TN_2020_2131 |  | 76912 20336392 | 732882L | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 CU5 TPR-35 | 10.96 | 14 | Vilanova | PTR35 | CD | 57.9 | 28.6 | No | 2020-06-23 | D_s2_d2 | 3.3 | 60.6 | 125.3 | 1500 | 104.5 | D | 73.1 | 0.15 | s2 | n | y | d2
20060006 |  | 18327 | CE6743 | K25 3G1.50-SH-NF F 55-625-255 | 11 | 14 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 44.7 | 25.5 | No | 2020-06-25 | B2_s1_d2 | 0.67 | 8 | 14.3 | 879 | 38 | B2 | 9 | 0.02 | s1 | y | y | d2
20060007 |  | 18313 | -- | CEC 2020 008 L1016 12 FO TPR 2049 | 6.1 | 25 | Paron | 1700SEES+AVECCALOXOL | -- | 44.8 | 26.1 | No | 2020-06-25 | C_s2_d2 | 1.6 | 13.3 | 37 | 627 | 124 | C | 69 | 0.24 | s2 | y | y | d2
20060008 |  | 18313 | -- | CEC 2020 008 L1016 12 FO TPR 2049 | 6.2 | 25 | Paron | 1700SEES+SANSCALOXOL | -- | 47.9 | 28.5 | No | 2020-06-25 | C_s2_d2 | 1.57 | 13.1 | 36.5 | 618 | 123 | C | 60 | 0.19 | s2 | y | y | d2
TN_2020_2126 |  | 77495 60089068 | 5096605 | ACOMETIDA INTERIOR 1X2X0.5 | 3.74 | 105 | Vilanova | MEGOLONS643WV | CD | 46.3 | 28.8 | No | 2020-06-26 | E ou F_s2_d1 | 3.3 | 86.9 | 214.6 | 1020 | 319.4 | E ou F | 67.9 | 0.15 | s2 | y | n | d1
TN_2020_2134 |  | 83526856 20305843 | 664279T | XGB 4X70 | 33.88 | 5 | Vilanova | AIS:PRS-03RELL:TPR-49CUB:TPR37 | CD | 48.7 | 26.99 | No | 2020-06-26 | B2_s1_d0 | 0.41 | 2.8 | 4 | 570 | 9 | B2 | 8.3 | 0.02 | s1 | n | n | d0
TN_2020_2135 |  | 83569147 20307574 | 714190U | EXAVB 4X16 | 22.67 | 7 | Vilanova | AIS:PRS-03RELL:PVC-08+07CUB:PVC-13 | CD | 77.2 | 24.89 | No | 2020-06-29 | C_s2_d1 | 0.83 | 14.4 | 18.7 | 1500 | 159.6 | C | 217.2 | 0.31 | s2 | y | n | d1
TN_2020_2136 |  | 83631610 20304184 | 727243G | XVB 4X95 | 38.03 | 5 | Vilanova | AIS:PRS-03RELL:PVC-14CUB:PVC-13 | CD | 76.7 | 25.99 | No | 2020-06-29 | C_s2_d1 | 0.74 | 23.1 | 38.7 | 1500 | 75.6 | C | 335.6 | 0.39 | s2 | y | n | d1
TN_2020_2137 |  | 83638404 20193641 | 702029A | AFUMEX CLASS 1KV RZ1-K (AS) 1X95MM2 | 18.06 | 8 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 54.3 | 22.17 | No | 2020-06-26 | B2_s1_d1 | 0.57 | 6.2 | 8.5 | 1371 | 17.2 | B2 | 3.4 | 0.01 | s1 | y | n | d1
TN_2020_2138 |  | 20226890 | 662955D | HEPRZ1 (AS) 20KV 1X400/16 12/20 KV | 46.74 | 4 | Vilanova | HEPR+1420FEES+6000SEES | CD | 52.3 | 24.67 | No | 2020-06-26 | C_s1_d2 | 0.81 | 15.8 | 24.5 | 1359 | 29.3 | C | 8.6 | 0.02 | s1 | n | y | d2
20060009 |  | 18327 | CE6743 | K25 3G1.50-SH-NF F 55-625-255 | 11 | 14 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 57.1 | 22.5 | No | 2020-06-29 | B2_s1_d1 | 0.67 | 7.5 | 12.6 | 819 | 33 | B2 | 4 | 0.01 | s1 | y | n | d1
TN_2020_2139 |  |  | 5096597 | TEST SAMPLE #90 PBT-FR + GEL FR (AFO415-1) | 16.05 | 9 | Vilanova | AFUMEXCPR+AFUMEXCPR | CD | 73.4 | 25.31 | No | 2020-06-30 | C_s1_d1 | 1.07 | 21 | 31.2 | 1017 | 54.1 | C | 35.3 | 0.12 | s1 | y | n | d1
TN_2020_2140 |  |  | 5096613 | TEST SAMPLE #96 PBT-FR+GEL FR (AFO414-1) | 12.72 | 12 | Vilanova | AFUMEXCPR+AFUMEXCPR | CD | 72.1 | 26.94 | No | 2020-06-30 | C_s1_d0 | 0.75 | 20 | 24.4 | 780 | 71.5 | C | 15.6 | 0.03 | s1 | n | n | d0
TN_2020_2141 |  | 75191 20327590 | 680336W | AL AFUMEX CLASS 1KV RZ1 (AS) 1X16 MM² | 9.93 | 15 | Vilanova | XLPE+TPR55 | CD | 69 | 27.3 | No | 2020-06-30 | B2_s1_d0 | 0.41 | 6.2 | 13.9 | 693 | 40.7 | B2 | 5.5 | 0.01 | s1 | n | n | d0
TN_2020_2142 |  | 75192 20327589 | 687784S | AL AFUMEX CLASS 1KV RZ1 (AS) 1X300 MM² | 28.4 | 6 | Vilanova | XLPE+TPR55 | OD | 50 | 29.43 | No | 2020-07-01 | B2_s1_d1 | 0.42 | 4.3 | 9.3 | 1500 | 17.3 | B2 | 10.4 | 0.01 | s1 | y | n | d1
TN_2020_2143 |  |  | 5096593 | TEST SAMPLE #94 PBT-FR + GEL FR (AFO417-2) | 14.59 | 10 | Vilanova | AFUMEXCPR | OD | 66.4 | 28.1 | No | 2020-07-01 | C_s2_d0 | 1.25 | 22.5 | 38.8 | 903 | 76.8 | C | 85.8 | 0.14 | s2 | n | n | d0
TN_2020_2144 |  |  | 5096612 | TEST SAMPLE #99 PBT-FR+GEL FR (AFO416-1) | 10.56 | 14 | Vilanova | AFUMEXCPR | OD | 55.5 | 29.69 | No | 2020-07-01 | B2_s1_d0 | 1.11 | 14.6 | 29.5 | 723 | 90.3 | B2 | 14.6 | 0.05 | s1 | n | n | d0
TN_2020_2145 |  |  | 646164C | RHZ1FA3Z1-2OL(AS) RR 30KV 1X400/16 AL AFUMEX | 56.41 | 4 | Vilanova | TPR28+TPR37 | OD | 51.7 | 30.17 | No | 2020-07-01 | B2_s1_d0 | 0.6 | 6 | 9 | 798 | 18.7 | B2 | 4.9 | 0.01 | s1 | n | n | d0
TN_2020_2149 |  | 75456 20282517 | 716998W | RHOZ1MZ1 500V 6X3X0.5 2RH | 21.17 | 7 | Vilanova | XLPE+GFR380+SWSA+GFR380 | CD | 74.6 | 27.58 | No | 2020-07-02 | B2_s1_d1 | 0.7 | 8.3 | 16 | 1263 | 20 | B2 | 18.7 | 0.04 | s1 | y | n | d1
TN_2020_2150 |  | 75457 20315022 | 717019U | RHOZ1MZ1 500V 2X2X0.5 2RH | 14.52 | 10 | Vilanova | XLPE+GFR380+SWSA+GFR380 | CD | 71.7 | 28.98 | No | 2020-07-02 | B2_s1_d0 | 0.29 | 9 | 10 | 1497 | 36.2 | B2 | 5.1 | 0.01 | s1 | n | n | d0
TN_2020_2051 |  | 75458 20314925 | 710912F | RHOZ1MZ1 500V 24X2X0.5 2RH | 33.55 | 5 | Vilanova | XLPE+GFR380+SWSA+GFR380 | CD | 67 | 29.83 | No | 2020-07-02 | B2_s1_d0 | 0.61 | 3.7 | 6.4 | 1500 | 17.9 | B2 | 3.2 | 0.01 | s1 | n | n | d0
TN_2020_2152 |  | 75460 20270394 | 719890P | ROZ1MZ1 500V 1X2X2.5 2RH | 14.19 | 11 | Vilanova | XLPE+GFR380+SWSA+GFR380 | CD | 63 | 30.96 | No | 2020-07-02 | B2_s1_d1 | 0.54 | 9.3 | 16.2 | 933 | 26.9 | B2 | 13.7 | 0.04 | s1 | y | n | d1
TN_2020_2153 |  |  | 5096595 | TEST SAMPLE #93 PBT-FR + GEL FR (AFO417-1) | 14.6 | 10 | Vilanova | LSOH | OD | 54 | 23.36 | No | 2020-07-03 | B2_s1_d0 | 0.81 | 8.5 | 20.8 | 750 | 49.5 | B2 | 39.9 | 0.12 | s1 | n | n | d0
20070001 |  | 18345 | -- | FG17 ES409A 8X1MM² | 16.4 | 9 | Paron | ID26AB+CFR+SV36AA+SV61AA | -- | 50.4 | 22.4 | No | 2020-07-03 | C_s1_d2 | 1 | 16.9 | 25.8 | 1209 | 32 | C | 34 | 0.06 | s1 | y | y | d2
20070002 |  | 18345 | -- | FG17 ES409A 16X1MM² | 20.8 | 7 | Paron | ID26AB+CFR+SV36AA+SV61AA | -- | 47.5 | 22.4 | No | 2020-07-03 | B2_s1_d2 | 0.57 | 8.1 | 12.1 | 1398 | 24 | B2 | 17 | 0.03 | s1 | y | y | d2
|  |  |  | FG17 ES409A 16X1MM² | 19.22 | 7 | LS Fire | ID26AB+CFR+SV36AA+SV61AA | -- | 50 | 28 | No | 2020-06-14 | C_s1_d2 | 0.92 | 16 | 30 | -- | 30 | C | 23 | 0.05 | s1 | y | y | d2
|  |  |  | FG17 ES409A 8X1MM² | 16.4 | 9 | LS Fire | ID26AB+CFR+SV36AA+SV61AA | -- | 50 | 22 | No | 2020-07-03 | E ou F_s1_d2 | 16.9 | 25.8 | 1209 | - | 31.5 | E ou F | 33.5 | 0.06 | s1 | y | y | d2
TN_2020_2155 |  | 83638404 20193641 | 702029A | AFUMEX CLASS 1KV RZ1-K (AS) 1X95MM2 | 18.06 | 8 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 59.7 | 23.58 | No | 2020-07-07 | B2_s1_d1 | 0.7 | 8 | 12.9 | 1332 | 17.7 | B2 | 3.4 | 0.01 | s1 | y | n | d1
TN_2020_2156 |  | 83676248 20193638 | 729248L | AFUMEX CLASS 1KV RZ1-K (AS) 1X35MM2 | 13.66 | 11 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 54 | 23.9 | No | 2020-07-07 | C_s1_d2 | 1.79 | 25.9 | 48.5 | 1425 | 45.6 | C | 8.4 | 0.04 | s1 | n | y | d2
TN_2020_2157 |  | 83676248 20193638 | 729248L | AFUMEX CLASS 1KV RZ1-K (AS) 1X35MM2 | 13.66 | 11 | Vilanova | SXLPE+1420FEES+1602SEES | CD | 47.3 | 26.54 | No | 2020-07-07 | C_s1_d2 | 1.58 | 19.8 | 45.5 | 1494 | 38.1 | C | 11.9 | 0.03 | s1 | n | y | d2
TN_2020_2158 |  | 83569223 20193983 | 5096602 | AFUMEX CLASS 750V H07Z1-K (AS) 1X2.5 | 3.58 | 105 | Vilanova | 1602SEES | CD | 47.6 | 29.56 | No | 2020-07-07 | D_s2_d0 | 3.1 | 26.9 | 41.8 | 738 | 104.9 | D | 57.6 | 0.11 | s2 | n | n | d0
CEL_0454_20-1 |  | 83451495 20194862 | 5096559 | ES05Z1-K 500V 1X1MM² | 2.5 | 270 | CEIS | 1602SEES | CD | 42 | 29.06 | No | 2020-07-01 | C_s1_d0 | 1.4 | 17.4 | 40.7 | 666 | 121.3 | C | 21.4 | 0.07 | s1 | n | n | d0
20070003 |  | 18327 | CE6743 | K25 3G1.50-SH-NF F 55-625-255 | 11 | 14 | Paron | SXLPE+0400FEIT+5300SEIT | -- | 46 | 21 | No | 2020-07-08 | B2_s1_d0 | 1 | 13.2 | 19.6 | 1071 | 51 | B2 | 41 | 0.14 | s1 | n | n | d0
20070004 |  | 18349 | CE6704A | VS8 K20 - 75 OHMS - PESS1151 - PRYSMIAN 255 | 10.3 | 15 | Paron | AXELERONCC3485NTCPD+5300SEIT | -- | 46.6 | 21.1 | No | 2020-07-08 | D_s1_d2 | 1.87 | 21.3 | 69.7 | 687 | 183 | D | 21 | 0.04 | s1 | y | y | d2
20070005 |  | 18349 | CE6704C | VS8 K20 - 75 OHMS - PESS1151 - PRYSMIAN 255 | 10.6 | 14 | Paron | AXELERONCC3485NTCPD+1602SEES | -- | 40.2 | 22.9 | No | 2020-07-08 | D_s1_d2 | 3.3 | 48.4 | 85.7 | 936 | 196 | D | 49 | 0.09 | s1 | y | y | d2
TN_2020_2161 |  | 77056 | OF179 | RHZ1-RA+2OL (AS) 76/132 KV 1X1000 | 94.53 | 2 | Vilanova | 61AA+SKIN30%DMZ-E+70%LE0563 | CD | 55.9 | 29.95 | No | 2020-07-08 | B2_s1_d2 | 0.94 | 10.7 | 13.7 | 1104 | 29.4 | B2 | 11.5 | 0.04 | s1 | n | y | d2
TN_2020_2162 |  | 83701548 20329100 | OF171 | PRYSMIAN CNE TSLI (F) 145KV 1X400AI2 H7 | 77.73 | 3 | Vilanova | 61AA+SKIN30%DMZ-E+70%LE0563 | CD | 72.9 | 25.81 | No | 2020-07-09 | C_s1_d0 | 0.86 | 15.5 | 18.9 | 849 | 42.2 | C | 11.1 | 0.03 | s1 | n | n | d0
TN_2020_2163 |  | 77239 20332582 | 733447A | RHZ1-OL(AS) 10KV 1X240 | 43.13 | 5 | Vilanova | 1420+6000 | CD | 73.6 | 26.82 | No | 2020-07-09 | D_s1_d2 | 1.6 | 38.9 | 69.8 | 1497 | 61.4 | D | 3.5 | 0.02 | s1 | n | y | d2
TN_2020_2160 |  | 83397267 20193661 | 724042C | AFUMEX CLASS 1KV RZ1-K (AS) 4X10 | 17.3 | 9 | Vilanova | 1420+1602 | CD | 63.4 | 29.02 | No | 2020-07-09 | C_s1_d2 | 1.08 | 17.8 | 35.1 | 1353 | 34.2 | C | 13 | 0.03 | s1 | n | y | d2
TN_2020_2164 |  | 78049 20341223 | 738485B | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.63 | 13 | Vilanova | 16HASEESBIGBAG | CD | 55.2 | 31.42 | No | 2020-07-09 | B2_s1_d0 | 0.36 | 3.8 | 7.8 | 786 | 16.4 | B2 | 0.7 | 0.01 | s1 | n | n | d0
TN_2020_2165 |  | 77240 20332583 | 720172W | RHZ1-OL(AS) 30KV 1X240 | 51.84 | 4 | Vilanova | 1420+6000 | CD | 51.6 | 21.23 | No | 2020-07-09 | C_s1_d2 | 1.26 | 20.8 | 34.9 | 1500 | 34.1 | C | 11.9 | 0.02 | s1 | n | y | d2
TN_2020_2167 |  | 78047 20341222 | 738492J | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.52 | 13 | Vilanova | 16HASEESBIGBAG | CD | 66.4 | 24.65 | No | 2020-07-10 | B2_s1_d1 | 0.42 | 5.9 | 11.9 | 822 | 24 | B2 | 18.5 | 0.03 | s1 | y | n | d1
TN_2020_2168 |  | 78050 20341224 | 738490G | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 10.97 | 14 | Vilanova | 16HASEESBIGBAG | CD | 67.3 | 25.89 | No | 2020-07-10 | C_s1_d2 | 1.51 | 18.8 | 23.5 | 1455 | 51 | C | 26.2 | 0.05 | s1 | n | y | d2
TN_2020_2169 |  | 78051 20341225 | 738489F | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.51 | 14 | Vilanova | TPR-55 | CD | 54.5 | 27.09 | No | 2020-07-10 | B2_s1_d0 | 0.49 | 4.9 | 11.2 | 861 | 22.7 | B2 | 3.6 | 0.01 | s1 | n | n | d0
TN_2020_2170 |  | 78048 20341226 | 738442E | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.51 | 14 | Vilanova | 16HASEESBIGBAG | CD | 51.2 | 29.37 | No | 2020-07-10 | B2_s1_d1 | 0.68 | 6.7 | 14.5 | 798 | 30.3 | B2 | 6.5 | 0.02 | s1 | y | n | d1
TN_2020_2171 |  | 76885 20329657 | 249318Y | MRHOZ1MZ1-K 500V 1X2X6 MM2 RH | 16.14 | 9 | Vilanova | XLPE+1602+GFR380 | CD | 53.3 | 30.78 | No | 2020-07-10 | C_s1_d2 | 0.89 | 21.1 | 36.9 | 1137 | 44.2 | C | 28.3 | 0.08 | s1 | n | y | d2
TN_2020_2175 |  | 77056 | OF179 | RHZ1-RA+2OL (AS) 76/132 KV 1X1000 | 94.53 | 2 | Vilanova | 61AA+SKIN30%DMZ-E+70%LE0563 | CD | 65.4 | 23.75 | No | 2020-07-14 | B2_s1_d0 | 0.45 | 8.3 | 11.2 | 939 | 25.8 | B2 | 7.4 | 0.01 | s1 | n | n | d0
TN_2020_2176 |  | 77056 | OF179 | RHZ1-RA+2OL (AS) 76/132 KV 1X1000 | 94.53 | 2 | Vilanova | 61AA+SKIN30%DMZ-E+70%LE0563 | CD | 67.3 | 25.46 | No | 2020-07-14 | B2_s1_d0 | 0.56 | 8.3 | 10.7 | 858 | 27 | B2 | 1.1 | 0 | s1 | n | n | d0
TN_2020_2183 |  | 78436 20343747 | 708809V | EXZHELLENT COMPACT RZ1-K (AS) 1KV 2X16 | 15.65 | 9 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 69.6 | 22.94 | No | 2020-07-17 | B2_s1_d0 | 0.48 | 8.2 | 12.8 | 1497 | 22.1 | B2 | 2.7 | 0.01 | s1 | n | n | d0
TN_2020_2184 |  | 78437 20343748 | 735484P | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 10.82 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 70.8 | 23.98 | No | 2020-07-17 | C_s1_d2 | 1.79 | 25.2 | 30.6 | 1458 | 60.3 | C | 37.5 | 0.1 | s1 | n | y | d2
TN_2020_2185 |  | 78440 20343785 | 748697B | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G1.5 | 9.34 | 17 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 69.1 | 25.33 | No | 2020-07-17 | B2_s1_d0 | 1.31 | 14.1 | 19.3 | 864 | 51.5 | B2 | 37.7 | 0.07 | s1 | n | n | d0
TN_2020_2186 |  | 78051 20341225 | 12T2039 | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 11.24 | 14 | Vilanova | TPR+PAPEL+1420+TPR-55VDPRY+1%CALOXOL | CD | 68.9 | 26.56 | No | 2020-07-17 | C_s1_d1 | 1.79 | 24.8 | 31.8 | 1053 | 55.3 | C | 21.6 | 0.05 | s1 | y | n | d1
TN_2020_2187 |  | 78048 20341226 ORIGINAL | 681393V | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 11.21 | 14 | Vilanova | PAPER+14200.5MM+16HB1.4MM | CD | 66.6 | 27.95 | No | 2020-07-17 | C_s1_d2 | 1.42 | 18.7 | 30.4 | 750 | 67.6 | C | 15.5 | 0.03 | s1 | n | y | d2
TN_2020_2188 |  | 78441 20343786 | 748691V | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 10.36 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 24.3 | 22.96 | No | 2020-07-19 | C_s1_d1 | 1.74 | 22.9 | 28.4 | 963 | 53.1 | C | 37.9 | 0.09 | s1 | y | n | d1
TN_2020_2189 |  | 78048 20341226 (V3) | 727680G | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 10.32 | 15 | Vilanova | PAPER+16HB1.4MM | CD | 71.1 | 25.78 | No | 2020-07-19 | D_s2_d2 | 3.3 | 67.4 | 117.7 | 1326 | 138.4 | D | 138.3 | 0.28 | s2 | n | y | d2
TN_2020_2190 |  | 78048 20341226 (V2) | 727683K | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 10.87 | 14 | Vilanova | PAPER+14200.3MM+16HB1.4MM | CD | 65.4 | 27.27 | No | 2020-07-19 | C_s1_d1 | 1.46 | 19.8 | 29.3 | 723 | 70 | C | 15.7 | 0.02 | s1 | y | n | d1
TN_2020_2177 |  |  | 725076B | FIRS LT-T3M1F2M2 48FO (11249) | 16.31 | 9 | Vilanova |  | CD | 64.6 | 29.46 | No | 2020-07-19 | B2_s1_d0 | 0.73 | 11.2 | 20.5 | 1017 | 34.5 | B2 | 18.7 | 0.03 | s1 | n | n | d0
TN_2020_2191 |  | 77239 20332582 | 733447A | RHZ1-OL(AS) 10KV 1X240 | 43.13 | 5 | Vilanova | 1420+6000 | CD | 63.2 | 30.4 | No | 2020-07-19 | D_s1_d2 | 1.89 | 38.6 | 65.4 | 1380 | 63.5 | D | 12.8 | 0.03 | s1 | n | y | d2
TN_2020_2192 |  | 784439 20343787 | 708825M | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G4 | 11.31 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 74.2 | 24 | No | 2020-07-20 | C_s1_d0 | 1.08 | 16.3 | 21.5 | 1032 | 42.6 | C | 35.2 | 0.08 | s1 | n | n | d0
TN_2020_2193 |  | 78438 20343749 | 708816C | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G16 | 20.34 | 8 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 74.1 | 25.39 | No | 2020-07-20 | C_s1_d1 | 0.68 | 12.8 | 31 | 1482 | 26.4 | C | 5.6 | 0.03 | s1 | y | n | d1
TN_2020_2194 |  | 83701548 20329100 | OF171 | PRYSMIAN CNE TSLI (F) 145KV 1X400AI2 H7 | 77.73 | 3 | Vilanova | 61AA+SKIN30%DMZ-E+70%LE0563 | CD | 70.1 | 29.26 | No | 2020-07-20 | C_s1_d2 | 0.97 | 18.6 | 24.3 | 996 | 45.2 | C | 14.5 | 0.04 | s1 | n | y | d2
TN_2020_2195 |  | 83612196 20302884 | 746581B | EXZHELLENT COMPACT RZ1-K (AS) 1KV 1X50 | 14.97 | 10 | Vilanova | PRS-03+TPR-55 | CD | 63.5 | 31.38 | No | 2020-07-20 | B2_s1_d1 | 0.77 | 9.7 | 14.2 | 1224 | 21.1 | B2 | 4.9 | 0.01 | s1 | y | n | d1
20070006 |  | 18361 | -- | 1000-1G70-SH NF F 55-625- PRYSMIAN 255 | 18.4 | 8 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 42.2 | 23.3 | No | 2020-07-21 | B2_s1_d2 | 0.67 | 6.5 | 11.5 | 1272 | 18 | B2 | 6 | 0.02 | s1 | y | y | d2
TN_2020_2196 |  | 74293 20321193 | 729710N | AL ROZ1-K B2CA TLM 1KV 2X50 | 27.55 | 6 | Vilanova | 1420+TPR55 | CD | 66 | 23.18 | No | 2020-07-21 | B2_s1_d1 | 0.53 | 7.1 | 9.8 | 1083 | 14.7 | B2 | 4.5 | 0.01 | s1 | y | n | d1
TN_2020_2197 |  | 78048 20341226 ORIGINAL | 681393V | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 11.21 | 14 | Vilanova | PAPER+14200.5MM+16HB1.4MM | CD | 62.1 | 25.73 | No | 2020-07-21 | B2_s1_d1 | 0.57 | 9.5 | 17.9 | 837 | 34.7 | B2 | 6.6 | 0.02 | s1 | y | n | d1
TN_2020_2198 |  | 74805 20321192 | 729688P | AL ROZ1-K B2CA TLM 1KV 2X25 | 22.35 | 7 | Vilanova | 1420+TPR55 | CD | 59.8 | 26.84 | No | 2020-07-21 | B2_s1_d0 | 0.69 | 5.9 | 8 | 1086 | 15.2 | B2 | 12.4 | 0.02 | s1 | n | n | d0
TN_2020_2199 |  | 78437 20343748 | 735484P | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 10.82 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 65.5 | 28.98 | No | 2020-07-21 | C_s1_d1 | 1.65 | 18.1 | 23 | 1083 | 55.1 | C | 33.6 | 0.08 | s1 | y | n | d1
TN_2020_2182 |  | 76393 | 727937L | EATST 25X4X0.90 | 39.55 | 5 | Vilanova | TPR28+TPR55 | CD | 64.1 | 30.53 | No | 2020-07-21 | B2_s1_d0 | 0.49 | 14.3 | 21.1 | 1500 | 32.2 | B2 | 7.2 | 0.01 | s1 | n | n | d0
TN_2020_2200 |  | 78048 20341226 (V2) | 727683K | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 10.87 | 14 | Vilanova | PAPER+14200.3MM+16HB1.4MM | CD | 62.2 | 22.91 | No | 2020-07-22 | C_s1_d2 | 1.34 | 16.5 | 25.7 | 837 | 50.9 | C | 15.5 | 0.03 | s1 | n | y | d2
TN_2020_2201 |  | 78048 20341226 ORIGINAL | 681393V | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 11.21 | 14 | Vilanova | PAPER+14200.5MM+16HB1.4MM | CD | 67 | 24.66 | No | 2020-07-22 | C_s1_d2 | 1.3 | 17.9 | 32.5 | 804 | 64.5 | C | 14.7 | 0.03 | s1 | n | y | d2
TN_2020_2202 |  | 78437 20343748 | 735484P | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 10.82 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 57.4 | 27.24 | No | 2020-07-22 | D_s2_d1 | 2.69 | 40 | 71.1 | 1500 | 66.2 | D | 52.8 | 0.13 | s2 | y | n | d1
TN_2020_2203 |  | 78048 20341226 (V2) | 727683K | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 10.87 | 14 | Vilanova | PAPER+14200.3MM+16HB1.4MM | CD | 48.1 | 30.04 | No | 2020-07-22 | C_s1_d2 | 1.7 | 23 | 40.4 | 756 | 89.8 | C | 23.3 | 0.04 | s1 | n | y | d2
TN_2020_2204 |  | 75866 | 739835U | CCTSST FR 1X4X1.4 | 15.61 | 9 | Vilanova | TPR55+DOOBLESTEELTAPE+1420SEES+TPR55 | CD | 44.4 | 30.78 | No | 2020-07-22 | B2_s1_d2 | 0.66 | 11.5 | 17.8 | 1062 | 30.8 | B2 | 21.7 | 0.05 | s1 | n | y | d2
TN_2020_2215 |  | 74926 20321197 | 729691T | AL ROZ1-K B2CA TLM 1KV 2X50 | 28.41 | 6 | Vilanova | 1420FEES+LANTOR+TPR55 | CD | 55.4 | 24.96 | No | 2020-07-23 | B2_s1_d0 | 0.38 | 4.2 | 5.8 | 894 | 12.2 | B2 | 0.2 | 0 | s1 | n | n | d0
TN_2020_2216 |  | 74809 20321196 | 717004C | AL ROZ1-K B2CA TLM 1KV 2X25 | 22.83 | 7 | Vilanova | 1420FEES+LANTOR+TPR55 | CD | 52.2 | 24.62 | No | 2020-07-23 | B2_s1_d0 | 0.43 | 5 | 7.7 | 693 | 23.4 | B2 | 1.2 | 0 | s1 | n | n | d0
TN_2020_2217 |  | 74803 20321190 | 735894K | AL ROZ1-K 2X25 MM2 B2CA S1A D1 A1 | 22.1 | 7 | Vilanova | XLPE+AL/PE+1420+1602ONESHOT | CD | 47.4 | 28.17 | No | 2020-07-23 | B2_s1_d0 | 0.49 | 5.3 | 7.4 | 750 | 16.7 | B2 | 4.4 | 0.01 | s1 | n | n | d0
TN_2020_2218 |  | 74807 20321194 | 735886B | AL ROZ1-K 2X25MM2 B2CA S1A D1 A1 | 22.86 | 7 | Vilanova | XLPE+AL/PE+1420+LANTOR+1602 | CD | 47.5 | 30.84 | No | 2020-07-23 | B2_s1_d0 | 0.49 | 5.9 | 7.8 | 873 | 14.1 | B2 | 12.2 | 0.02 | s1 | n | n | d0
TN_2020_2219 |  | 75966 20328834 | 709727T | H07Z1-K 1X240 TYPE2 | 24.5 | 7 | Vilanova | TPR-27 | CD | 54.1 | 31.39 | No | 2020-07-23 | B2_s1_d1 | 0.65 | 5.5 | 16.9 | 621 | 54.8 | B2 | 7.1 | 0.01 | s1 | y | n | d1
TN_2020_2213 |  | 8379240 20302792 | 5096603 | EXZHELLENT CLASS 05Z1-K 1X0.75 C200 MR | 2.26 | 270 | Vilanova | TPR-52/TPR-53 | CD | 65.7 | 25.83 | No | 2020-07-24 | C_s2_d1 | 1.87 | 18.1 | 32.3 | 732 | 83.7 | C | 69.3 | 0.16 | s2 | y | n | d1
TN_2020_2220 |  | 74924 20321195 | 729697Z | AL ROZ1-K 2X50MM2 B2CA S1A D1 A1 | 28.19 | 6 | Vilanova | XLPE+AL/PE+1420+LANTOR+1602 | CD | 60.2 | 26.94 | No | 2020-07-24 | B2_s1_d0 | 0.48 | 4.8 | 6 | 1482 | 13.3 | B2 | 3.2 | 0 | s1 | n | n | d0
TN_2020_2221 |  | 74922 20321191 | 729717W | AL ROZ1-K 2X50MM2 B2CA S1A D1 A1 | 27.9 | 6 | Vilanova | XLPE+AL/PE+1420+1602ONESHOT | CD | 57.2 | 28.3 | No | 2020-07-24 | B2_s1_d0 | 0.48 | 4.5 | 5.9 | 1227 | 11.5 | B2 | 2.3 | 0.01 | s1 | n | n | d0
TN_2020_2205 |  | 78437 20343748 | 735484P | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 10.82 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 65.5 | 28.98 | No | 2020-07-28 | C_s1_d1 | 1.7 | 18.1 | 23 | 1083 | 55.1 | C | 33.6 | 0.08 | s1 | y | n | d1
TN_2020_2206 |  | 78436 20343747 | 708809V | EXZHELLENT COMPACT RZ1-K (AS) 1KV 2X16 | 15.65 | 9 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 53.1 | 27.99 | No | 2020-07-23 | B2_s1_d1 | 0.57 | 8 | 12.4 | 1341 | 18.6 | B2 | 5.5 | 0.01 | s1 | y | n | d1
TN_2020_2208 |  | 76474 | 687920P | CCTSST FR 0.3 48X1.4 | 28.74 | 6 | Vilanova | RELLENOAFUMEXCPR+TPR55 | CD | 48.8 | 30.45 | No | 2020-07-28 | B2_s1_d1 | 0.42 | 2.4 | 6.5 | 579 | 23.3 | B2 | 0.4 | 0 | s1 | y | n | d1
TN_2020_2209 |  | 76475 | 705952P | CCTSST FR 0.3 10X4X1.4 | 36.79 | 5 | Vilanova | RELLENOAFUMEXCPR+TPR55 | CD | 50.6 | 31.04 | No | 2020-07-28 | B2_s1_d1 | 0.45 | 4.3 | 6.8 | 849 | 21.9 | B2 | 8.5 | 0.02 | s1 | y | n | d1
TN_2020_2210 |  | 76390 | 544582M | CCTSST (H) FR 0.3 4X1.4 | 28.33 | 6 | Vilanova | RELLENOAFUMEXCPR+TPR55 | CD | 58.2 | 31.37 | No | 2020-07-28 | B2_s1_d0 | 0.52 | 3.4 | 6.7 | 600 | 22.2 | B2 | 18.1 | 0.03 | s1 | n | n | d0
TN_2020_2211 |  | 76391 | 687922S | CCTSST (X) FR 0.3 5X4X1.4 | 27.57 | 6 | Vilanova | RELLENOAFUMEXCPR+TPR55 | OD | 69.4 | 25.94 | No | 2020-07-29 | B2_s1_d1 | 0.47 | 3.6 | 6.8 | 612 | 23 | B2 | 9.4 | 0.01 | s1 | y | n | d1
TN_2020_2212 |  | 77056 | OF179 | RHZ1-RA+2OL (AS) 76/132 KV 1X1000 | 94.53 | 2 | Vilanova | 61AA+SKIN30%DMZ-E+70%LE0563 | OD | 68 | 27.74 | No | 2020-07-29 | B2_s1_d0 | 0.71 | 7.4 | 10.2 | 834 | 23.4 | B2 | 0.3 | 0 | s1 | n | n | d0
TN_2020_2214 |  | 76885 20329657 | 249318Y | MRHOZ1MZ1-K 500V 1X2X6 MM2 RH | 16.14 | 9 | Vilanova | XLPE+1602+GFR380 | OD | 59.3 | 29.79 | No | 2020-07-29 | B2_s1_d2 | 0.76 | 11.7 | 21.4 | 1224 | 30.2 | B2 | 16.3 | 0.04 | s1 | y | y | d2
TN_2020_2222 |  | 77468 20318519 | 720087D | DHZ1MZ1(AS) RH 10 KV 3X95 AFUMEX | 62.79 | 3 | Vilanova | 1420+1602+GSWARMOUR+GFR380 | CD | 63.8 | 26.35 | No | 2020-07-30 | B2_s1_d0 | 0.45 | 3.4 | 5.2 | 549 | 20.8 | B2 | 7.3 | 0.01 | s1 | n | n | d0
TN_2020_2223 |  | 76442 20319578 | 727841G | DHZ1MAZ1-OL(AS) RH 10 KV 1X120 AFUMEX | 41.47 | 5 | Vilanova | 1420+1602+GSWARMOUR+GFR380 | CD | 64.3 | 27.5 | No | 2020-07-30 | B2_s1_d1 | 0.58 | 6.1 | 6.9 | 1341 | 25.3 | B2 | 10.1 | 0.01 | s1 | y | n | d1
TN_2020_2224 |  | 78813 (3) 20345303 | 767098C | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.12 | 15 | Vilanova | PP+PAPEL+0.31420+16HBTHICKNESSMEASURED:0.4+1.6 | CD | 67.1 | 28.23 | No | 2020-08-19 | B2_s1_d2 | 0.53 | 8.2 | 20.4 | 738 | 48 | B2 | 9.6 | 0.03 | s1 | y | y | d2
TN_2020_2225 |  | 78813 (1) 20345303 | 767110R | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.01 | 15 | Vilanova | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.3+1.7 | CD | 70.3 | 30.33 | No | 2020-08-19 | D_s1_d2 | 2.72 | 38.3 | 51.7 | 1230 | 81.8 | D | 43.1 | 0.07 | s1 | y | y | d2
TN_2020_2226 |  | 78811 (2) 20345304 | 767088S | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.98 | 13 | Vilanova | PP+PAPEL+0.51420+16HATHICKNESSMEASURED:0.4+1.6 | CD | 65 | 31.81 | No | 2020-08-19 | D_s1_d2 | 2.48 | 38.9 | 60.3 | 1122 | 78.1 | D | 32 | 0.06 | s1 | y | y | d2
TN_2020_2227 |  | 78811 (1) 20345304 | 767118Z | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.61 | 13 | Vilanova | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.4+1.6 | CD | 75.7 | 27.16 | No | 2020-08-20 | C_s1_d2 | 1.37 | 18.5 | 26.6 | 843 | 49.2 | C | 13.6 | 0.003 | s1 | n | y | d2
TN_2020_2228 |  | 78815 20345305 | 767097B | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.41 | 17 | Vilanova | PP+PAPEL+16HBTHICKNESSMEASURED:1.6 | CD | 76.1 | 29.08 | No | 2020-08-20 | D_s2_d2 | 3.3 | 68.4 | 129.3 | 1344 | 123.9 | D | 117.6 | 0.27 | s2 | n | y | d2
TN_2020_2229 |  | 78813(2) 20345303 | 767119A | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.72 | 14 | Vilanova | PP+PAPEL+0.51420+16HATHICKNESSMEASURED:0.5+1.8 | CD | 72.1 | 31.29 | No | 2020-08-20 | C_s1_d2 | 1.49 | 20.9 | 30.7 | 822 | 60.9 | C | 18.1 | 0.04 | s1 | n | y | d2
TN_2020_2230 |  | 78812 20345306 | 767104J | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.12 | 14 | Vilanova | PP+PAPEL+16HBTHICKNESSMEASURED:1.6 | CD | 64.5 | 32.1 | No | 2020-08-20 | E ou F_s2_d2 | 3.2 | 88.4 | 168.6 | 1206 | 220.6 | E ou F | 159.8 | 0.34 | s2 | n | y | d2
TN_2020_2231 |  | 78811(3) 20345304 | 767094Y | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.91 | 13 | Vilanova | PP+PAPEL+0.31420+16HBTHICKNESSMEASURED:0.4+1.4 | CD | 64 | 26.96 | No | 2020-08-21 | C_s1_d2 | 1.37 | 16.3 | 24.6 | 753 | 54.4 | C | 20.7 | 0.03 | s1 | n | y | d2
TN_2020_2232 |  | 73193 20310305 | 736175R | RHZ1-2OL (AS) 12/20 KV 1X240 AL+H16 | 43.44 | 5 | Vilanova | XLPE+14201.8+61AA3.2 | CD | 62.8 | 27.78 | No | 2020-08-21 | C_s1_d2 | 0.72 | 17.6 | 22.8 | 894 | 48.5 | C | 4.6 | 0.01 | s1 | n | y | d2
TN_2020_2233 |  | 73193 20310305 | 736162B | RHZ1-2OL (AS) 12/20 KV 1X240 AL+H16 | 44.97 | 4 | Vilanova | XLPE+14202.5+61AA3.3 | CD | 64.2 | 30.29 | No | 2020-08-21 | B2_s2_d2 | 0.38 | 12.7 | 17.7 | 987 | 33.3 | B2 | 69.7 | 0.11 | s2 | n | y | d2
TN_2020_2234 |  | 76857 20335963 | 733571K | LXHIOZ1 1X240/16 | 46.06 | 4 | Vilanova | XLPE+14201.2+61AA1.8 | CD | 60 | 31.36 | No | 2020-08-24 | B2_s1_d0 | 0.67 | 8.7 | 11.9 | 732 | 35.9 | B2 | 5 | 0.01 | s1 | n | n | d0
TN_2020_2235 |  | 83742816 20267026 | 687488V | HEPRZ1 (AS) 30KV 1X630/25 | 59.22 | 4 | Vilanova | HEPR+14202.3+60003 | CD | 54.4 | 31.99 | No | 2020-08-24 | B2_s1_d2 | 1.04 | 14.5 | 24.1 | 1248 | 30.7 | B2 | 6.3 | 0.01 | s1 | n | y | d2
TN_2020_2236 |  | 78812 20345306 | 767104J | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.12 | 14 | Vilanova | PP+PAPEL+16HBTHICKNESSMEASURED:1.6 | CD | 76.1 | 27.07 | No | 2020-08-26 | E ou F_s2_d2 | 3.3 | 96.8 | 228.8 | 1299 | 237.7 | E ou F | 167.9 | 0.5 | s2 | n | y | d2
TN_2020_2237 |  | 78811 (1) 20345304 | 767118Z | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.61 | 13 | Vilanova | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.4+1.6 | CD | 74.7 | 27.61 | No | 2020-08-26 | C_s1_d2 | 1.56 | 21.1 | 33.8 | 1035 | 57.6 | C | 28.8 | 0.05 | s1 | n | y | d2
TN_2020_2238 |  | 78811(3) 20345304 | 767094Y | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.91 | 13 | Vilanova | PP+PAPEL+0.31420+16HBTHICKNESSMEASURED:0.4+1.4 | CD | 75.3 | 29.39 | No | 2020-08-26 | C_s1_d2 | 1.75 | 22.6 | 35.5 | 1152 | 41.8 | C | 24.9 | 0.04 | s1 | n | y | d2
TN_2020_2239 |  | 78813 (3) 20345303 | 767098C | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.12 | 15 | Vilanova | PP+PAPEL+0.31420+16HBTHICKNESSMEASURED:0.4+1.6 | CD | 70.9 | 31.3 | No | 2020-08-26 | B2_s1_d2 | 0.7 | 6.2 | 19.5 | 696 | 50.3 | B2 | 10.1 | 0.03 | s1 | n | y | d2
TN_2020_2240 |  | 78811 (2) 20345304 | 767088S | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.98 | 13 | Vilanova | PP+PAPEL+0.51420+16HATHICKNESSMEASURED:0.4+1.6 | CD | 62.9 | 33.54 | No | 2020-08-26 | B2_s1_d1 | 0.69 | 8.1 | 16.3 | 771 | 34.7 | B2 | 11.1 | 0.02 | s1 | y | n | d1
TN_2020_2250 |  | 78813 (1) 20345303 | 767110R | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.01 | 15 | Vilanova | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.3+1.7 | CD | 77.7 | 26.85 | No | 2020-08-27 | B2_s1_d1 | 0.8 | 7.5 | 19.1 | 726 | 49 | B2 | 10.6 | 0.02 | s1 | y | n | d1
TN_2020_2251 |  | 78813(2) 20345303 | 767119A | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.72 | 14 | Vilanova | PP+PAPEL+0.51420+16HATHICKNESSMEASURED:0.5+1.8 | CD | 79.8 | 28.32 | No | 2020-08-27 | B2_s1_d2 | 0.69 | 8.2 | 19.7 | 783 | 41.8 | B2 | 14.7 | 0.02 | s1 | n | y | d2
TN_2020_2252 |  |  | CAB 1 test 1 | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 78.4 | 29.03 | No | 2020-08-27 | C_s1_d0 | 1.31 | 16.2 | 29.7 | 915 | 55 | C | 48.3 | 0.12 | s1 | n | n | d0
TN_2020_2253 |  |  | CAB 1 test 2 | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 69.2 | 31.84 | No | 2020-08-27 | B2_s2_d0 | 1.21 | 14.7 | 28.3 | 846 | 52.4 | B2 | 55.7 | 0.15 | s2 | n | n | d0
TN_2020_2254 |  |  | CAB 1 test 3 | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 64.1 | 33.22 | No | 2020-08-27 | C_s2_d0 | 1.17 | 15.1 | 25.2 | 852 | 55.9 | C | 54.3 | 0.13 | s2 | n | n | d0
TN_2020_2255 |  |  | CAB 1 test 2 | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 74.1 | 27.49 | No | 2020-08-28 | B2_s1_d0 | 1.12 | 13.8 | 25.1 | 768 | 62.3 | B2 | 45.6 | 0.12 | s1 | n | n | d0
TN_2020_2256 |  |  | CAB 2 test 1 | LEONI 4 PAIR SHIELDED TWISTED PAIR DATA CABLE | 7 | 21 | Vilanova |  | CD | 74.7 | 27.17 | No | 2020-08-28 | B2_s1_d0 | 0.59 | 4.3 | 19.6 | 480 | 115.4 | B2 | 16.2 | 0.06 | s1 | n | n | d0
TN_2020_2257 |  |  | CAB 2 test 2 | LEONI 4 PAIR SHIELDED TWISTED PAIR DATA CABLE | 7 | 21 | Vilanova |  | CD | 75.8 | 29.79 | No | 2020-08-28 | C_s1_d1 | 1.5 | 16.5 | 29.7 | 621 | 141.6 | C | 21.2 | 0.07 | s1 | y | n | d1
TN_2020_2258 |  |  | CAB 2 test 3 | LEONI 4 PAIR SHIELDED TWISTED PAIR DATA CABLE | 7 | 21 | Vilanova |  | CD | 68.8 | 31.93 | No | 2020-08-28 | B2_s1_d2 | 0.8 | 4.1 | 22 | 537 | 115.9 | B2 | 16.4 | 0.05 | s1 | n | y | d2
TN_2020_2259 |  | 78815 20345305 | 767097B | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.41 | 17 | Vilanova | PP+PAPEL+16HBTHICKNESSMEASURED:1.6 | CD | 65.6 | 32.33 | No | 2020-08-28 | D_s2_d2 | 3.3 | 68.9 | 144.5 | 1374 | 135.2 | D | 96.5 | 0.26 | s2 | n | y | d2
TN_2020_2260 |  |  | CAB 3 test 1 | NEXANS POWER CABLE 0.6/1KV | 12 | 13 | Vilanova |  | CD | 67 | 18.37 | No | 2020-08-30 | B2_s1_d2 | 0.43 | 5.3 | 9.7 | 903 | 28 | B2 | 7.8 | 0.02 | s1 | n | y | d2
TN_2020_2261 |  |  | CAB 2 test 2 | LEONI 4 PAIR SHIELDED TWISTED PAIR DATA CABLE | 7 | 21 | Vilanova |  | CD | 60.7 | 18.39 | No | 2020-08-30 | B2_s1_d0 | 0.6 | 3.7 | 17 | 471 | 107.1 | B2 | 27.1 | 0.07 | s1 | n | n | d0
TN_2020_2262 |  | 78811 (2) 20345304 | 767088S | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.98 | 13 | Vilanova | PP+PAPEL+0.51420+16HATHICKNESSMEASURED:0.4+1.6 | CD | 58.8 | 19.22 | No | 2020-08-30 | B2_s1_d2 | 1.08 | 12.4 | 19.8 | 831 | 44.1 | B2 | 15.6 | 0.03 | s1 | n | y | d2
TN_2020_2263 |  |  | CAB 3 test 2 | NEXANS POWER CABLE 0.6/1KV | 12 | 13 | Vilanova |  | CD | 53.7 | 22.61 | No | 2020-08-30 | B2_s1_d0 | 0.27 | 1.7 | 4.5 | 540 | 16.4 | B2 | 6 | 0.01 | s1 | n | n | d0
TN_2020_2264 |  |  | CAB 3 test 3 | NEXANS POWER CABLE 0.6/1KV | 12 | 13 | Vilanova |  | CD | 47.6 | 26.34 | No | 2020-08-30 | B2_s1_d1 | 0.39 | 3.1 | 5.9 | 984 | 16.4 | B2 | 7.7 | 0.01 | s1 | y | n | d1
TN_2020_2265 |  | G 60090800 | 5096762 | U/UTP6 LSZH 60090800 PROTOTIPO G METRAGEM 4X2X0.5 | 5.72 | 25 | Vilanova | SHEATH:TPR-320.4+CONGUARDS6650*0.2 | CD | 64.1 | 18.12 | No | 2020-08-31 | D_s2_d2 | 3.3 | 33.3 | 227 | 723 | 536.6 | D | 69.3 | 0.42 | s2 | n | y | d2
TN_2020_2266 |  | 76857 20335963 | 736165E | LXH1OZ1 1X240/16 | 46.86 | 4 | Vilanova | XLPE+14201.1+61AA2.4 | CD | 59.4 | 18.86 | No | 2020-08-31 | B2_s1_d0 | 0.5 | 9.5 | 11.8 | 828 | 38.7 | B2 | 0.6 | 0 | s1 | n | n | d0
TN_2020_2267 |  | K 60090805 | 5096754 | U/UTP6 LSZH 60090805 PROTOTIPO K METRAGEM 4X2X0.5 | 5.65 | 25 | Vilanova | SHEATH:TPR-320.4+MEGOLONS533*0.2 | CD | 54.6 | 21.9 | No | 2020-08-31 | D_s2_d2 | 3.3 | 35.7 | 278.9 | 699 | 703.4 | D | 80.7 | 0.51 | s2 | n | y | d2
TN_2020_2268 |  | L 60090806 | 5096756 | U/UTP6 LSZH 60090806 PROTOTIPO L METRAGEM 4X2X0.5 | 5.98 | 25 | Vilanova | SHEATH:TPR-320.6+MEGOLONS533*0.2 | CD | 50.2 | 24.38 | No | 2020-08-31 | D_s2_d2 | 3.3 | 39.8 | 269.6 | 729 | 628.4 | D | 88.3 | 0.47 | s2 | n | y | d2
TN_2020_2269 |  | 77339 20313825 | 545870M | DHVMV 3X95 | 60.63 | 3 | Vilanova | ID7140IT+PVC2400+PVC2400 | CD | 54.1 | 26.76 | No | 2020-08-31 | B2_s3_d2 | 0.63 | 6.3 | 9.4 | 1500 | 30.1 | B2 | 738.2 | 0.92 | s3 | n | y | d2
TN_2020_2270 |  | M 60090807 | 5096760 | U/UTP6 LSZH 60090807 PROTOTIPO M METRAGEM 4X2X0.5 | 6.25 | 25 | Vilanova | SHEATH:TPR-320.8+MEGALONS533*0.2 | CD | 40.3 | 29.62 | No | 2020-08-31 | D_s2_d2 | 3.2 | 43.7 | 301.9 | 720 | 721.2 | D | 91.9 | 0.48 | s2 | n | y | d2
TN_2020_2271 |  | R 60090849 | 5096758 | U/UTP6 LSZH 60090849 PROTOTIPO R METRAGEM 4X2X0.5 | 5.58 | 25 | Vilanova | SHEATH:MEGOLONS533*0.55 | CD | 37.5 | 29.52 | No | 2020-08-31 | D_s2_d1 | 3.3 | 36.2 | 264.2 | 735 | 607.7 | D | 85.1 | 0.47 | s2 | y | n | d1
TN_2020_2272 |  | I 60090802 | 5096759 | U/UTP6 LSZH 60090800 PROTOTIPO I METRAGEM 4X2X0.5 | 6.37 | 25 | Vilanova | SHEATH:TPR-32+CONGUARDS6650*0.2 | CD | 40.8 | 26.7 | No | 2020-08-31 | D_s2_d2 | 3.3 | 34.8 | 119.1 | 981 | 175.1 | D | 79.8 | 0.25 | s2 | y | y | d2
TN_2020_2273 |  | S 60090850 | 5096761 | U/UTP6 LSZH 60090850 PROTOTIPO S METRAGEM 4X2X0.5 | 5.78 | 25 | Vilanova | SHEATH:MEGALONS533*0.75 | CD | 57.9 | 30.53 | No | 2020-09-01 | D_s2_d1 | 3.3 | 34.6 | 154.2 | 873 | 269.5 | D | 82.9 | 0.3 | s2 | y | n | d1
TN_2020_2274 |  |  | 5096752 | U/UTP6 | 5.63 | 25 | Vilanova | TPR55Y33 | CD | 52.1 | 28.55 | No | 2020-09-01 | D_s2_d2 | 3.3 | 36.5 | 237.2 | 804 | 472.6 | D | 104.8 | 0.59 | s2 | y | y | d2
TN_2020_2275 |  | 60080944 | 5096764 | JTL F/FTP/4P LSZH B500 DCA S2D2A1 4X2X23 AWG | 7.77 | 19 | Vilanova | LSOH | CD | 55 | 27.7 | No | 2020-09-01 | D_s2_d2 | 3.3 | 46.6 | 388.7 | 606 | 1293 | D | 88 | 0.52 | s2 | y | y | d2
TN_2020_2276 |  | H 60090801 | 5096763 | U/UTP6 LSZH 60090801 PROTOTIPO H METRAGEM 4X2X0.5 | 5.89 | 25 | Vilanova | SHEATH:TPR-320.6+CONGUARDS6650*0.2 | CD | 56.6 | 27.4 | No | 2020-09-01 | D_s2_d2 | 3.3 | 43.4 | 297.5 | 666 | 812.9 | D | 95.1 | 0.5 | s2 | y | y | d2
20080002 |  | 18388 | -- | AFUMEX TECNUC -PK3PS794-PRYSMIAN 255-12P1.00MM²-CU CL5-BLG-LSOH-0.3/0.5(0.6)-CSTB 74.C.068-K3 | 23 | 7 | Paron | IX2100FR+SW3100FR | -- | 46.8 | 23.6 | No | 2020-08-27 | B2_s1_d0 | 0.57 | 5.5 | 13.3 | 1497 | 15 | B2 | 15 | 0.07 | s1 | n | n | d0
20080003 |  | 18388 | -- | AFUMEX TECNUC -PK3CZ014-PRYSMIAN 255-19*0.5MM²-CU CL2-BLG-LSOH-0.3/0.5(0.6)-3 011 330-CSTB 74.C.068-K3 | 15.5 | 9 | Paron | IX2100FR+SW3100FR | -- | 46.1 | 24.3 | No | 2020-08-27 | B2_s2_d2 | 0.67 | 12.6 | 25.4 | 1356 | 24 | B2 | 58 | 0.12 | s2 | y | y | d2
20090002 |  | 18390 | -- | SNCF RESEAU -ZPFU- SH- 1*P1MM² CT445- PRYSMIAN 255 | 12 | 13 | Paron | TPR248+SW3800FR | -- | 47.9 | 21.8 | No | 2020-09-03 | D_s2_d2 | 2.1 | 32.8 | 46.9 | 921 | 92 | D | 68 | 0.09 | s2 | y | y | d2
20090001 |  | 18392 | EBM210942 | FR-N1X1G1 3G10MM² | 16.3 | 9 | Paron | IX1000FR+0400FEIT+5300SEIT | -- | 47.8 | 21.9 | No | 2020-09-03 | B2_s1_d1 | 0.67 | 5.2 | 8.7 | 1485 | 23 | B2 | 7 | 0.02 | s1 | y | n | d1
20090003 |  | 18392 |  | FR-N1X1G1 5G6MM² | 17.6 | 8 | Paron | IX1000FR+0400FEIT+5300SEIT | -- | 49.5 | 23.1 | No | 2020-09-04 | B2_s1_d2 | 0.6 | 4 | 9.3 | 1497 | 19 | B2 | 9 | 0.01 | s1 | y | y | d2
20090004 |  | 18392 |  | FR-N1X1G1 4G10MM² | 18.2 | 8 | Paron | IX1000FR+0400FEIT+5300SEIT | -- | 46.2 | 24.5 | No | 2020-09-04 | B2_s1_d0 | 0.5 | 5.3 | 7.4 | 1500 | 22 | B2 | 4 | 0.01 | s1 | n | n | d0
TN_2020_2278 |  |  | CAB 1 | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 63.6 | 22.5 | No | 2020-09-07 | C_s1_d1 | 1.42 | 20.6 | 37 | 855 | 75.6 | C | 45 | 0.08 | s1 | y | n | d1
TN_2020_2279 |  |  | CAB 2 | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 55.9 | 25.07 | No | 2020-09-07 | C_s1_d0 | 1.54 | 20.9 | 42 | 789 | 87.5 | C | 39 | 0.08 | s1 | n | n | d0
TN_2020_2280 |  |  | CAB 3 | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 45.1 | 28.45 | No | 2020-09-07 | C_s1_d0 | 1.42 | 20.8 | 39.4 | 783 | 83.5 | C | 40.5 | 0.08 | s1 | n | n | d0
TN_2020_2281 |  |  | CAB 2 test 3 | LEONI 4 PAIR SHIELDED TWISTED PAIR DATA CABLE | 7 | 10 | Vilanova | LSOH | CD | 42.8 | 29.66 | No | 2020-09-07 | D_s1_d2 | 1.21 | 11.6 | 70 | 528 | 309.2 | D | 28 | 0.1 | s1 | n | y | d2
TN_2020_2282 |  | 73193 20310305 | 736163C | RHZ1-2OL (AS) 20KV 1X240 AL+H16 | 43.52 | 5 | Vilanova | XLPE+14201.8+61AA3.4 | CD | 42.1 | 30.4 | No | 2020-09-07 | C_s1_d2 | 0.42 | 15.7 | 19.9 | 1044 | 39.2 | C | 15 | 0.06 | s1 | n | y | d2
TN_2020_2283 |  | 83775636 20339809 | 758223F | HEPRZ1 (AS) 45KV 1X150 AL+H25 | 44.8 | 4 | Vilanova | HEPR+1420FEES2.5+61AA3.5 | CD | 64.3 | 19.06 | No | 2020-09-08 | B2_s1_d0 | 0.97 | 14.5 | 18.6 | 1134 | 29.6 | B2 | 4 | 0.02 | s1 | n | n | d0
TN_2020_2277 |  |  | 5096753 | U/UTP6 TPR55 | 5.31 | 30 | Vilanova | LSOH | CD | 61.5 | 19.01 | No | 2020-09-08 | E ou F_s2_d2 | 3.3 | 38 | 369 | 546 | 1517.1 | E ou F | 86.4 | 0.54 | s2 | n | y | d2
TN_2020_2284 |  | 83767002 20193980 | 5096634 | AFUMEX CLASS 750V H07Z1-K (AS) 1X1.5 | 2.88 | 165 | Vilanova | 1602SEES | CD | 56.8 | 22.16 | No | 2020-09-08 | C_s2_d1 | 1.69 | 13.9 | 35 | 660 | 138.6 | C | 66.9 | 0.19 | s2 | y | n | d1
TN_2020_2285 |  | 83737791 20193987 | 5096633 | AFUMEX CLASS 750V H07Z1-K (AS) 1X2.5 | 3.53 | 120 | Vilanova | 1602SEES | CD | 52.4 | 23.65 | No | 2020-09-08 | C_s1_d0 | 1.21 | 10.9 | 30.4 | 612 | 132.7 | C | 48.8 | 0.17 | s1 | n | n | d0
TN_2020_2286 |  | 73193 20310305 | 736175R | RHZ1-2OL (AS) 12/20 KV 1X240 AL+H16 | 43.44 | 5 | Vilanova | XLPE+14201.8+61AA3.2 | CD | 49.7 | 27.55 | No | 2020-09-08 | B2_s1_d1 | 0.89 | 12.5 | 19.1 | 915 | 40.7 | B2 | 43.2 | 0.15 | s1 | y | n | d1
CEL-0573-20-1 |  | 83638404 20193641 | 702029A | AFUMEX CLASS 1KV RZ1-K (AS) 1X95MM2 | 18.06 | 8 | CEIS | SXLPE+1420FEES+1602SEES | CD | 30 | 34.57 | No | 2020-08-07 | B2_s1_d2 | 0.72 | 12.2 | 23.5 | 1290 | 28 | B2 | 2.9 | 0.01 | s1 | n | y | d2
TN_2020_2287 |  | 73193 20310305 | 736162B | RHZ1-2OL (AS) 12/20 KV 1X240 AL+H16 | 44.97 | 4 | Vilanova | XLPE+14202.5+61AA3.3 | CD | 45.1 | 27.39 | No | 2020-09-08 | C_s1_d2 | 1.32 | 16.7 | 20.9 | 978 | 39.7 | C | 9.8 | 0.03 | s1 | n | y | d2
TN_2020_2288 |  | 83742816 20267026 | 687488V | HEPRZ1 (AS) 30KV 1X630/25 | 59.22 | 4 | Vilanova | HEPR+14202.3+60003 | CD | 46.6 | 27.27 | No | 2020-09-08 | C_s1_d2 | 1.29 | 17 | 24.7 | 1227 | 31.4 | C | 10.4 | 0.02 | s1 | n | y | d2
CEL-0871-20-1 |  | 83742816 20267026 | 687488V | HEPRZ1 (AS) 30KV 1X630/25 | 59.22 | 4 | CEIS | HEPR+14202.3+60003 | CD | 46.6 | 27.27 | No | 2020-10-21 | D_s1_d2 | 1.5 | 39.71 | 67.55 |  | 64.28 | D | 3.4 | 0.01 | s1 | n | y | d2
TN_2020_2289 |  | 76857 20335963 | 733571K | LXHIOZ1 1X240/16 | 46.06 | 4 | Vilanova | XLPE+14201.2+61AA1.8 | CD | 48.4 | 26.62 | No | 2020-09-08 | B2_s1_d0 | 1.23 | 9 | 13.4 | 708 | 39.7 | B2 | 9.2 | 0.02 | s1 | n | n | d0
TN_2020_2290 |  | 76822 20313251 | 459719V | DHVMAV 6/10 KV 1X120 | 35.12 | 5 | Vilanova | ID72AA+PVC2400+PVCFKN939 | CD | 49.2 | 26.33 | No | 2020-09-08 | B2_s3_d2 | 0.79 | 13.6 | 27.3 | 1377 | 48.7 | B2 | 904.1 | 1.14 | s3 | n | y | d2
TN_2020_2291 |  | 75863 | 704843J | AFUMEX ATEX RZ1MZ1-K 2RH 4G10 1KV CCA | 20.59 | 7 | Vilanova | GFR380 | CD | 72.4 | 20.44 | No | 2020-09-09 | B2_s1_d2 | 0.69 | 10.1 | 18.3 | 1497 | 28.1 | B2 | 19.5 | 0.07 | s1 | n | y | d2
TN_2020_2292 |  | 75862 | 710982G | AFUMEX ATEX RZ1MZ1-K 2RH 3X35 1KV CCA | 28.23 | 6 | Vilanova | GFR380 | CD | 73 | 20.69 | No | 2020-09-09 | B2_s1_d2 | 0.62 | 6.2 | 9 | 1443 | 22.8 | B2 | 5.6 | 0.01 | s1 | n | y | d2
TN_2020_2293 |  | 77806 20267026 | 758233S | HEPRZ1 (AS) 30KV 1X630/25 | 59.69 | 4 | Vilanova | HEPR+1420FEES2.2+61AA3.5 | CD | 77.1 | 24.6 | No | 2020-09-09 | C_s1_d0 | 0.85 | 16.6 | 26 | 1434 | 28.5 | C | 0 | 0 | s1 | n | n | d0
20090005 |  | 18392 | -- | FR-N1X1G1 5G4MM² | 15.9 | 9 | Paron | IX1000FR+0400FEIT+5300SEIT | -- | 48.8 | 24.5 | No | 2020-09-09 | B2_s1_d2 | 0.7 | 7.9 | 13 | 1335 | 34 | B2 | 10 | 0.02 | s1 | y | y | d2
20090006 |  | 18392 | -- | FR-N1X1G1 3G6MM² | 14.4 | 11 | Paron | IX1000FR+0400FEIT+5300SEIT | -- | 48.3 | 22.9 | No | 2020-09-09 | B2_s1_d0 | 0.7 | 10.3 | 16.3 | 1278 | 28 | B2 | 19 | 0.04 | s1 | n | n | d0
20090007 |  | 18392 | -- | FR-N1X1G1 4G6MM² | 15.5 | 9 | Paron | IX1000FR+0400FEIT+5300SEIT | -- | 48.1 | 9 | No | 2020-09-09 | B2_s1_d2 | 0.7 | 8 | 14.4 | 1359 | 18 | B2 | 16 | 0.03 | s1 | y | y | d2
TN_2020_2294 |  | 74801 20292827 | 729239B | AL ROZ1-K DCA TELEMANDO SEC 1KV 2X25 | 20.07 | 8 | Vilanova | XLPE+PET+CINTAAL/PET+1602SEES | CD | 75 | 19.63 | No | 2020-09-10 | D_s2_d2 | 1.71 | 40.1 | 77.1 | 1110 | 95.9 | D | 64.3 | 0.15 | s2 | n | y | d2
TN_2020_2295 |  | 74921 20321141 | 729235X | AL ROZ1-K DCA TELEMANDO SEC 1KV 2X50 | 25.24 | 7 | Vilanova | XLPE+PET+CINTAAL/PET+1602SEES | CD | 73.4 | 21.01 | No | 2020-09-10 | D_s2_d2 | 1.25 | 27.5 | 68.8 | 1176 | 78.6 | D | 64.9 | 0.19 | s2 | n | y | d2
TN_2020_2298 |  | 78811 (2) 20345304 | 767088S | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.98 | 13 | Vilanova | PP+PAPEL+0.51420+16HATHICKNESSMEASURED:0.4+1.6 | CD | 53.7 | 31.55 | No | 2020-09-10 | D_s1_d2 | 2.37 | 39.6 | 59.3 | 1053 | 101.4 | D | 36 | 0.06 | s1 | n | y | d2
TN_2020_2299 |  | 78811(3) 20345304 | 767094Y | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.91 | 13 | Vilanova | PP+PAPEL+0.31420+16HBTHICKNESSMEASURED:0.4+1.4 | CD | 53.7 | 31.81 | No | 2020-09-10 | E ou F_s2_d2 | 2.76 | 72.8 | 133.8 | 1305 | 136.6 | E ou F | 100.4 | 0.37 | s2 | n | y | d2
TN_2020_2300 |  | 78811 (1) 20345304 | 767118Z | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.61 | 13 | Vilanova | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.4+1.6 | CD | 58 | 27.82 | No | 2020-09-10 | D_s2_d2 | 3.3 | 50.9 | 85.7 | 1494 | 100.7 | D | 70.8 | 0.15 | s2 | n | y | d2
TN_2020_2302 |  | 79231 60090808 | 5096662 | U/UTP 6 4X2X0.5: XWEB ZH DE WA | 5.55 | 25 | Vilanova | BAINHAMEGOLONS533NS0.55N | CD | 68.2 | 21.79 | No | 2020-09-11 | D_s2_d1 | 3.3 | 30.8 | 155.8 | 672 | 427.3 | D | 76 | 0.3 | s2 | y | n | d1
TN_2020_2303 |  | 79230 60090803 | 5096661 | U/UTP 6: 4X2X0.5: XWEB ZH DE WA | 5.53 | 25 | Vilanova | BAINHACONGUARDS66500.55P | CD | 66.7 | 21.92 | No | 2020-09-11 | D_s2_d1 | 3.3 | 35 | 163.1 | 666 | 446.7 | D | 55.9 | 0.29 | s2 | y | n | d1
TN_2020_2304 |  | 78813 (3) 20345303 | 767098C | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.12 | 15 | Vilanova | PP+PAPEL+0.31420+16HBTHICKNESSMEASURED:0.4+1.6 | CD | 63.3 | 24.73 | No | 2020-09-11 | C_s1_d2 | 1.86 | 25 | 39.2 | 903 | 92.2 | C | 15.5 | 0.03 | s1 | n | y | d2
TN_2020_2305 |  | 78813(2) 20345303 | 767119A | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.72 | 14 | Vilanova | PP+PAPEL+0.51420+16HATHICKNESSMEASURED:0.5+1.8 | CD | 58.2 | 27.71 | No | 2020-09-11 | D_s1_d2 | 1.81 | 30.4 | 49.5 | 894 | 86.4 | D | 31.1 | 0.05 | s1 | n | y | d2
TN_2020_2306 |  | 78813 (1) 20345303 | 767110R | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.01 | 15 | Vilanova | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.3+1.7 | CD | 51.7 | 30.4 | No | 2020-09-11 | D_s2_d2 | 3.3 | 63.9 | 94.7 | 1392 | 146.6 | D | 64.9 | 0.13 | s2 | n | y | d2
TN_2020_2307 |  | 70182 | 5096635 | CABLESTYL SOZ1-K (AS+)500V 2X1.5 | 8.08 | 19 | Vilanova |  | CD | 56.,6 | 31.54 | No | 2020-09-14 | B2_s1_d0 | 0.86 | 7.5 | 25.6 | 618 | 84.1 | B2 | 20.8 | 0.06 | s1 | n | n | d0
TN_2020_2308 |  | 79231 60090808 | 5096662 | U/UTP 6 4X2X0.5: XWEB ZH DE WA | 5.55 | 25 | Vilanova | BAINHAMEGOLONS533NS0.55N | CD | 58 | 31.97 | No | 2020-09-14 | D_s2_d0 | 3.3 | 27.1 | 121 | 696 | 306.3 | D | 59.2 | 0.21 | s2 | n | n | d0
TN_2020_2309 |  | 79230 60090803 | 5096661 | U/UTP 6: 4X2X0.5: XWEB ZH DE WA | 5.53 | 25 | Vilanova | BAINHACONGUARDS66500.55P | CD | 54.2 | 31.37 | No | 2020-09-14 | D_s2_d1 | 3.3 | 31.3 | 188.5 | 657 | 530.7 | D | 72.1 | 0.37 | s2 | y | n | d1
TN_2020_2310 |  | 74922 20321191 | 729717W | AL ROZ1-K 2X50MM2 B2CA S1A D1 A1 | 27.9 | 6 | Vilanova | XLPE+AL/PE+1420+1602ONESHOT | CD | 71.5 | 20.19 | No | 2020-09-15 | B2_s1_d0 | 0.5 | 8.6 | 11.2 | 912 | 21.5 | B2 | 9.5 | 0.02 | s1 | n | n | d0
TN_2020_2311 |  | 76857 20335963 | 736165E | LXH1OZ1 1X240/16 | 46.86 | 4 | Vilanova | XLPE+14201.1+61AA2.4 | CD | 68.3 | 23.18 | No | 2020-09-15 | C_s1_d1 | 0.72 | 15.4 | 16.9 | 771 | 42.8 | C | 15.4 | 0.02 | s1 | y | n | d1
TN_2020_2244 |  | 78597 | 5096765 | PRYSUN H1Z2Z2-K 1X6 1.5 KV | 6.35 | 25 | Vilanova | ID3800/GV4200FR | CD | 69.2 | 26.04 | No | 2020-09-15 | D_s2_d2 | 3.3 | 42.5 | 115.2 | 771 | 304 | D | 124.9 | 0.38 | s2 | n | y | d2
TN_2020_2241 |  | 78589 20344953 | 5096769 | PRYSUN H1Z2Z2-K 1X6 1.5 KV | 5.93 | 25 | Vilanova | ID3800FR/41AA | CD | 67.2 | 28.61 | No | 2020-09-15 | E ou F_s2_d2 | 3.3 | 50.2 | 413.6 | 543 | 1779.1 | E ou F | 66.8 | 0.39 | s2 | n | y | d2
TN_2020_2312 |  | 77806 20267026 | 758233S | HEPRZ1 (AS) 30KV 1X630/25 | 59.69 | 4 | Vilanova | HEPR+1420FEES2.2+61AA3.5 | CD | 63.5 | 30.7 | No | 2020-09-15 | C_s1_d0 | 0.93 | 18.6 | 31.6 | 1494 | 29 | C | 6.3 | 0.01 | s1 | n | n | d0
TN_2020_2243 |  | 78599 20344955 | 5096766 | PRYSUN H1Z2Z2-K 1X6 1.5 KV | 6.25 | 25 | Vilanova | ID8340/GV4200FR | CD | 76.2 | 23.48 | No | 2020-09-16 | D_s2_d2 | 3.3 | 51.6 | 281.8 | 666 | 770 | D | 107.5 | 0.51 | s2 | n | y | d2
TN_2020_2242 |  | 78598 20344954 | 5096768 | PRYSUN H1Z2Z2-K 1X6 1.5 KV | 6.45 | 25 | Vilanova | ID8000IT/4200FR | CD | 76.8 | 23.24 | No | 2020-09-16 | D_s2_d2 | 3.3 | 54.8 | 315 | 681 | 836 | D | 99.3 | 0.55 | s2 | n | y | d2
TN_2020_2313 |  | 74803 20321190 | 735894K | AL ROZ1-K 2X25 MM2 B2CA S1A D1 A1 | 22.1 | 7 | Vilanova | XLPE+AL/PE+1420+1602ONESHOT | CD | 76.7 | 25.73 | No | 2020-09-16 | B2_s1_d0 | 0.57 | 8 | 10.3 | 875 | 23.2 | B2 | 20.8 | 0.03 | s1 | n | n | d0
TN_2020_2245 |  | 78699 20345697 | 5096767 | PRYSUN H1Z2Z2-K 1X6 1.5 KV | 6 | 25 | Vilanova | GOM01/471AA | CD | 74.4 | 27.93 | No | 2020-09-16 | E ou F_s2_d2 | 3.3 | 47.4 | 403.6 | 549 | 1644.8 | E ou F | 66.9 | 0.44 | s2 | n | y | d2
TN_2020_2246 |  | 78594 20344950 | 5096770 | PRYSUN H1Z2Z2-K 1X6 1.5 KV | 6.58 | 21 | Vilanova | ID72AA/41AA | CD | 68.8 | 29.64 | No | 2020-09-16 | E ou F_s2_d2 | 3.3 | 48.7 | 408.1 | 567 | 1535.1 | E ou F | 68.8 | 0.34 | s2 | n | y | d2
20090008 |  | 18392 | -- | FR-N1X1G1 4G2.5MM² | 13 | 12 | Paron | IX1000FR+0400FEIT+5300SEIT | -- | 51.8 | 21 | No | 2020-09-14 | B2_s1_d1 | 0.67 | 8.1 | 11.6 | 1113 | 30 | B2 | 18 | 0.04 | s1 | y | n | d1
20090009 |  | 18392 | -- | FR-N1X1G1 3G4MM² | 13 | 12 | Paron | IX1000FR+0400FEIT+5300SEIT | -- | 51.8 | 22.2 | No | 2020-09-14 | B2_s1_d1 | 0.67 | 8.3 | 11.5 | 1110 | 28 | B2 | 13 | 0.02 | s1 | y | n | d1
20090010 |  | 18392 | -- | FR-N1X1G1 4G4MM² | 14.6 | 10 | Paron | IX1000FR+0400FEIT+5300SEIT | -- | 57.1 | 22.7 | No | 2020-09-14 | B2_s1_d2 | 0.67 | 8.6 | 14.8 | 1137 | 25 | B2 | 23 | 0.03 | s1 | y | y | d2
TN_2020_2247 |  | 78594 | 5096771 | PRYSUN H1Z2Z2-K 1X6 1.5 KV | 6.15 | 25 | Vilanova | ID2000/41AA | CD | 66.4 | 22.33 | No | 2020-09-17 | E ou F_s2_d2 | 3.3 | 50 | 373.9 | 573 | 1403.2 | E ou F | 53.5 | 0.29 | s2 | n | y | d2
TN_2020_2316 |  | 73193 20310305 | 736163C | RHZ1-2OL (AS) 20KV 1X240 AL+H16 | 43.52 | 5 | Vilanova | XLPE+14201.8+61AA3.4 | CD | 65.8 | 22.62 | No | 2020-09-17 | C_s1_d2 | 0.93 | 17.3 | 23.7 | 870 | 50.5 | C | 21.6 | 0.07 | s1 | n | y | d2
TN_2020_2248 |  | 78595 | 5096772 | PRYSUN H1Z2Z2-K 1X6 1.5 KV | 6.15 | 25 | Vilanova | ID8000IT/41AA | CD | 61.6 | 25.48 | No | 2020-09-17 | E ou F_s2_d2 | 3.3 | 55.4 | 473.8 | 564 | 1814.4 | E ou F | 66.9 | 0.42 | s2 | n | y | d2
TN_2020_2249 |  | 78596 20344952 | 5096774 | PRYSUN H1Z2Z2-K 1X6 1.5 KV | 6.23 | 25 | Vilanova | ID8340IT/41AA | CD | 58.2 | 28.15 | No | 2020-09-17 | E ou F_s2_d2 | 3.3 | 55 | 444.9 | 591 | 1561.3 | E ou F | 65.7 | 0.32 | s2 | n | y | d2
TN_2020_2317 |  | 83795645 80193655 | 764178D | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.71 | 13 | Vilanova | CUBIERTAAFUMEXRM631582 | CD | 55.8 | 30.36 | No | 2020-09-17 | D_s1_d1 | 2.15 | 34.4 | 46.2 | 1149 | 74.6 | D | 32.6 | 0.06 | s1 | y | n | d1
TN_2020_2318 |  | 83795645 80193655 | 764178D | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.71 | 13 | Vilanova | CUBIERTAAFUMEXRM631582 | CD | 75.7 | 23.75 | No | 2020-09-18 | C_s1_d1 | 1.83 | 29.7 | 37.1 | 1068 | 73.2 | C | 34 | 0.06 | s1 | y | n | d1
TN_2020_2319 |  | 83795645 80193655 | 764178D | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.71 | 13 | Vilanova | CUBIERTAAFUMEXRM631582 | CD | 74 | 23.97 | No | 2020-09-18 | D_s1_d0 | 1.71 | 35.3 | 43.9 | 1248 | 68.6 | D | 27.5 | 0.06 | s1 | n | n | d0
TN_2020_2320 |  | 78697 | 5096794 | PRYSUN H1Z2Z2-K 1X6 1.5 KV | 5.99 | 25 | Vilanova | 3G705+41AA | CD | 69.8 | 22.27 | No | 2020-09-21 | E ou F_s2_d2 | 3.3 | 47.7 | 452.3 | 558 | 1768.2 | E ou F | 59.1 | 0.34 | s2 | n | y | d2
TN_2020_2321 |  | 78698 | 5096795 | PRYSUN H1Z2Z2-K 1X6 1.5 KV | 6.13 | 25 | Vilanova | TECSUNVERSION | CD | 68.5 | 22.55 | No | 2020-09-21 | D_s2_d2 | 3.3 | 46.9 | 271.7 | 705 | 670.9 | D | 105.3 | 0.48 | s2 | n | y | d2
TN_2020_2324 |  | 890669 | 727937L | EATST 25X4X0.90 | 39.55 | 5 | Vilanova | TPR28+TPR55 | CD | 47 | 30.9 | No | 2020-09-22 | B2_s1_d0 | 0.26 | 6.6 | 8.7 | 1032 | 27.6 | B2 | 4.3 | 0.01 | s1 | n | n | d0
TN_2020_2325 |  | 890664 | 10J2614 | EATST 2X1.4 | 13.64 | 11 | Vilanova | TPR28+TPR55 | CD | 47.5 | 29.98 | No | 2020-09-22 | B2_s1_d0 | 0.27 | 4.6 | 8.4 | 519 | 46.8 | B2 | 5 | 0.01 | s1 | n | n | d0
TN_2020_2326 |  | 890671 | 14J7742 | EATST 10X4X1.4 | 35.91 | 5 | Vilanova | TPR28+TPR55 | CD | 54.8 | 29.93 | No | 2020-09-22 | B2_s1_d0 | 0.26 | 7.6 | 10.1 | 795 | 34.1 | B2 | 0.5 | 0 | s1 | n | n | d0
TN_2020_2327 |  | 890668 | 708491Z | EATST 14X4X0.9 | 34.33 | 5 | Vilanova | TPR28+TPR55 | CD | 49.3 | 30.45 | No | 2020-09-22 | B2_s1_d0 | 0.39 | 10.4 | 12.5 | 774 | 40 | B2 | 8.9 | 0.02 | s1 | n | n | d0
TN_2020_2328 |  | 76442 20319578 | 727841G | DHZ1MAZ1-OL(AS) RH 10 KV 1X120 AFUMEX | 41.47 | 5 | Vilanova | 1420+1602+GSWARMOUR+GFR380 | CD | 50 | 28.05 | No | 2020-09-22 | B2_s1_d0 | 0.31 | 8.3 | 9.4 | 858 | 39.9 | B2 | 7.4 | 0.01 | s1 | n | n | d0
TN_2020_2329 |  | 77468 20318519 | 720087D | DHZ1MZ1(AS) RH 10 KV 3X95 AFUMEX | 62.79 | 3 | Vilanova | 1420+1602+GSWARMOUR+GFR380 | CD | 71.3 | 20.08 | No | 2020-09-23 | B2_s1_d1 | 0.36 | 4.2 | 5.7 | 603 | 22.1 | B2 | 0 | 0 | s1 | y | n | d1
TN_2020_2330 |  | 74803 20321190 | 735894K | AL ROZ1-K 2X25 MM2 B2CA S1A D1 A1 | 22.1 | 7 | Vilanova | XLPE+AL/PE+1420+1602ONESHOT | CD | 70 | 22.28 | No | 2020-09-23 | B2_s1_d0 | 0.68 | 10.8 | 14.7 | 1500 | 26.8 | B2 | 10.5 | 0.02 | s1 | n | n | d0
TN_2020_2331 |  | 74922 20321191 | 729717W | AL ROZ1-K 2X50MM2 B2CA S1A D1 A1 | 27.9 | 6 | Vilanova | XLPE+AL/PE+1420+1602ONESHOT | CD | 67.9 | 25.24 | No | 2020-09-23 | B2_s1_d0 | 0.68 | 7.4 | 9.8 | 888 | 20.5 | B2 | 8.4 | 0.02 | s1 | n | n | d0
TN_2020_2332 |  | 77339 20313825 | 545870M | DHVMV 3X95 | 60.63 | 3 | Vilanova | ID7140IT+PVC2400+PVC2400 | CD | 63.5 | 27.19 | No | 2020-09-23 | B2_s3_d0 | 0.79 | 13.2 | 14 | 1500 | 67.4 | B2 | 940.7 | 1 | s3 | n | n | d0
TN_2020_2333 |  | 76822 20313251 | 459719V | DHVMAV 6/10 KV 1X120 | 35.12 | 5 | Vilanova | ID72AA+PVC2400+PVCFKN939 | CD | 60.9 | 28.7 | No | 2020-09-23 | C_s3_d2 | 1.1 | 26.8 | 53.8 | 1497 | 75.1 | C | 1076.4 | 1.43 | s3 | n | y | d2
TN_2020_2334 |  | 83775636 20339809 | 758223F | HEPRZ1 (AS) 45KV 1X150 AL+H25 | 44.8 | 4 | Vilanova | HEPR+1420FEES2.5+61AA3.5 | CD | 50.9 | 32.4 | No | 2020-09-23 | B2_s1_d0 | 0.61 | 11.5 | 14.4 | 1065 | 31.1 | B2 | 4.7 | 0.03 | s1 | n | n | d0
TN_2020_2322 |  | 77495 60089068 | 5096755 | ACOMETIDA INTERIOR 1X2X0.50 | 3.83 | 90 | Vilanova | MEGOLONS643WV | CD | 60.2 | 22.35 | No | 2020-09-24 | D_s2_d1 | 3.3 | 65.4 | 168.2 | 1008 | 273.8 | D | 58.8 | 0.13 | s2 | y | n | d1
TN_2020_2323 |  | 77436 60087613 | 5096757 | ACOMETIDA INTERIOR 1X2X0.50 | 3.8 | 90 | Vilanova | TPR-32+SKINTPR-53 | CD | 61.7 | 22.18 | No | 2020-09-24 | D_s2_d2 | 3.3 | 65.8 | 195.9 | 963 | 299.4 | D | 51.1 | 0.19 | s2 | n | y | d2
|  | 78437 20343748 | 735484P | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 10.85 | 14 | Manlleu | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 50 | 23.1 | No | 2020-09-23 | D_s1_d2 | 2.34 | 19.5 | 29.6 | 1455 | 38.1 | D | 17.6 | 0.05 | s1 | n | y | d2
|  | 78436 20343747 | 708809V | EXZHELLENT COMPACT RZ1-K (AS) 1KV 2X16 | 15.65 | 9 | Manlleu | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 50 | 23 | No | 2020-09-24 | B2_s1_d2 | 0.82 | 5.5 | 11.6 | 1368 | 11 | B2 | 0.2 | 0 | s1 | n | y | d2
|  | 78438 20343749 | 708816C | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G16 | 20.34 | 8 | Manlleu | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 50 | 23.3 | No | 2020-09-23 | B2_s1_d2 | 1.24 | 11.1 | 27 | 1500 | 24.1 | B2 | 1.3 | 0.01 | s1 | n | y | d2
20090011 |  | 18417 | -- | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Paron | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | -- | 49.9 | 23.4 | No | 2020-09-24 | C_s2_d0 | 1.2 | 16.3 | 26.8 | 987 | 57 | C | 61 | 0.14 | s2 | n | n | d0
20090012 |  | 18417 | -- | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Paron | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | -- | 52.4 | 22.5 | No | 2020-09-24 | C_s2_d0 | 1.18 | 17 | 29.8 | 843 | 60 | C | 64 | 0.15 | s2 | n | n | d0
20090013 |  | 18415 | -- | SNCF RESEAU -ZPFU- SH- 1*P1MM² CT445- PRYSMIAN 255 | 12 | 13 | Paron | TPR248+SW3800FR | -- | 48.4 | 23.5 | No | 2020-09-26 | C_s2_d2 | 1 | 15.8 | 22.6 | 1104 | 45 | C | 56 | 0.11 | s2 | y | y | d2
TN_2020_2343 |  | 78811 (1) 20345304 | 767118Z | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.61 | 13 | Vilanova | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.4+1.6 | CD | 49.4 | 16.25 | No | 2020-09-26 | D_s2_d2 | 2.4 | 38.5 | 57.3 | 975 | 91.5 | D | 53.3 | 0.09 | s2 | n | y | d2
TN_2020_2344 |  | 78437 20343748 | 735484P | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 10.82 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 46.3 | 19.14 | No | 2020-09-26 | E ou F_s2_d2 | 3.3 | 70.7 | 206.6 | 1491 | 173.5 | E ou F | 97.8 | 0.42 | s2 | n | y | d2
TN_2020_2345 |  | 78811 (2) 20345304 | 767088S | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.98 | 13 | Vilanova | PP+PAPEL+0.51420+16HATHICKNESSMEASURED:0.4+1.6 | CD | 41.9 | 23.15 | No | 2020-09-26 | D_s1_d2 | 2.26 | 36 | 52.2 | 1035 | 89.4 | D | 37.7 | 0.07 | s1 | n | y | d2
TN_2020_2346 |  | 78813(2) 20345303 | 767119A | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.72 | 14 | Vilanova | PP+PAPEL+0.51420+16HATHICKNESSMEASURED:0.5+1.8 | CD | 37.6 | 26.04 | No | 2020-09-26 | C_s1_d2 | 1.47 | 20.3 | 32.3 | 786 | 74.6 | C | 28.8 | 0.04 | s1 | n | y | d2
TN_2020_2347 |  | 78437 20343748 | 735484P | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 10.82 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 46.2 | 16.05 | No | 2020-09-28 | D_s2_d2 | 3.3 | 54.5 | 117.9 | 1494 | 98.8 | D | 72.3 | 0.17 | s2 | n | y | d2
TN_2020_2348 |  | 78813 (1) 20345303 | 767110R | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.01 | 15 | Vilanova | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.3+1.7 | CD | 46.6 | 16.16 | No | 2020-09-28 | C_s1_d2 | 1.99 | 28.8 | 47 | 948 | 97.3 | C | 28.7 | 0.05 | s1 | n | y | d2
TN_2020_2341 |  | 83769133 20193677 | 751708Z | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.79 | 13 | Vilanova | 1420+1602 | CD | 47 | 19.43 | No | 2020-09-28 | D_s1_d2 | 3.3 | 59.1 | 184.9 | 1500 | 154.1 | D | 36.1 | 0.18 | s1 | n | y | d2
TN_2020_2349 |  | 83698813 20193661 | 751706X | AFUMEX CLASS 1KV RZ1-K (AS) 4X10 | 11.79 | 13 | Vilanova | 1420+1602 | CD | 42.8 | 23.08 | No | 2020-09-28 | C_s1_d2 | 1.33 | 21.6 | 43.5 | 1443 | 38.1 | C | 17 | 0.04 | s1 | n | y | d2
TN_2020_2350 |  |  | BBT 908944 | CABLE RTE SF 740 2X16MM2 | 20.96 | 7 | Vilanova | INSULATION4400IPFR+BEDDING1200FPFR+INNERSHEATH1000GPFR+OUTERSHEATH2800SPFR | CD | 39.8 | 24.52 | No | 2020-09-28 | B2_s3_d2 | 0.91 | 11.5 | 23.4 | 723 | 55.4 | B2 | 446.3 | 0.87 | s3 | n | y | d2
TN_2020_2352 |  |  | BBT 908947 | CABLE RTE SF 740 37X1.5MM2 | 30.69 | 6 | Vilanova | INSULATION4400IPFR+BEDDING1200FPFR+INNERSHEATH1000GPFR+OUTERSHEATH2800SPFR | CD | 56.7 | 17.47 | No | 2020-09-29 | C_s3_d2 | 1.13 | 18.7 | 26.5 | 1065 | 57.5 | C | 869.8 | 1.03 | s3 | n | y | d2
TN_2020_2353 |  | 78437 20343748 | 735484P | EXZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 10.82 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 53.6 | 17.15 | No | 2020-09-29 | D_s2_d2 | 3.3 | 44.8 | 68.4 | 1473 | 84.9 | D | 64.4 | 0.15 | s2 | n | y | d2
TN_2020_2340 |  | 20226053 | 684707X | AFUMEX PANELES H07Z1-R (AS) 1X16 | 6.78 | 21 | Vilanova | INSULATIONAFUMEXCPRBASE+INSULATIONAFUMEXCPRSKIN | CD | 50.3 | 20.59 | No | 2020-09-29 | B2_s1_d1 | 0.88 | 4.7 | 18.3 | 516 | 92.5 | B2 | 7.3 | 0.02 | s1 | y | n | d1
TN_2020_2351 |  | 83552002 20193654 | 5096632 | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.57 | 14 | Vilanova | 1420+1602 | CD | 50.4 | 24.75 | No | 2020-09-29 | D_s1_d2 | 2.52 | 36.3 | 50.1 | 570 | 94.6 | D | 38 | 0.07 | s1 | n | y | d2
TN_2020_2354 |  | 74965 20316993 | 667287M | EXZHELLENT RZ1-K (AS) 1 KV 5G1.5 | 11.97 | 13 | Vilanova | SXLPE+0400FEIT+1602SEES | CD | 52 | 27.38 | No | 2020-09-29 | C_s1_d1 | 1.62 | 25.4 | 34 | 894 | 63.3 | C | 32.3 | 0.05 | s1 | y | n | d1
TN_2020_2357 |  | 784439 20343787 | 708825M | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G4 | 11.31 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 67 | 17.49 | No | 2020-09-30 | D_s2_d2 | 2.12 | 34.9 | 46.5 | 1122 | 69.7 | D | 53 | 0.12 | s2 | n | y | d2
TN_2020_2358 |  | 77495 60089068 | 5096755 | ACOMETIDA INTERIOR 1X2X0.50 | 3.83 | 90 | Vilanova | MEGOLONS643WV | CD | 66.2 | 17.53 | No | 2020-09-30 | D_s2_d2 | 3.3 | 63.1 | 188.3 | 1050 | 251 | D | 67.8 | 0.2 | s2 | n | y | d2
TN_2020_2359 |  | 78440 20343785 | 748697B | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G1.5 | 9.34 | 17 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 61.4 | 23.65 | No | 2020-09-30 | D_s2_d2 | 3.3 | 69.3 | 116.5 | 1344 | 122.6 | D | 108.1 | 0.24 | s2 | n | y | d2
TN_2020_2360 |  | 78441 20343786 | 748691V | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 10.36 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 60.4 | 26.46 | No | 2020-09-30 | D_s1_d2 | 2.12 | 30.4 | 39.9 | 771 | 84.7 | D | 43.3 | 0.08 | s1 | n | y | d2
TN_2020_2361 |  | 74965 20316993 | 667287M | EXZHELLENT RZ1-K (AS) 1 KV 5G1.5 | 11.97 | 13 | Vilanova | SXLPE+0400FEIT+1602SEES | CD | 56 | 27.12 | No | 2020-09-30 | C_s1_d0 | 1.79 | 26.7 | 35.9 | 1089 | 55.8 | C | 31.2 | 0.07 | s1 | n | n | d0
|  | 784439 20343787 | 708825M | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G4 | 11.31 | 14 | Manlleu | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 26 | 22.1 | No | 2020-09-25 | B2_s1_d0 | 0.58 | 6.1 | 10.4 | 810 | 21.5 | B2 | 8.1 | 0.02 | s1 | n | n | d0
|  | 74965 20316993 | 667287M | EXZHELLENT RZ1-K (AS) 1 KV 5G1.5 | 11.97 | 13 | Manlleu | SXLPE+0400FEIT+1602SEES | CD | 33 | 22.9 | No | 2020-09-25 | B2_s1_d0 | 0.52 | 5.1 | 10.3 | 762 | 22.4 | B2 | 2.1 | 0.01 | s1 | n | n | d0
|  | 78440 20343785 | 748697B | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G1.5 | 9.34 | 17 | Manlleu | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 37 | 22.9 | No | 2020-09-25 | D_s1_d1 | 2.68 | 27.2 | 41.2 | 1383 | 44.8 | D | 13.6 | 0.04 | s1 | y | n | d1
|  | 78441 20343786 | 748691V | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 10.36 | 14 | Manlleu | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 34 | 21.4 | No | 2020-09-25 | C_s1_d2 | 1.89 | 15.1 | 22 | 1122 | 35.3 | C | 15.9 | 0.04 | s1 | n | y | d2
20090015 |  | 18388 | -- | AFUMEX TECNUC -PK3PS794-PRYSMIAN 255-12P1.00MM²-CU CL5-BLG-LSOH-0.3/0.5(0.6)-CSTB 74.C.068-K3 | 23 | 7 | Paron | IX2100FR+SW3100FR | -- | 54.1 | 24.9 | No | 2020-09-30 | B2_s1_d0 | 0.45 | 4.2 | 9.8 | 1500 | 10 | B2 | 11 | 0.06 | s1 | n | n | d0
20090016 |  | 18388 | -- | AFUMEX TECNUC -PK3CZ014-PRYSMIAN 255-19*0.5MM²-CU CL2-BLG-LSOH-0.3/0.5(0.6)-3 011 330-CSTB 74.C.068-K3 | 15.5 | 9 | Paron | IX2100FR+SW3100FR | -- | 54.7 | 24.5 | No | 2020-09-30 | B2_s1_d0 | 0.45 | 5 | 8.8 | 1398 | 9 | B2 | 23 | 0.05 | s1 | n | n | d0
TN_2020_2362 |  | 784439 20343787 | 708825M | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G4 | 11.31 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 65.4 | 27.77 | No | 2020-10-01 | D_s1_d0 | 2.11 | 34.9 | 51.9 | 11.67 | 70.9 | D | 38.7 | 0.1 | s1 | n | n | d0
TN_2020_2363 |  | 74965 20316993 | 667287M | EXZHELLENT RZ1-K (AS) 1 KV 5G1.5 | 11.97 | 13 | Vilanova | SXLPE+0400FEIT+1602SEES | CD | 53.4 | 29.38 | No | 2020-10-01 | C_s1_d0 | 1.27 | 20.4 | 32 | 888 | 56.1 | C | 25.1 | 0.05 | s1 | n | n | d0
TN_2020_2364 |  | 78441 20343786 | 748691V | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 10.46 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 45.9 | 30.95 | No | 2020-10-01 | C_s1_d0 | 1.67 | 21 | 26.4 | 780 | 55.2 | C | 19.7 | 0.04 | s1 | n | n | d0
TN_2020_2365 |  | 78440 20343785 | 748697B | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G1.5 | 9.34 | 17 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 45.3 | 29.02 | No | 2020-10-01 | E ou F_s2_d2 | 3.2 | 82.7 | 233.3 | 1278 | 238.5 | E ou F | 123.7 | 0.44 | s2 | n | y | d2
TN_2020_2366 |  | 784439 20343787 | 708825M | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G4 | 11.31 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 52.2 | 26.33 | No | 2020-10-01 | C_s1_d0 | 0.88 | 15.5 | 24.4 | 861 | 43.8 | C | 23.3 | 0.05 | s1 | n | n | d0
TN_2020_2367 |  | 104 | 5096655 | DROP I_O ED5 1X1 DRY | 5.07 | 30 | Vilanova | PC/PE+AFUMEX1700SEIT | CD | 71.6 | 19.97 | No | 2020-10-02 | E ou F_s2_d0 | 3.3 | 35.3 | 275.1 | 510 | 1328.6 | E ou F | 70 | 0.31 | s2 | n | n | d0
TN_2020_2368 |  | 77436 60087613 | 5096757 | ACOMETIDA INTERIOR 1X2X0.50 | 3.8 | 90 | Vilanova | TPR-32+SKINTPR-53 | CD | 72.4 | 20.44 | No | 2020-10-02 | D_s2_d2 | 3.3 | 68.4 | 217 | 984 | 367.3 | D | 57 | 0.17 | s2 | n | y | d2
TN_2020_2369 |  | 78440 20343785 | 748697B | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G1.5 | 9.34 | 17 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 76.6 | 21.71 | No | 2020-10-02 | D_s1_d1 | 2.8 | 33.3 | 52.6 | 1491 | 67.2 | D | 40.5 | 0.11 | s1 | y | n | d1
TN_2020_2370 |  | 78441 20343786 | 748691V | EXZHELLENT COMPACT RZ1-K (AS) 1KV 3G2.5 | 10.46 | 14 | Vilanova | TPR+PAPEL+TPR-54VD+1%CALOXOL | CD | 76.8 | 21.79 | No | 2020-10-02 | D_s1_d1 | 2.07 | 30.8 | 43.7 | 1110 | 67.5 | D | 34.7 | 0.06 | s1 | y | n | d1
TN_2020_2371 |  | 105 | 5096656 | NEW DROP I_O 1X1 DRY | 5.1 | 30 | Vilanova | PC/PE+AFUMEX1700SEIT | CD | 73 | 21.06 | No | 2020-10-02 | D_s1_d0 | 3.3 | 24.7 | 86 | 543 | 453.9 | D | 28.4 | 0.12 | s1 | n | n | d0
20100001 |  | 18432 | 767110R | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10 | 15 | Paron | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.3+1.7 | -- | 58.9 | 20.1 | No | 2020-10-02 | D_s1_d2 | 2.5 | 34.7 | 52.5 | 906 | 87 | D | 36 | 0.06 | s1 | y | y | d2
20100002 |  | 18432 | 767088S | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.98 | 13 | Paron | PP+PAPEL+0.51420+16HATHICKNESSMEASURED:0.4+1.6 | -- | 58.5 | 21.4 | No | 2020-10-02 | D_s1_d2 | 2.1 | 33.1 | 47.4 | 1131 | 75 | D | 31 | 0.05 | s1 | y | y | d2
20100003 |  | 18432 | 767118Z | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.7 | 13 | Paron | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.4+1.6 | -- | 62.4 | 21.7 | No | 2020-10-02 | C_s1_d2 | 2 | 25.5 | 43.2 | 987 | 63 | C | 32 | 0.06 | s1 | y | y | d2
20100004 |  | 18432 | 767118Z | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.7 | 13 | Paron | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.4+1.6 | -- | 57.3 | 20.9 | No | 2020-10-03 | D_s1_d2 | 2.25 | 37.1 | 57.5 | 1227 | 76 | D | 39 | 0.08 | s1 | y | y | d2
20100005 |  | 18432 | 767088S | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.98 | 13 | Paron | PP+PAPEL+0.51420+16HATHICKNESSMEASURED:0.4+1.6 | -- | 52.7 | 20.6 | No | 2020-10-03 | D_s1_d2 | 2.03 | 32.9 | 47.7 | 1029 | 67 | D | 28 | 0.04 | s1 | y | y | d2
20100006 |  | 18432 | 767110R | AFUMEX CLASS RZ1-K (AS) 1KV 3G1.5 | 10 | 15 | Paron | PP+PAPEL+0.31420+16HATHICKNESSMEASURED:0.3+1.7 | -- | 52.2 | 20.8 | No | 2020-10-03 | D_s1_d2 | 2.3 | 35.5 | 55.6 | 981 | 90 | D | 33 | 0.05 | s1 | y | y | d2
TN_2020_2372 |  | 83887729 20217699 | 758006V | AFUMEX CLASS 1KV RZ1-K (AS) 1X185 | 22.74 | 7 | Vilanova | MESCLA16HC | CD | 31.8 | 27.12 | No | 2020-10-05 | B2_s1_d2 | 0.59 | 8.7 | 29.7 | 1500 | 24.7 | B2 | 2.2 | 0.02 | s1 | n | y | d2
TN_2020_2373 |  | 75353 20320359 | 782604G | XAZ1 1X300 CCA-S1B.D1.A1 (PROTO D) | 34.15 | 5 | Vilanova | INSULATIONPRS-03+TALCO+BEDDINGTPR-38+STEELTAPE30X0.20+LANTORTAPE3F905040MMID152/OD5 | CD | 31.4 | 26.53 | No | 2020-10-05 | C_s1_d2 | 0.87 | 15.2 | 26.4 | 1500 | 28.4 | C | 12.9 | 0.03 | s1 | n | y | d2
TN_2020_2374 |  | 83824421 | 754426D | LXHIOZ1 (CBE.FRT) 15KV 1X240/16 | 38.91 | 5 | Vilanova | 14201.3MM+61AA2.7MM | CD | 31.4 | 26.17 | No | 2020-10-05 | B2_s1_d1 | 0.83 | 13.4 | 18 | 888 | 42.1 | B2 | 10.2 | 0.03 | s1 | y | n | d1
TN_2020_2375 |  | 75352 20320360 | 782604G | XAZ1 1X300 CCA-S1B.D1.A1 (PROTO C) | 33.87 | 5 | Vilanova | INSULATIONPRS-03+TALCO+BEDDINGTPR-38+STEELTAPE30X0.20+SHEATHAFUMEX1602SEES | CD | 32.9 | 23.47 | No | 2020-10-05 | B2_s1_d2 | 0.73 | 14.3 | 22.8 | 1224 | 27.9 | B2 | 15.4 | 0.04 | s1 | n | y | d2
TN_2020_2376 |  | 106 | 5096654 | L1081 1X1 TIGHT | 2.12 | 330 | Vilanova | AFUMEX1700SEES | CD | 35.9 | 21.04 | No | 2020-10-05 | C_s1_d1 | 1.69 | 21.3 | 46.1 | 699 | 142.7 | C | 19.7 | 0.07 | s1 | y | n | d1
20100007 |  | 18420 | CE6756 A/ESS-881 | 1000-1X6MM²-SH-NF F55-625-255 | 8.3 | 19 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 56.8 | 21.7 | No | 2020-10-06 | B2_s1_d1 | 0.2 | 3 | 7.3 | 474 | 87 | B2 | 6 | 0.01 | s1 | y | n | d1
20100008 |  | 18420 | CE6756 B/ESS-1162 | 1000-1X6MM²-SH-NF F55-625-255 | 8.3 | 19 | Paron | IX1400+0400FEIT+5300SEIT | -- | 57.7 | 21.8 | No | 2020-10-06 | B2_s1_d2 | 0.9 | 10.1 | 24.2 | 705 | 71 | B2 | 19 | 0.05 | s1 | y | y | d2
TN_2020_2377 |  | 73193 20310305 | 736162B | RHZ1-2OL (AS) 12/20 KV 1X240 AL+H16 | 44.97 | 4 | Vilanova | XLPE+14202.5+61AA3.3 | CD | 42.1 | 27.8 | No | 2020-10-06 | C_s1_d1 | 0.73 | 15.1 | 21.2 | 918 | 48.7 | C | 16.7 | 0.05 | s1 | y | n | d1
TN_2020_2378 |  | 83775636 20339809 | 758223F | HEPRZ1 (AS) 45KV 1X150 AL+H25 | 44.8 | 4 | Vilanova | HEPR+1420FEES2.5+61AA3.5 | CD | 40 | 29.16 | No | 2020-10-06 | B2_s1_d0 | 0.65 | 13.4 | 18.6 | 1086 | 30.3 | B2 | 13 | 0.04 | s1 | n | n | d0
TN_2020_2379 |  |  | 779098W | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.18 | 13 | Vilanova | 1420FEES0.7MMMEASURED+1602SEES1.5MMMEASURED | CD | 59.6 | 21.22 | No | 2020-10-07 | D_s1_d2 | 2.56 | 39.7 | 59.9 | 1500 | 71.6 | D | 32.2 | 0.05 | s1 | n | y | d2
TN_2020_2380 |  |  | 774618B | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12 | 13 | Vilanova | 1420FEES0.5MMMEASURED+16HFSEES1.6MMMEASURED | CD | 55.7 | 22.11 | No | 2020-10-07 | D_s1_d2 | 1.99 | 31.6 | 42.7 | 1062 | 65.9 | D | 31.7 | 0.07 | s1 | n | y | d2
TN_2020_2381 |  |  | 772825C | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 11.28 | 14 | Vilanova | 1420FEES0.5MMMEASURED+16HASEES2.0MMMEASURED | CD | 52.3 | 23.94 | No | 2020-10-07 | B2_s1_d0 | 1.1 | 12.3 | 24.5 | 732 | 57 | B2 | 11.9 | 0.02 | s1 | n | n | d0
TN_2020_2382 |  |  | 774636W | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.35 | 15 | Vilanova | 1420FEES0.5MMMEASURED+16HFSEES1.5MMMEASURED | CD | 79.7 | 27 | No | 2020-10-07 | D_s1_d2 | 2.97 | 40.1 | 52.3 | 1002 | 104.4 | D | 42.5 | 0.07 | s1 | n | y | d2
TN_2020_2383 |  |  | 772819W | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.29 | 15 | Vilanova | 1420FEES0.6MMMEASURED+1602SEES1.6MMMEASURED | CD | 46.5 | 28.16 | No | 2020-10-07 | D_s1_d2 | 3.3 | 49 | 111.5 | 1497 | 93.2 | D | 27.5 | 0.09 | s1 | n | y | d2
TN_2020_2384 |  |  | 774627L | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 13.13 | 12 | Vilanova | 1420FEES0.7MMMEASURED+16HCSEES1.9MMMEASURED | CD | 64.8 | 24.93 | No | 2020-10-07 | C_s1_d1 | 1.12 | 19.5 | 28.4 | 942 | 46.3 | C | 13.2 | 0.03 | s1 | y | n | d1
TN_2020_2385 |  |  | 774624H | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.39 | 15 | Vilanova | 1420FEES0.6MMMEASURED+16HGSEES1.5MMMEASURED | CD | 63.7 | 24.63 | No | 2020-10-07 | C_s1_d0 | 1.19 | 15.5 | 23.9 | 1011 | 55.7 | C | 13.4 | 0.02 | s1 | n | n | d0
TN_2020_2386 |  |  | 774625J | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.56 | 14 | Vilanova | 1420FEES0.6MMMEASURED+16HCSEES1.6MMMEASURED | CD | 66.7 | 22.62 | No | 2020-10-07 | C_s1_d2 | 1.4 | 18.3 | 31.9 | 837 | 62.6 | C | 18.7 | 0.03 | s1 | n | y | d2
TN_2020_2387 |  |  | 772807H | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 13.5 | 11 | Vilanova | 1420FEES0.8MMMESURED+16HGSEES2MMMEASURED | CD | 65.9 | 22.89 | No | 2020-10-07 | B2_s1_d1 | 0.74 | 11.7 | 20.1 | 1038 | 33.6 | B2 | 12 | 0.04 | s1 | y | n | d1
TN_2020_2388 |  |  | 774604L | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.97 | 12 | Vilanova | 1420FEES0.6MMMEASURED+16HASSEES1.8MMMEASURED | CD | 66.5 | 21.84 | No | 2020-10-07 | C_s1_d2 | 0.84 | 15.5 | 24.2 | 900 | 41.7 | C | 12 | 0.02 | s1 | n | y | d2
TN_2020_2389 |  |  | 779111K | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.31 | 13 | Vilanova | 1420FEES0.9MMMEASURED+16HDSEES1.5MMMEASURED | CD | 61.9 | 27.61 | No | 2020-10-08 | C_s1_d2 | 1.5 | 24.9 | 36.1 | 957 | 59.7 | C | 21.7 | 0.04 | s1 | n | y | d2
TN_2020_2390 |  |  | 774622F | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.81 | 14 | Vilanova | 1420FEES0.6MMMEASURED+16HDSEES1.8MMMEASURED | CD | 61 | 27.95 | No | 2020-10-08 | C_s1_d1 | 1.18 | 15.3 | 30.5 | 783 | 65.1 | C | 23.9 | 0.05 | s1 | y | n | d1
TN_2020_2391 |  |  | 774636W | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.35 | 15 | Vilanova | 1420FEES0.5MMMEASURED+16HFSEES1.5MMMEASURED | CD | 60.9 | 28.16 | No | 2020-10-08 | D_s1_d1 | 3.3 | 41.5 | 52.9 | 957 | 100.2 | D | 30.5 | 0.05 | s1 | y | n | d1
TN_2020_2392 |  |  | 779098W | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.18 | 13 | Vilanova | 1420FEES0.7MMMEASURED+1602SEES1.5MMMEASURED | CD | 62.7 | 24.88 | No | 2020-10-08 | D_s1_d2 | 3.3 | 59.9 | 133.5 | 1497 | 112.8 | D | 33.4 | 0.08 | s1 | n | y | d2
TN_2020_2393 |  |  | 774618B | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12 | 13 | Vilanova | 1420FEES0.5MMMEASURED+16HFSEES1.6MMMEASURED | CD | 65.3 | 23.32 | No | 2020-10-08 | D_s1_d2 | 2.22 | 38.2 | 53.9 | 1062 | 75 | D | 14.7 | 0.04 | s1 | n | y | d2
TN_2020_2394 |  |  | 772819W | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.29 | 15 | Vilanova | 1420FEES0.6MMMEASURED+1602SEES1.6MMMEASURED | CD | 75.8 | 20.43 | No | 2020-10-09 | D_s1_d2 | 2.62 | 40.3 | 50.7 | 1110 | 84.9 | D | 27.2 | 0.05 | s1 | n | y | d2
TN_2020_2395 |  |  | 772825C | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 11.28 | 14 | Vilanova | 1420FEES0.5MMMEASURED+16HASEES2.0MMMEASURED | CD | 73.7 | 20.41 | No | 2020-10-09 | C_s1_d0 | 1.11 | 16 | 27.3 | 732 | 65.7 | C | 18 | 0.03 | s1 | n | n | d0
TN_2020_2396 |  |  | 774604L | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.97 | 12 | Vilanova | 1420FEES0.6MMMEASURED+16HASSEES1.8MMMEASURED | CD | 74.2 | 21.97 | No | 2020-10-09 | C_s1_d2 | 1.7 | 11.6 | 18.8 | 807 | 40.7 | C | 15.8 | 0.03 | s1 | n | y | d2
TN_2020_2397 |  |  | 774627L | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 13.13 | 12 | Vilanova | 1420FEES0.7MMMEASURED+16HCSEES1.9MMMEASURED | CD | 73.9 | 23.34 | No | 2020-10-09 | C_s1_d2 | 1.15 | 16.6 | 25.9 | 816 | 51.2 | C | 20.5 | 0.04 | s1 | n | y | d2
TN_2020_2398 |  |  | 774625J | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.56 | 14 | Vilanova | 1420FEES0.6MMMEASURED+16HCSEES1.6MMMEASURED | CD | 72.5 | 24.97 | No | 2020-10-09 | B2_s1_d1 | 0.7 | 9.8 | 22.4 | 741 | 54 | B2 | 9.8 | 0.02 | s1 | y | n | d1
TN_2020_2399 |  |  | 774624H | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.39 | 15 | Vilanova | 1420FEES0.6MMMEASURED+16HGSEES1.5MMMEASURED | CD | 61.1 | 21.1 | No | 2020-10-11 | D_s1_d1 | 1.54 | 32.2 | 48.2 | 849 | 94.6 | D | 30.6 | 0.05 | s1 | y | n | d1
TN_2020_2400 |  |  | 774622F | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.81 | 14 | Vilanova | 1420FEES0.6MMMEASURED+16HDSEES1.8MMMEASURED | CD | 51.4 | 25.33 | No | 2020-10-11 | C_s1_d0 | 0.99 | 15.2 | 27.7 | 798 | 55.5 | C | 18.7 | 0.05 | s1 | n | n | d0
20100010 |  | 18421 | CE6740B | VS6 K20-75 OHMS-PESS1152 | 6.2 | 25 | Paron | 5300SEIT | -- | 55.1 | 22 | No | 2020-10-09 | D_s1_d1 | 3.3 | 43.5 | 211.8 | 711 | 521 | D | 47 | 0.18 | s1 | y | n | d1
20100011 |  | 18421 | CE6740D | VS6 K20-75 OHMS-PESS1154 | 5.94 | 25 | Paron | 1602SEES | -- | 63.4 | 21.5 | No | 2020-10-09 | D_s2_d2 | 3.3 | 44.9 | 246 | 705 | 615 | D | 53 | 0.22 | s2 | y | y | d2
TN_2020_2401 |  |  | 772807H | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 13.5 | 11 | Vilanova | 1420FEES0.8MMMESURED+16HGSEES2MMMEASURED | CD | 47.1 | 14.11 | No | 2020-10-12 | C_s1_d2 | 0.71 | 16.7 | 26.9 | 753 | 61.7 | C | 5.5 | 0.02 | s1 | n | y | d2
TN_2020_2402 |  |  | 779111K | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.31 | 13 | Vilanova | 1420FEES0.9MMMEASURED+16HDSEES1.5MMMEASURED | CD | 47.6 | 14.39 | No | 2020-10-12 | D_s1_d2 | 1.41 | 30.4 | 43.8 | 1119 | 65.2 | D | 11.8 | 0.05 | s1 | n | y | d2
TN_2020_2403 |  |  | 403686P | ASCABLE RECAEL RZ1-K (AS) 1 KV 1X240 | 27.17 | 6 | Vilanova | COMPETITORSAMPLE | CD | 47.4 | 16.6 | No | 2020-10-12 | C_s1_d2 | 1.21 | 28.2 | 47.5 | 1254 | 50.6 | C | 5.1 | 0.03 | s1 | n | y | d2
TN_2020_2404 |  |  | 5096640 | ASCABLE RECAEL RZ1-K (AS) 1 KV 3G1.5 | 11.21 | 14 | Vilanova | COMPETITORSAMPLE | CD | 42.8 | 21.52 | No | 2020-10-12 | C_s1_d0 | 1.53 | 20.4 | 29.2 | 897 | 70 | C | 39.5 | 0.06 | s1 | n | n | d0
TN_2020_2405 |  |  | 5096642 | ASCABLE RECAEL RZ1-K (AS) 1 KV 5G1.5 | 12.95 | 12 | Vilanova | COMPETITORSAMPLE | CD | 35.2 | 25.25 | No | 2020-10-12 | D_s2_d2 | 1.73 | 32.6 | 45.1 | 1101 | 74 | D | 60.2 | 0.1 | s2 | n | y | d2
TN_2020_2406 |  |  | 5096787 | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 3G1.5MM2 | 10.35 | 15 | Vilanova | COMPETITORSAMPLE | CD | 66.2 | 15.31 | No | 2020-10-14 | D_s1_d2 | 2.53 | 43.2 | 52.1 | 993 | 110 | D | 36 | 0.07 | s1 | n | y | d2
TN_2020_2407 |  |  | 5096788 | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 5G1.5 | 12.43 | 13 | Vilanova | COMPETITORSAMPLE | CD | 65.5 | 14.82 | No | 2020-10-14 | C_s1_d0 | 1.03 | 21.8 | 29 | 948 | 76.1 | C | 20.2 | 0.04 | s1 | n | n | d0
TN_2020_2408 |  |  | 5096636 | ASCABLE RECAEL RZ1-K (AS) 1 KV 1X16 | 12.11 | 13 | Vilanova | COMPETITORSAMPLE | CD | 63.9 | 15.91 | No | 2020-10-14 | C_s1_d0 | 1.11 | 20.9 | 30 | 954 | 58.8 | C | 36.2 | 0.08 | s1 | n | n | d0
TN_2020_2409 |  |  | 080652K | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 1X240 | 26.89 | 6 | Vilanova | COMPETITORSAMPLE | CD | 59.7 | 20.34 | No | 2020-10-14 | C_s1_d2 | 1.87 | 18.1 | 51.3 | 1440 | 45 | C | 26.2 | 0.07 | s1 | n | y | d2
TN_2020_2410 |  |  | 5096786 | AENOR MIGUELEZ AFIRENAS X RZ1-K (AS) 1KV 1X16 | 9.62 | 15 | Vilanova | COMPETITORSAMPLE | CD | 52.1 | 23.37 | No | 2020-10-14 | B2_s1_d1 | 0.89 | 9.5 | 18.9 | 801 | 45.8 | B2 | 21.1 | 0.03 | s1 | y | n | d1
20100012 |  | 18440 | ES409A | ES409A 16X1MM² | 26 | 6 | Paron | ID26AB+CFR+5300SEIT | -- | 47.2 | 21.2 | No | 2020-10-13 | C_s1_d2 | 0.98 | 16.5 | 29.8 | 1248 | 43 | C | 21 | 0.04 | s1 | y | y | d2
20100013 |  | 18440 | ES409A | ES409A 8X1MM² | 22 | 7 | Paron | ID26AB+CFR+5300SEIT | -- | 47.3 | 21 | No | 2020-10-13 | B2_s1_d2 | 0.8 | 12.4 | 27.7 | 1320 | 27 | B2 | 22 | 0.1 | s1 | y | y | d2
20100014 |  | 18440 | ES409A | ES409A 16X1MM² | 26.2 | 7 | Paron | ID26AB+CFR+COGEGUMGFR/380 | -- | 49.1 | 20.8 | No | 2020-10-13 | B2_s1_d2 | 0.9 | 10.9 | 25.9 | 1338 | 25 | B2 | 23 | 0.06 | s1 | y | y | d2
20100015 |  | 18440 | ES409A | ES409A 8X1MM² | 22 | 7 | Paron | ID26AB+CFR+COGEGUMGFR/380 | -- | 52.9 | 20.9 | No | 2020-10-13 | B2_s1_d2 | 0.6 | 9.2 | 17.6 | 1086 | 22 | B2 | 34 | 0.12 | s1 | y | y | d2
TN_2020_2411 |  |  | 5096784 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 5G1.5 | 12.66 | 12 | Vilanova | COMPETITORSAMPLE | CD | 52.2 | 11.93 | No | 2020-10-15 | C_s1_d0 | 1.02 | 16.9 | 25.4 | 822 | 48.7 | C | 25.4 | 0.04 | s1 | n | n | d0
TN_2020_2412 |  | 78194 20300592 | 786482X | EPR/PVC FRRT 3.8/6.6KV 400MM2 | 37.93 | 5 | Vilanova | ID7140IT+CUTAPE+PVCFKN931B | CD | 53.2 | 12.05 | No | 2020-10-15 | B2_s2_d1 | 0.7 | 10.8 | 19.2 | 1500 | 56.3 | B2 | 316.2 | 0.76 | s2 | y | n | d1
TN_2020_2413 |  |  | 5096775 | MIGUELEZ AFIRENAS H07Z1-K 1.5MM2 AZ | 2.91 | 165 | Vilanova | COMPETITORSAMPLE | CD | 50.4 | 15.47 | No | 2020-10-15 | B2_s1_d1 | 1.32 | 13.6 | 25.6 | 672 | 68.9 | B2 | 46.5 | 0.11 | s1 | y | n | d1
TN_2020_2414 |  |  | 5096776 | MIGUELEZ AFIRENAS H07Z1-K 2.5MM2 AZ | 3.67 | 105 | Vilanova | COMPETITORSAMPLE | CD | 45.7 | 19.44 | No | 2020-10-15 | B2_s1_d1 | 1.29 | 12.4 | 25.7 | 732 | 81.2 | B2 | 37.1 | 0.12 | s1 | y | n | d1
TN_2020_2415 |  |  | 5096649 | ASCABLE-RECAEL HO7Z1-K (AS) TYPE2 AENOR (HAR) 1X1.5 | 2.93 | 165 | Vilanova | COMPETITORSAMPLE | CD | 39.9 | 22.92 | No | 2020-10-15 | D_s2_d1 | 2.71 | 28 | 50 | 768 | 109.9 | D | 63.2 | 0.12 | s2 | y | n | d1
TN_2020_2416 |  |  | 5096783 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 1X240 | 27.1 | 6 | Vilanova | COMPETITORSAMPLE | CD | 32.3 | 25.79 | No | 2020-01-15 | B2_s1_d0 | 0.14 | 4.4 | 5.5 | 663 | 18.1 | B2 | 2.3 | 0.01 | s1 | n | n | d0
TN_2020_2417 |  |  | 5096785 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 3G1.5 | 10.51 | 14 | Vilanova | COMPETITORSAMPLE | CD | 29.2 | 24.6 | No | 2020-10-15 | C_s1_d0 | 1.12 | 15.5 | 26.8 | 762 | 73.4 | C | 23.6 | 0.05 | s1 | n | n | d0
TN_2020_2418 |  |  | 5096660 | TOP CABLE TOXFREE ZH RZ1-K (AS) 1KV 1X16 | 10.21 | 15 | Vilanova | COMPETITORSAMPLE | CD | 27.4 | 24.73 | No | 2020-10-15 | B2_s1_d0 | 0.72 | 8.3 | 19 | 795 | 41.6 | B2 | 14.2 | 0.04 | s1 | n | n | d0
TN_2020_2419 |  |  | 5096648 | ASCABLE-RECAEL HO7Z1-K (AS) TYPE2 AENOR (HAR) 1X2.5 | 3.5 | 120 | Vilanova | COMPETITORSAMPLE | CD | 28.2 | 21.52 | No | 2020-10-15 | C_s1_d1 | 1.64 | 16.3 | 31.3 | 741 | 81.1 | C | 27.3 | 0.08 | s1 | y | n | d1
TN_2020_2420 |  |  | 5096658 | TOP CABLE TOXFREE ZH H07Z1-K (AS) TYPE 2 1.5 MM2 AZ | 2.93 | 293 | Vilanova | COMPETITORSAMPLE | CD | 29.2 | 19.45 | No | 2020-10-15 | D_s1_d0 | 2.12 | 20.7 | 37.3 | 726 | 117.8 | D | 24.2 | 0.04 | s1 | n | n | d0
TN_2020_2421 |  | 20049222 | OF864 | RED ELEC RHZ1-RA+2OL (AS) 1X2000MM2 127/220KV+H315 | 129.5 | 2 | Vilanova | 6000SEES+SKINSC | CD | 46.9 | 15.47 | No | 2020-10-16 | C_s1_d2 | 1.97 | 21.9 | 29.1 | 1500 | 61.9 | C | 26.9 | 0.05 | s1 | n | y | d2
TN_2020_2422 |  |  | 5096659 | TOP CABLE TOXFREE ZH H07Z1-K (AS) TYPE 2 2.5MM2 AZ | 3.57 | 105 | Vilanova | COMPETITORSAMPLE | CD | 50.2 | 12.96 | No | 17/10/1020 | B2_s1_d1 | 1.14 | 10.4 | 26.4 | 624 | 84.8 | B2 | 13.7 | 0.05 | s1 | y | n | d1
TN_2020_2423 |  |  | 06-63989 | REVI ECOCLASS RZ1-K (AS) 1KV 1X240 | 27.86 | 6 | Vilanova | COMPETITORSAMPLE | CD | 50.1 | 13.09 | No | 17/10/1020 | B2_s1_d2 | 0.53 | 10.3 | 17.1 | 1479 | 25 | B2 | 4.3 | 0.01 | s1 | n | y | d2
TN_2020_2424 |  |  | 5096791 | REVI ECOCLASS RZ1-K (AS) 1KV 5G1.5 | 11.52 | 13 | Vilanova | COMPETITORSAMPLE | CD | 50.5 | 15.56 | No | 17/10/1020 | B2_s1_d0 | 1.05 | 13.3 | 20.8 | 822 | 45 | B2 | 36.5 | 0.11 | s1 | n | n | d0
TN_2020_2425 |  |  | 5096792 | REVI ECOCLASS RZ1-K (AS) 1KV 3G1.5 | 9.69 | 15 | Vilanova | COMPETITORSAMPLE | CD | 49.2 | 21.27 | No | 17/10/1020 | C_s1_d0 | 1.71 | 18 | 26.3 | 993 | 66.1 | C | 42 | 0.08 | s1 | n | n | d0
TN_2020_2426 |  |  | 5096793 | REVI ECOCLASS RZ1-K (AS) 1KV 1X16 | 9.92 | 15 | Vilanova | COMPETITORSAMPLE | CD | 48.9 | 23.45 | No | 2020-10-17 | B2_s1_d2 | 0.89 | 9.8 | 19.5 | 813 | 64.9 | B2 | 8.7 | 0.03 | s1 | n | y | d2
20100016 |  | 18454 | -- | AFUMEX TECNUC-PESS 1103-PRYSMIAN 255-62 C 0.22MM² -CUET-BG-LSOH-0.15/0.25(0.3) | 14.7 | 10 | Paron | PEEKKESTASPIRE | -- | 38 | 20.3 | No | 2020-10-19 | B2_s1_d2 | 0.6 | 6.8 | 15.4 | 927 | 30 | B2 | 35 | 0.11 | s1 | y | y | d2
20100017 |  | 18447 | 774634U | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10 | 15 | Paron | SXLPE+1420FEES+16HCSEES | -- | 39.6 | 20 | No | 2020-10-19 | C_s1_d2 | 1.4 | 16.8 | 30.4 | 897 | 66 | C | 22 | 0.03 | s1 | y | y | d2
20100018 |  | 18447 | 779096U | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.4 | 15 | Paron | SXLPE+1420FEES+16HGSEES | -- | 42.8 | 19.8 | No | 2020-10-19 | D_s1_d2 | 2 | 31.6 | 46 | 933 | 74 | D | 25 | 0.04 | s1 | y | y | d2
20100019 |  | 18447 | 774620D | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.6 | 12 | Paron | SXLPE+1420FEES+16HFSEES | -- | 46.2 | 21 | No | 2020-10-19 | D_s1_d2 | 2.3 | 38.3 | 51.3 | 1131 | 77 | D | 40 | 0.09 | s1 | y | y | d2
20100020 |  | 18447 | 779102A | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.4 | 13 | Paron | SXLPE+1420FEES+16HASEES | -- | 38.5 | 21.4 | No | 2020-10-19 | C_s1_d2 | 1.4 | 22.2 | 32.5 | 1047 | 52 | C | 24 | 0.04 | s1 | y | y | d2
TN_2020_2427 |  |  | 5096669 | 7.F/UTP5E EOLO CCA PROTO E (0.85) | 7.65 | 19 | Vilanova | BAINHADUBLATPR-32+CONGUARDS66500.85 | CD | 74.5 | 19 | No | 2020-10-20 | B2_s1_d2 | 1.31 | 12.2 | 29.2 | 600 | 99.1 | B2 | 12 | 0.04 | s1 | n | y | d2
TN_2020_2428 |  |  | 5096668 | 7.F/UTP5E EOLO CCA PROTO D (0.75) | 7.66 | 19 | Vilanova | BAINHADUBLATPR-32+CONGUARDS66500.75 | CD | 73.9 | 19.26 | No | 2020-10-20 | B2_s1_d0 | 0.52 | 5.1 | 15.8 | 474 | 91 | B2 | 21.5 | 0.05 | s1 | n | n | d0
TN_2020_2429 |  |  | 5096779 | ALSECURE NEXANS H07Z1-K 2.5MM2 AZ | 3.58 | 105 | Vilanova | COMPETITORSAMPLE | CD | 71.4 | 21.15 | No | 2020-10-20 | C_s1_d0 | 1.6 | 13.3 | 29.3 | 651 | 102 | C | 41.4 | 0.06 | s1 | n | n | d0
TN_2020_2430 |  |  | 5096790 | REVI ECOCLASS 1X2.5 H07Z1-K (AS) TYPE2 AENOR HAR 750V | 3.52 | 105 | Vilanova | COMPETITORSAMPLE | CD | 68.3 | 21.79 | No | 2020-10-20 | B2_s1_d0 | 1.43 | 11.1 | 23.8 | 669 | 71.3 | B2 | 29.2 | 0.07 | s1 | n | n | d0
TN_2020_2431 |  |  | 5096778 | ALSECURE NEXANS H07Z1-K 1.5MM2 AZ | 2.88 | 165 | Vilanova | COMPETITORSAMPLE | CD | 63.7 | 23.8 | No | 2020-10-20 | B2_s1_d0 | 1.18 | 12.3 | 26.9 | 669 | 94.9 | B2 | 34.7 | 0.1 | s1 | n | n | d0
TN_2020_2432 |  |  | 5096781 | NEXANS AL SECURE RZ1-K (AS) 1KV 3G1.5 | 10.59 | 14 | Vilanova | COMPETITORSAMPLE | CD | 69.8 | 20.92 | No | 2020-10-20 | D_s2_d2 | 3.2 | 62.2 | 147 | 1242 | 156 | D | 64.2 | 0.2 | s2 | n | y | d2
TN_2020_2433 |  |  | 5096789 | REVI ECOCLASS 1X1.5 H07Z1-K (AS) TYPE2 AENOR HAR 750V | 2.95 | 165 | Vilanova | COMPETITORSAMPLE | CD | 71.4 | 21.29 | No | 2020-10-20 | C_s1_d0 | 1.52 | 16.9 | 31.6 | 798 | 83.9 | C | 28.3 | 0.06 | s1 | n | n | d0
TN_2020_2434 |  |  | 5096782 | NEXANS AL SECURE RZ1-K (AS) 1KV 1X16 | 10.13 | 15 | Vilanova | COMPETITORSAMPLE | CD | 76.9 | 20.29 | No | 2020-10-21 | C_s1_d1 | 1.55 | 18.8 | 30.6 | 831 | 63.9 | C | 48.2 | 0.14 | s1 | y | n | d1
TN_2020_2435 |  |  | 5096780 | NEXANS AL SECURE RZ1-K (AS) 1KV 5G1.5 | 12.32 | 13 | Vilanova | COMPETITORSAMPLE | CD | 74.1 | 20.89 | No | 2020-10-21 | D_s1_d0 | 1.9 | 30.3 | 43.7 | 1044 | 81.5 | D | 33 | 0.05 | s1 | n | n | d0
TN_2020_2436 |  |  | 5096777 | NEXANS AL SECURE RZ1-K (AS) 1KV 1X240 | 27.67 | 6 | Vilanova | COMPETITORSAMPLE | CD | 70.2 | 21.65 | No | 2020-10-21 | D_s1_d2 | 2.9 | 36.7 | 134.7 | 1497 | 112.5 | D | 23.4 | 0.09 | s1 | n | y | d2
TN_2020_2438 |  |  | 5096667 | 4.F/UTP6 CCA PROTO E (0.55) | 7.6 | 19 | Vilanova | BAINHACONGUARDS66500.65 | CD | 76.8 | 19.56 | No | 2020-10-22 | C_s1_d1 | 0.68 | 5.9 | 26.5 | 510 | 152.7 | C | 19 | 0.1 | s1 | y | n | d1
TN_2020_2439 |  |  | 5096666 | 4.F/UTP6 CCA PROTO D (0.55) | 7.03 | 21 | Vilanova | BAINHACONGUARDS66500.55 | CD | 76 | 19.62 | No | 2020-10-22 | B2_s1_d1 | 0.95 | 6.1 | 25 | 498 | 129.7 | B2 | 25.1 | 0.1 | s1 | y | n | d1
TN_2020_2440 |  |  | 5096670 | 4.F/UTP6 CCA PROTO G (0.55) | 7.31 | 21 | Vilanova | BAINHAS5330.55 | CD | 73.6 | 19.72 | No | 2020-10-22 | D_s2_d1 | 2.13 | 16.6 | 43.2 | 639 | 162.2 | D | 53.8 | 0.11 | s2 | y | n | d1
TN_2020_2441 |  |  | 5096671 | 4.F/UTP6 CCA PROTO H (0.65) | 7.53 | 19 | Vilanova | BAINHAS5330.65 | CD | 70.1 | 20.96 | No | 2020-10-22 | B2_s1_d0 | 0.78 | 7.4 | 23.6 | 552 | 118.4 | B2 | 23.8 | 0.06 | s1 | n | n | d0
TN_2020_2442 |  | 20193682 83805798 | 782207A | AFUMEX CLASS 1KV RZ1-K (AS) 5G16MM2 | 21.69 | 7 | Vilanova | 14200.2MMMEASURED+16022.14MMMEASUREDREPLÈ0.25 | CD | 80.2 | 18.32 | No | 2020-10-23 | B2_s1_d0 | 0.44 | 6.5 | 7.3 | 705 | 30.3 | B2 | 3.8 | 0.01 | s1 | n | n | d0
TN_2020_2443 |  | 20193682 83805798 | 782169J | AFUMEX CLASS 1KV RZ1-K (AS) 5G16MM2 | 22.06 | 7 | Vilanova | 14200.34MMMEASURED+16022.10MMMEASUREDREPLÈ0.55 | CD | 78.4 | 18.03 | No | 2020-10-23 | B2_s1_d1 | 0.51 | 7.6 | 8.6 | 1470 | 27 | B2 | 6.5 | 0.01 | s1 | y | n | d1
TN_2020_2444 |  | 20193682 | 764423V | AFUMEX CLASS 1KV RZ1-K (AS) 5G16MM2 | 22.17 | 7 | Vilanova | 14200.20MMMEASURED+16022.28MMMEASURED | CD | 79.3 | 19.34 | No | 2020-10-23 | C_s1_d2 | 1.11 | 21.8 | 50.9 | 1410 | 45.9 | C | 18.2 | 0.05 | s1 | n | y | d2
TN_2020_2445 |  |  | NTO64616 | Z1OZ1MZ1-K 500V 4X2X0.5 | 14.9 | 10 | Vilanova | COMPETITORSAMPLE | CD | 66.6 | 27.01 | No | 2020-10-23 | B2_s1_d2 | 0.81 | 10.7 | 18.6 | 1074 | 35.6 | B2 | 10.2 | 0.03 | s1 | n | y | d2
20100021 |  | 18456 |  | AFUMEX TECNUC -PK3HC006-PRYSMIAN 255-1*70 CU CL 2 | 28.6 | 6 | Paron |  | -- | 51.8 | 25.9 | No | 2020-10-23 | B2_s1_d1 | 0.5 | 8.2 | 13.2 | 1500 | 26 | B2 | 11 | 0.05 | s1 | y | n | d1
20100022 |  | 18447 | 779093R | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.3 | 15 | Paron | SXLPE+1420FEES+16HFSEES | -- | 54.5 | 25.1 | No | 2020-10-23 | D_s1_d2 | 3.3 | 62.8 | 116.2 | 1500 | 116 | D | 40 | 0.23 | s1 | y | y | d2
20100023 |  | 18447 | 772811M | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 11.31 | 14 | Paron | SXLPE+1420FEES+1602SEES | -- | 55.5 | 24.8 | No | 2020-10-23 | D_s1_d2 | 3 | 45.9 | 65.9 | 1500 | 84 | D | 30 | 0.05 | s1 | y | y | d2
TN_2020_2446 |  |  | 5096631 | RZ1MZ1H-K 0.6/1KV 4X2.5 | 17.97 | 8 | Vilanova | COMPETITORSAMPLE | CD | 48.3 | 15.99 | No | 2020-10-26 | B2_s1_d1 | 0.33 | 6.2 | 8.3 | 1329 | 25 | B2 | 8.5 | 0.02 | s1 | y | n | d1
TN_2020_2447 |  | 20316601 78111 | 787825G | HEPRHZ1-2OL B2CA 10KV 1X300 | 44.33 | 5 | Vilanova | HEPR+0400FEIT+TPR37 | CD | 42.6 | 19.7 | No | 2020-10-26 | B2_s1_d0 | 0.46 | 6.1 | 8.8 | 693 | 25.3 | B2 | 6.7 | 0.01 | s1 | n | n | d0
TN_2020_2448 |  |  | (06-3803) | RZ1MZ1H-K 0.6/1KV 4X10 | 22.33 | 7 | Vilanova | COMPETITORSAMPLE | CD | 41.4 | 21.37 | No | 2020-10-26 | B2_s1_d1 | 0.7 | 9.6 | 17.7 | 1398 | 41.9 | B2 | 14.2 | 0.05 | s1 | y | n | d1
TN_2020_2449 |  |  | 06-1381 | Z1OZ1MZ1-K 500V 6X2X1.5 | 20.09 | 8 | Vilanova | COMPETITORSAMPLE | CD | 39 | 23.84 | No | 2020-10-26 | C_s1_d2 | 0.86 | 18.7 | 27.8 | 1122 | 35.4 | C | 21.1 | 0.04 | s1 | n | y | d2
20100024 |  | 18447 | 774626K | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 11.06 | 14 | Paron | SXLPE+1420FEES+16HASEES | -- | 43.8 | 22.2 | No | 2020-10-26 | D_s1_d2 | 2.1 | 33.7 | 52.1 | 873 | 93 | D | 27 | 0.04 | s1 | y | y | d2
20100025 |  | 18447 | 779091N | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.9 | 14 | Paron | SXLPE+1420FEES+16HDSEES | -- | 43.8 | 22.1 | No | 2020-10-26 | B2_s1_d1 | 0.9 | 14.4 | 25.5 | 768 | 56 | B2 | 20 | 0.04 | s1 | y | n | d1
20100026 |  | 18447 | 772827E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.18 | 13 | Paron | SXLPE+1420FEES+16HDSEES | -- | 42 | 21.1 | No | 2020-10-26 | C_s1_d2 | 1.9 | 29.1 | 47.1 | 993 | 70 | C | 30 | 0.04 | s1 | y | y | d2
20100027 |  | 18447 | 774619C | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.11 | 13 | Paron | SXLPE+1420FEES+16HCSEES | -- | 42.1 | 22.3 | No | 2020-10-26 | C_s1_d2 | 1.4 | 22.5 | 34.1 | 1089 | 54 | C | 24 | 0.04 | s1 | y | y | d2
TN_2020_2454 |  | 20319525 74532 | 657656U | MRZ1FA3Z1-K(AS+) B2CA 1KV 5G6MM2 | 22.5 | 7 | Vilanova | 1602SEES | CD | 45.5 | 14.9 | No | 2020-10-27 | B2_s1_d2 | 0.39 | 8.7 | 11.7 | 1500 | 32 | B2 | 6.6 | 0.02 | s1 | n | y | d2
TN_2020_2455 |  | 20310896 73261 | 657684Z | MRZ1FA3Z1-K(AS+) B2CA 1KV 1X240MM2 | 34.29 | 5 | Vilanova | 1602SEES | CD | 46.6 | 14.72 | No | 2020-10-27 | B2_s1_d0 | 0.57 | 8.4 | 9.6 | 984 | 28.2 | B2 | 4.7 | 0.01 | s1 | n | n | d0
TN_2020_2456 |  | 20319524 74531 | 657688D | MRZ1FA3Z1-K(AS+) B2CA 1KV 5G1.5MM2 | 17.34 | 9 | Vilanova | 1602SEES | CD | 44 | 18.88 | No | 2020-10-27 | C_s1_d2 | 0.86 | 16.2 | 34.3 | 1218 | 37.3 | C | 28.5 | 0.07 | s1 | n | y | d2
TN_2020_2457 |  | 203194389 79666 | 796840F | AFUMEX CLASS 750V H07Z1-K (AS) 1X35 | 9.81 | 15 | Vilanova | TPR56 | CD | 41.2 | 22.56 | No | 2020-10-27 | B2_s1_d0 | 0.28 | 2.2 | 5.4 | 528 | 25.1 | B2 | 5.5 | 0.01 | s1 | n | n | d0
TN_2020_2458 |  | 20328397 76633 | 796844K | AFUMEX CLASS 750V H07Z1-K (AS) 1X240 | 23.25 | 7 | Vilanova | TPR56 | CD | 37.9 | 25.03 | No | 2020-10-27 | B2_s1_d0 | 0.29 | 3.2 | 5.5 | 504 | 23.4 | B2 | 0.6 | 0 | s1 | n | n | d0
20100028 |  | 18447 | 774610T | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 13.04 | 12 | Paron | SXLPE+1420FEES+16HGSEES | -- | 39.8 | 23.3 | No | 2020-10-27 | C_s1_d2 | 1.4 | 23.2 | 35.9 | 1077 | 56 | C | 21 | 0.03 | s1 | y | y | d2
20100029 |  | 18447 | 774619C | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.11 | 13 | Paron | SXLPE+1420FEES+16HCSEES | -- | 41.8 | 23 | No | 2020-10-27 | E ou F_s1_d2 | 3.3 | 74.7 | 167.4 | 1500 | 141 | E ou F | 48 | 0.22 | s1 | y | y | d2
20100030 |  | 18452 | FBM 216479 | 1800-S-1X400MM²-SH-NF F 55-625-255 | 38.6 | 5 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 43.3 | 22.4 | No | 2020-10-27 | B2_s1_d1 | 0.5 | 3.4 | 4.2 | 657 | 12 | B2 | 5 | 0.01 | s1 | y | n | d1
TN_2020_2463 |  | 20341607 78239 | 775830U | AFUMEX HEPRHZ1-2OL B2CA 10KV 1X300 | 43.43 | 5 | Vilanova | HEPR+61AASEES | CD | 49.6 | 15.26 | No | 2020-10-28 | B2_s1_d0 | 0.48 | 10.4 | 15.6 | 723 | 43.9 | B2 | 6 | 0.02 | s1 | n | n | d0
TN_2020_2464 |  | 20340564 78006 | 775814B | AFUMEX HEPRHZ1-2OL B2CA 10KV 1X300 | 44.92 | 4 | Vilanova | HEPR+0400FEES+TPO03 | CD | 51.1 | 18.82 | No | 2020-10-28 | B2_s1_d0 | 0.8 | 13.4 | 19.9 | 774 | 54.3 | B2 | 20.7 | 0.03 | s1 | n | n | d0
TN_2020_2465 |  | 20348075 79338 | 795124R | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 11 | 14 | Vilanova | TPR-54 | CD | 47.2 | 22.46 | No | 2020-10-28 | D_s2_d2 | 2.44 | 34.6 | 58.3 | 1767 | 69.8 | D | 65.7 | 0.12 | s2 | n | y | d2
TN_2020_2466 |  | 20316601 78111 | 787825G | HEPRHZ1-2OL B2CA 10KV 1X300 | 44.33 | 5 | Vilanova | HEPR+0400FEIT+TPR37 | CD | 64.9 | 15.61 | No | 2020-10-29 | B2_s1_d0 | 0.49 | 6 | 8.6 | 720 | 28.5 | B2 | 10.4 | 0.02 | s1 | n | n | d0
TN_2020_2467 |  | 20316324 79519 | 725473H | XHIOZ1 (CBE. FRT) 1X500/16 15KV | 49.76 | 4 | Vilanova | XLPE+1420FEES1.9MM+61AASEES2.1MM | CD | 64.2 | 22.14 | No | 2020-10-29 | B2_s1_d0 | 0.69 | 12.5 | 16.3 | 771 | 42.6 | B2 | 20.9 | 0.04 | s1 | n | n | d0
TN_2020_2468 |  | 20340563 78007 | 707007L | AFUMEX HEPRHZ1-2OL B2CA 10KV 1X150 | 37.62 | 5 | Vilanova | HEPR+0400FEIT+TPO03 | CD | 62.5 | 25.12 | No | 2020-10-29 | B2_s1_d0 | 0.74 | 14 | 23.4 | 756 | 69.9 | B2 | 15.9 | 0.04 | s1 | n | n | d0
TN_2020_2469 |  | 79336 20343748 | 795123P | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 10.52 | 14 | Vilanova | TPR-54 | CD | 55 | 25.22 | No | 2020-10-29 | D_s2_d1 | 2.87 | 35.7 | 59.7 | 1500 | 76.2 | D | 52.9 | 0.11 | s2 | y | n | d1
TN_2020_2470 |  | 79935 20343785 | 789476B | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 BEDDING FREE | 9.01 | 17 | Vilanova | TPR-54 | CD | 54.6 | 25.29 | No | 2020-10-29 | C_s1_d0 | 1.14 | 17 | 24.6 | 678 | 78.2 | C | 35.7 | 0.08 | s1 | n | n | d0
TN_2020_2471 |  | 79337 20348074 | 795262R | AFUMEX CLASS 1KV RZ1-K (AS) 5G2.5 BEDDING FREE | 12.02 | 13 | Vilanova | TPR-54 | CD | 53.2 | 22.24 | No | 2020-10-29 | B2_s1_d2 | 0.7 | 11.7 | 20.2 | 846 | 37.8 | B2 | 16 | 0.03 | s1 | n | y | d2
TN_2020_2472 |  | 79122 20184153 | 797125R | LXHIOZ1 (CBE.FRT) 1X120/16 15KV | 34.7 | 5 | Vilanova | XLPE+1420FEES1.3MM+61AASEES2.6MM | CD | 55.9 | 19.99 | No | 2020-10-29 | C_s1_d2 | 0.87 | 15.6 | 20.8 | 1500 | 44.3 | C | 4.5 | 0.01 | s1 | n | y | d2
TN_2020_2473 |  | 77711 20317801 | 5096672 | PROTOTIPO H07Z1-K 750V 1X1.5 NG | 2.88 | 165 | Vilanova | TPR-56AFUMEXVILANOVA1602 | CD | 55.8 | 18.76 | No | 2020-10-29 | D_s2_d1 | 2.12 | 19.9 | 38.6 | 744 | 99.7 | D | 82.2 | 0.18 | s2 | y | n | d1
20100031 |  | 18420 | ESS1172AA/CE6762A | 750-3G1.5-SH-NF F 55-625-255 | 11 | 14 | Paron | IX1400+04ANFEIT+5300SEIT | -- | 52.7 | 22.6 | No | 2020-10-30 | B2_s1_d0 | 0.7 | 12.2 | 23.5 | 822 | 54 | B2 | 17 | 0.03 | s1 | n | n | d0
TN_2020_2474 |  | 79337 20348074 | 795262R | AFUMEX CLASS 1KV RZ1-K (AS) 5G2.5 BEDDING FREE | 12.02 | 13 | Vilanova | TPR-54 | CD | 63 | 14.91 | No | 2020-10-30 | C_s1_d1 | 0.89 | 15.5 | 22.4 | 732 | 52 | C | 18.4 | 0.04 | s1 | y | n | d1
TN_2020_2475 |  | 79935 20343785 | 789476B | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 BEDDING FREE | 9.01 | 17 | Vilanova | TPR-54 | CD | 62.7 | 15.08 | No | 2020-10-30 | D_s1_d1 | 2.2 | 25.5 | 34 | 936 | 85.6 | D | 39.4 | 0.07 | s1 | y | n | d1
TN_2020_2476 |  | 20348075 79338 | 795124R | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 11 | 14 | Vilanova | TPR-54 | CD | 59.4 | 21.87 | No | 2020-10-30 | D_s2_d1 | 2.05 | 28.6 | 37.1 | 1035 | 68.4 | D | 53.8 | 0.1 | s2 | y | n | d1
TN_2020_2477 |  | 20348075 79338 | 795124R | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 11 | 14 | Vilanova | TPR-54 | CD | 55.2 | 24.43 | No | 2020-10-30 | D_s2_d2 | 2.25 | 34.3 | 56.9 | 1464 | 75.2 | D | 60.7 | 0.11 | s2 | n | y | d2
TN_2020_2478 |  | 79337 20348074 | 795262R | AFUMEX CLASS 1KV RZ1-K (AS) 5G2.5 BEDDING FREE | 12.02 | 13 | Vilanova | TPR-54 | CD | 75.2 | 26.8 | No | 2020-10-30 | D_s2_d1 | 3.1 | 42.8 | 76.8 | 1500 | 70.3 | D | 54.5 | 0.12 | s2 | y | n | d1
20100032 |  | 18420 | CE6756 C/ESS-1163 | 1000-1X6MM²-SH-NF F55-625-255 | 8.4 | 19 | Paron | IX1400+04ANFEIT+5300SEIT | -- | 52.1 | 23.3 | No | 2020-10-30 | C_s1_d2 | 1.4 | 16.1 | 39.9 | 720 | 100 | C | 21 | 0.04 | s1 | y | y | d2
20100033 |  | 18420 | ESS1173AA/CE6762B | 750-3G1.5-SH-NF F 55-625-255 | 11 | 14 | Paron | IX1400+04ANFEIT+56ACSEIT | -- | 52 | 22.8 | No | 2020-10-30 | B2_s1_d1 | 0.7 | 8 | 15.8 | 810 | 47 | B2 | 17 | 0.03 | s1 | y | n | d1
20100034 |  | 18465 | Mat 9041 | PRYSMIAN 255-800MM² CU XLPE -500 KV | 123.8 | 2 | Paron | XLPE+TUBEAL+6000SEESNATUREL+SKINSC | -- | 48.1 | 23.4 | No | 2020-10-30 | B2_s1_d0 | 0.8 | 5.3 | 10.4 | 717 | 33 | B2 | 9 | 0.02 | s1 | n | n | d0
TN_2020_2479 |  | 20193682 83805798 | 782169J | AFUMEX CLASS 1KV RZ1-K (AS) 5G16MM2 | 22.06 | 7 | Vilanova | 14200.34MMMEASURED+16022.10MMMEASUREDREPLÈ0.55 | CD | 77.6 | 17.83 | No | 2020-11-02 | B2_s1_d1 | 0.51 | 6.6 | 8.5 | 777 | 27.3 | B2 | 6.7 | 0.01 | s1 | y | n | d1
TN_2020_2480 |  | 79935 20343785 | 789476B | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 BEDDING FREE | 9.01 | 17 | Vilanova | TPR-54 | CD | 76.1 | 17.54 | No | 2020-11-02 | D_s2_d2 | 2.65 | 33.6 | 41.1 | 1170 | 101.1 | D | 54.4 | 0.1 | s2 | n | y | d2
TN_2020_2481 |  | 20193682 | 764423V | AFUMEX CLASS 1KV RZ1-K (AS) 5G16MM2 | 22.17 | 7 | Vilanova | 1420FEES0.20MMMEASURED+1602SEES2.28MMMEASURED | CD | 74 | 19.15 | No | 2020-11-02 | D_s1_d2 | 1.23 | 24.9 | 63.5 | 1494 | 56.8 | D | 16.4 | 0.07 | s1 | n | y | d2
TN_2020_2482 |  | 20193682 83805798 | 782207A | AFUMEX CLASS 1KV RZ1-K (AS) 5G16MM2 | 21.69 | 7 | Vilanova | 1420FEES0.2MMMEASURED+1602SEES2.14MMMEASUREDREPLÈ0.25 | CD | 71.7 | 20.45 | No | 2020-11-02 | B2_s1_d2 | 0.68 | 7.6 | 18.3 | 1500 | 26.9 | B2 | 5.7 | 0.02 | s1 | n | y | d2
TN_2020_2483 |  | 79336 20343748 | 795123P | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 10.52 | 14 | Vilanova | TPR-54 | CD | 67.3 | 24.01 | No | 2020-11-02 | B2_s1_d1 | 1.45 | 15 | 21 | 600 | 61.3 | B2 | 20.4 | 0.04 | s1 | y | n | d1
TN_2020_2484 |  | 79337 20348074 | 795262R | AFUMEX CLASS 1KV RZ1-K (AS) 5G2.5 BEDDING FREE | 12.02 | 13 | Vilanova | TPR-54 | CD | 59 | 25.47 | No | 2020-11-02 | D_s1_d1 | 2.7 | 33 | 57.4 | 1485 | 56.1 | D | 37.4 | 0.09 | s1 | y | n | d1
TN_2020_2485 |  | 79337 20348074 | 795262R | AFUMEX CLASS 1KV RZ1-K (AS) 5G2.5 BEDDING FREE | 12.02 | 13 | Vilanova | TPR-54 | CD | 61.1 | 23.65 | No | 2020-11-02 | D_s1_d2 | 3.3 | 39 | 75.4 | 1476 | 65.2 | D | 46.1 | 0.11 | s1 | n | y | d2
TN_2020_2486 |  | 79336 20343748 | 795123P | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 10.52 | 14 | Vilanova | TPR-54 | CD | 65.3 | 21.1 | No | 2020-11-02 | B2_s1_d2 | 0.55 | 12.1 | 19.9 | 840 | 50.7 | B2 | 13.7 | 0.04 | s1 | n | y | d2
TN_2020_2487 |  | 79337 20348074 | 795262R | AFUMEX CLASS 1KV RZ1-K (AS) 5G2.5 BEDDING FREE | 12.02 | 13 | Vilanova | TPR-54 | CD | 68.2 | 20.39 | No | 2020-11-02 | B2_s1_d1 | 0.72 | 14.2 | 19.4 | 789 | 43.1 | B2 | 23.8 | 0.06 | s1 | y | n | d1
TN_2020_2488 |  | 20316324 79519 | 725473H | XHIOZ1 (CBE. FRT) 1X500/16 15KV | 49.76 | 4 | Vilanova | XLPE+1420FEES1.9MM+61AASEES2.1MM | CD | 76.2 | 15.07 | No | 2020-11-04 | B2_s1_d0 | 0.7 | 12.5 | 16.3 | 1071 | 37.5 | B2 | 11.2 | 0.03 | s1 | n | n | d0
TN_2020_2489 |  | 78695 | 545871N | HEPRZ1 (AS) 30KV 400 CU | 52.95 | 4 | Vilanova | HEPR+1420FEES+61AASEES | CD | 76.5 | 15.01 | No | 2020-11-04 | B2_s1_d0 | 0.81 | 13.6 | 18.4 | 1233 | 32.4 | B2 | 5.3 | 0.01 | s1 | n | n | d0
TN_2020_2490 |  | 107 | 5096684 | TEST SAMPLE 107 PBT-FR +GEL FR (AFO429) 4X8 TKT | 12.71 | 12 | Vilanova | FILLEDFR+AFUMEXCPR+AFUMEXCPR | CD | 75 | 15.28 | No | 2020-11-04 | C_s1_d1 | 0.88 | 15.3 | 27.6 | 768 | 68.5 | C | 18.3 | 0.05 | s1 | y | n | d1
TN_2020_2491 |  | 108 | 5096683 | TEST SAMPLE 108 PBT-FR +GEL FR (AFO430) 4X8 TKEST | 16.1 | 9 | Vilanova | FILLEDFR+AFUMEXCPR+AFUMEXCPR | CD | 74.1 | 15.24 | No | 2020-11-04 | C_s1_d1 | 0.79 | 15.1 | 23.1 | 867 | 46.2 | C | 29.8 | 0.07 | s1 | y | n | d1
TN_2020_2492 |  | 78695 | 545871N | HEPRZ1 (AS) 30KV 400 CU | 52.95 | 4 | Vilanova | HEPR+1420FEES+61AASEES | CD | 74.4 | 15.64 | No | 2020-11-04 | B2_s1_d0 | 0.68 | 14.3 | 18.1 | 1059 | 34.9 | B2 | 10.7 | 0.04 | s1 | n | n | d0
TN_2020_2493 |  | 111 | 5096686 | TEST SAMPLE 111 PBT-FR + GEL FR (AFO424) 4X12 VT-FR | 10.21 | 15 | Vilanova | FILLEDFR+AFUMEXCPR | CD | 69.8 | 13.61 | No | 2020-11-05 | D_s2_d0 | 3.3 | 47.1 | 60.2 | 741 | 151 | D | 81 | 0.11 | s2 | n | n | d0
TN_2020_2494 |  | 110 | 5096685 | TEST SAMPLE 110 PBT-FR + GEL FR (AFO423) 4X12 TVT-FR | 12.84 | 12 | Vilanova | FILLEDFR+AFUMEXCPR+AFUMEXCPR | CD | 68.3 | 13.77 | No | 2020-11-05 | C_s1_d0 | 1.13 | 19.6 | 37.4 | 828 | 88.5 | C | 43.1 | 0.11 | s1 | n | n | d0
TN_2020_2495 |  | 109 | 5096677 | TEST SAMPLE 109 PBT-FR + GEL FR (AFO428) 4X8 KT-FR | 11.3 | 14 | Vilanova | FILLEDFR+AFUMEXCPR | CD | 68.1 | 17.68 | No | 2020-11-05 | D_s1_d1 | 3.3 | 44.3 | 64.3 | 855 | 133 | D | 49.4 | 0.07 | s1 | y | n | d1
TN_2020_2496 |  | 113 | 5096689 | TEST SAMPLE 113 DROP I_O ED5 1X1 | 5.07 | 30 | Vilanova | DRY+PC/PELT+DHF9740 | CD | 64.7 | 20.38 | No | 2020-11-05 | C_s1_d0 | 1.78 | 11.6 | 40.7 | 507 | 230.9 | C | 33.5 | 0.11 | s1 | n | n | d0
TN_2020_2497 |  | 112 | 5096690 | TEST SAMPLE 112 DROP I_O ED5 1X1 | 5.07 | 30 | Vilanova | DRY+PC/PELT+AFUMEXCPR | CD | 64.3 | 20.83 | No | 2020-11-05 | D_s2_d0 | 3.3 | 34 | 250 | 522 | 1143.9 | D | 56.2 | 0.25 | s2 | n | n | d0
TN_2020_2498 |  | 108 | 5096683 | TEST SAMPLE 108 PBT-FR +GEL FR (AFO430) 4X8 TKEST | 16.1 | 9 | Vilanova | FILLEDFR+AFUMEXCPR+AFUMEXCPR | CD | 78.6 | 17.49 | No | 2020-11-06 | C_s1_d2 | 0.86 | 16.1 | 22 | 996 | 46.4 | C | 22.8 | 0.04 | s1 | n | y | d2
TN_2020_2499 |  | 107 | 5096684 | TEST SAMPLE 107 PBT-FR +GEL FR (AFO429) 4X8 TKT | 12.71 | 12 | Vilanova | FILLEDFR+AFUMEXCPR+AFUMEXCPR | CD | 77.3 | 17.71 | No | 2020-11-06 | C_s2_d1 | 1.45 | 24.5 | 40.3 | 891 | 96 | C | 52.4 | 0.12 | s2 | y | n | d1
TN_2020_2500 |  | 114 | 5096688 | TEST SAMPLE 114 DROP I_O ED5 1X1 | 5.04 | 30 | Vilanova | DRY+PC/PELT+CYGSA | CD | 75.3 | 18.8 | No | 2020-11-06 | D_s2_d1 | 3.3 | 34.9 | 171.2 | 603 | 569.5 | D | 65.6 | 0.23 | s2 | y | n | d1
TN_2020_2501 |  |  | 5096695 | U/UTP5E P4 CCA | 5.42 | 30 | Vilanova | LSHFINSULATION+CONGUARDS66500.6MM | CD | 75.3 | 19.86 | No | 2020-11-06 | D_s1_d0 | 2.13 | 11.7 | 27.5 | 507 | 136.5 | D | 24.7 | 0.06 | s1 | n | n | d0
TN_2020_2505 |  |  | 5096693 | F/UTP5E P5 CCA | 6.49 | 25 | Vilanova | CONGUARDS6650SHEATH0.80MM | CD | 69.5 | 13.59 | No | 2020-11-09 | C_s1_d0 | 0.81 | 8.7 | 35.9 | 543 | 158.5 | C | 16.8 | 0.05 | s1 | n | n | d0
TN_2020_2506 |  |  | 5096692 | U/UTP5E P6 CCA | 5.22 | 30 | Vilanova | CONGUARDS6650SHEATH0.65MM | CD | 69.1 | 13.52 | No | 2020-11-09 | D_s2_d1 | 3.3 | 27.5 | 71.7 | 963 | 145.4 | D | 66.2 | 0.17 | s2 | y | n | d1
TN_2020_2507 |  |  | 5096694 | U/UTP5E P5 CCA | 5.21 | 30 | Vilanova | CONGUARDS6650SHEATH0.80MM | CD | 68.6 | 18.79 | No | 2020-11-09 | D_s1_d0 | 3.3 | 18.4 | 37.5 | 594 | 151.3 | D | 49.9 | 0.1 | s1 | n | n | d0
TN_2020_2508 |  | 75543 20329100 | 771630D | TSLI(F) 145KV 1X400 AI2 H70 | 75.9 | 3 | Vilanova | 61AA+LE0563 | CD | 65.5 | 21.65 | No | 2020-11-09 | C_s1_d0 | 1.09 | 18.9 | 26.3 | 933 | 46.4 | C | 28 | 0.09 | s1 | n | n | d0
TN_2020_2509 |  |  | 5096691 | F/UTP5E P6 CCA | 6.03 | 25 | Vilanova | LSHFINSULATION+CONGUARDS66500.6MM | CD | 55 | 22.85 | No | 2020-11-09 | B2_s1_d1 | 1.32 | 7.3 | 23.9 | 534 | 111 | B2 | 13.7 | 0.04 | s1 | y | n | d1
TN_2020_2510 |  | 80263 20173170 | 771624X | RHZ1-RA+2OL (AS) 66KV 1X1000K AL+H135 | 75.25 | 3 | Vilanova | 61AA+LE0563 | CD | 55.3 | 24.91 | No | 2020-11-09 | C_s1_d0 | 0.76 | 15.9 | 22.3 | 942 | 51.9 | C | 27.4 | 0.07 | s1 | n | n | d0
TN_2020_2511 |  |  | 5096696 | F/UTP5E P4 CCA | 6.3 | 25 | Vilanova | CONGUARDS6650SHEATH0.65MM | CD | 58.7 | 23.08 | No | 2020-11-09 | B2_s1_d0 | 0.58 | 5.3 | 22.7 | 513 | 123 | B2 | 3.8 | 0.03 | s1 | n | n | d0
TN_2020_2512 |  | 80053 202098811 | 744848T | EXZHELLENT-XXI RZ1-K (AS) 1KV 1X4MM2 | 8.08 | 19 | Vilanova | PENDINGTOCONFIRM | CD | 61.5 | 18.9 | No | 2020-11-09 | D_s2_d2 | 3.3 | 39.8 | 68.7 | 1500 | 98.2 | D | 56.1 | 0.2 | s2 | n | y | d2
TN_2020_2516 |  |  | 5096968 | AFUMEX CLASS 750V H07Z-1-K (AS) TYPE 2 1X25 CCAS1BD1 | 8.88 | 17 | Vilanova | REFENCESAMPLE | CD | 76.2 | 16.23 | No | 2020-11-13 | B2_s1_d0 | 0.64 | 5.2 | 10.8 | 732 | 43.9 | B2 | 5 | 0.02 | s1 | n | n | d0
TN_2020_2517 |  |  | 5096970 | AFUMEX CLASS 750V H07Z-1-K (AS) TYPE 2 1X25 CCAS1BD1 | 8.74 | 17 | Vilanova | REFENCESAMPLE | CD | 74.3 | 18.48 | No | 2020-11-13 | B2_s1_d0 | 0.72 | 5.7 | 14.1 | 633 | 54 | B2 | 13.2 | 0.03 | s1 | n | n | d0
TN_2020_2518 |  | 80024 20351401 | 5096674 | PRYSUN H1Z2Z2-K 6MM2 1.5/1.5 (1.8 KV) | 6.14 | 25 | Vilanova | SOLARINT-SOLAREXT | CD | 71.6 | 20.81 | No | 2020-11-13 | D_s2_d2 | 3.3 | 36.5 | 72.6 | 1170 | 146.9 | D | 72.7 | 0.14 | s2 | n | y | d2
TN_2020_2519 |  | 80062 20351631 | 5096675 | PRYSUN H1Z2Z2-K 6MM2 1.5/1.5 (1.8 KV) | 6.23 | 25 | Vilanova | IE15AAIT-4G352 | CD | 67.1 | 24.15 | No | 2020-11-13 | D_s2_d2 | 3.3 | 48.8 | 306.3 | 699 | 767.6 | D | 104.5 | 0.48 | s2 | n | y | d2
CEL-0877 |  | 78194 20300592 | 786482X | EPR/PVC FRRT 3.8/6.6KV 400MM2 | 38 | 5 | CEIS | ID7140IT+CUTAPE+PVCFKN931B | CD | 44 | 21.79 | No | 2020-11-20 | B2_s2_d1 | 0.7 | 8.2 | 12.4 | 1497 | 89.8 | B2 | 130.1 | 0.37 | s2 | y | n | d1
TN_2020_2520 |  | 80053 202098811 | 744848T | EXZHELLENT-XXI RZ1-K (AS) 1KV 1X4MM2 | 8.08 | 19 | Vilanova | PENDINGTOCONFIRM | CD | 77.1 | 16.04 | No | 2020-11-15 | D_s2_d0 | 3.3 | 39.4 | 49.2 | 1068 | 86.1 | D | 51.4 | 0.09 | s2 | n | n | d0
TN_2020_2521 |  | 80165 20352271 | 812111E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.03 | 13 | Vilanova | 1420+1602 | CD | 76.8 | 15.72 | No | 2020-11-15 | D_s1_d2 | 2.52 | 42.7 | 59.8 | 1209 | 74.6 | D | 36.1 | 0.1 | s1 | n | y | d2
TN_2020_2522 |  | 20166 20352258 | 812124U | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.22 | 15 | Vilanova | 1420+1602 | CD | 74.8 | 19.49 | No | 2020-11-15 | D_s1_d2 | 2.17 | 33.8 | 50 | 1101 | 85.1 | D | 37 | 0.07 | s1 | n | y | d2
TN_2020_2523 |  | 77711 20317801 | 5095687 | PROTOTIPO H07Z1-K 750V 1X1.5 NG | 2.88 | 165 | Vilanova | TPR-56AFUMEXVILANOVA1602 | CD | 71.9 | 22.76 | No | 2020-11-15 | D_s2_d1 | 2.38 | 23.9 | 44 | 750 | 112.8 | D | 98.3 | 0.18 | s2 | y | n | d1
TN_2020_2524 |  | 83931469 20193657 | 802544F | AFUMEX CLASS 1KV RZ1-K (AS) 3G6 | 13.76 | 11 | Vilanova | 1420+1602 | CD | 63.8 | 24.16 | No | 2020-11-15 | B2_s1_d0 | 0.78 | 14.6 | 22.7 | 1134 | 38.3 | B2 | 22.8 | 0.05 | s1 | n | n | d0
TN_2020_2525 |  | 79467 20349179 | 812112F | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.98 | 13 | Vilanova | TPR-49+1602 | CD | 69.6 | 18.18 | No | 2020-11-16 | E ou F_s2_d2 | 3.3 | 100.3 | 188.7 | 1182 | 214.8 | E ou F | 83.5 | 0.25 | s2 | n | y | d2
TN_2020_2526 |  | 20171 20352259 | 812109C | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 10.86 | 14 | Vilanova | 1420+1602 | CD | 68.2 | 17.91 | No | 2020-11-16 | D_s1_d2 | 2.18 | 33 | 44.3 | 966 | 90 | D | 39.8 | 0.06 | s1 | n | y | d2
TN_2020_2527 |  | 20166 20352258 | 812124U | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.22 | 15 | Vilanova | 1420+1602 | CD | 70.7 | 19.87 | No | 2020-11-16 | D_s1_d2 | 2.12 | 31.5 | 43.2 | 1212 | 65.9 | D | 27.6 | 0.07 | s1 | n | y | d2
TN_2020_2528 |  | 75543 20329100 | 771630D | TSLI(F) 145KV 1X400 AI2 H70 | 75.9 | 3 | Vilanova | 61AA+LE0563 | CD | 71.8 | 19.19 | No | 2020-11-16 | C_s1_d0 | 1 | 18.6 | 24 | 939 | 46.8 | C | 19.4 | 0.06 | s1 | n | n | d0
TN_2020_2529 |  | 80165 20352271 | 812111E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.03 | 13 | Vilanova | 1420+1602 | CD | 67.5 | 20.34 | No | 2020-11-16 | D_s2_d2 | 3.3 | 68 | 149.2 | 1500 | 132.6 | D | 56.8 | 0.11 | s2 | n | y | d2
TN_2020_2531 |  | 83554105 20226615 | 5096699 | FG16OM16 3G6- 0.6/1 KV | 13.52 | 11 | Vilanova | LSOH | CD | 64.4 | 13.73 | No | 2020-11-17 | B2_s1_d0 | 0.7 | 10 | 15.9 | 1074 | 41.2 | B2 | 7.9 | 0.01 | s1 | n | n | d0
TN_2020_2533 |  | 83822111 20215171 | 09-I22750 | FG16R16 1X25- 0.6/1 KV | 11.48 | 14 | Vilanova | PVC | CD | 63.7 | 13.8 | No | 2020-11-17 | C_s2_d1 | 0.83 | 10.2 | 31.7 | 684 | 82.8 | C | 161.4 | 0.58 | s2 | y | n | d1
TN_2020_2532 |  | 83771934 20215632 | T9-I22755 | FG16OM16 12G1.5 - 0.6/1 KV | 18.48 | 8 | Vilanova | LSOH | CD | 60.4 | 17.89 | No | 2020-11-17 | B2_s1_d2 | 0.68 | 8.8 | 16.7 | 1461 | 36.9 | B2 | 23.5 | 0.05 | s1 | n | y | d2
TN_2020_2530 |  | 20078005 | 588957W | HEPRZ1(AS) 132KV 1X800K AL+H280 EPROTENAX | 94.8 | 2 | Vilanova | DMZ-26000SEES+LE0563@70%+DMZ-E@30% | CD | 66 | 20.88 | No | 2020-11-17 | B2_s1_d2 | 0.83 | 9.7 | 12.2 | 1500 | 29.2 | B2 | 14.9 | 0.02 | s1 | n | y | d2
TN_2020_2534 |  | 80263 20173170 | 771624X | RHZ1-RA+2OL (AS) 66KV 1X1000K AL+H135 | 75.25 | 3 | Vilanova | 61AA+LE0563 | CD | 51.6 | 24.7 | No | 2020-11-17 | C_s1_d0 | 0.81 | 16.7 | 22.1 | 936 | 43.4 | C | 28.7 | 0.08 | s1 | n | n | d0
TN_2020_2535 |  | 83931469 20193657 | 802544F | AFUMEX CLASS 1KV RZ1-K (AS) 3G6 | 13.75 | 11 | Vilanova | 1420+1602 | CD | 54.9 | 23.95 | No | 2020-11-17 | B2_s1_d2 | 0.47 | 12.7 | 18.4 | 1179 | 43.6 | B2 | 7.2 | 0.02 | s1 | n | y | d2
TN_2020_2536 |  | 83931469 20193657 | 802544F | AFUMEX CLASS 1KV RZ1-K (AS) 3G6 | 13.75 | 11 | Vilanova | 1420+1602 | CD | 57.6 | 21.42 | No | 2020-11-17 | C_s1_d0 | 0.82 | 15.4 | 25.9 | 1074 | 39.2 | C | 11.4 | 0.07 | s1 | n | n | d0
TN_2020_2537 |  | 83648280 20290311 | 5096698 | FS18OR18 3G2.5 500V | 8.37 | 19 | Vilanova | PVC | CD | 61.4 | 18.74 | No | 2020-11-17 | C_s2_d0 | 0.71 | 6.7 | 21.8 | 441 | 156.7 | C | 199.8 | 1.02 | s2 | n | n | d0
TN_2020_2538 |  | 83813507 20290330 | 09-I22731 | FS18OR18 7G1.5 500V | 9.62 | 15 | Vilanova | PVC | CD | 64.1 | 16.88 | No | 2020-11-17 | B2_s2_d0 | 0.75 | 7.6 | 19.2 | 447 | 133.5 | B2 | 203.3 | 0.9 | s2 | n | n | d0
TN_2020_2539 |  | 80171 20352259 | 812109C | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 10.86 | 14 | Vilanova | 1420+1602 | CD | 66.2 | 16.44 | No | 2020-11-17 | D_s1_d2 | 2.65 | 42.9 | 63.5 | 969 | 100 | D | 47.1 | 0.1 | s1 | n | y | d2
TN_2020_2540 |  |  | 5096508 | 3.U/UTP6 4P CCA 3.W | 5.75 | 25 | Vilanova | LSHFSKIN+S6650SHEATH0.55MM | CD | 72.7 | 13.58 | No | 2020-11-18 | B2_s1_d0 | 0.62 | 3.7 | 11.3 | 516 | 93 | B2 | 4.4 | 0.02 | s1 | n | n | d0
TN_2020_2541 |  | 79467 20349179 | 812112F | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.98 | 13 | Vilanova | TPR-49+1602 | CD | 72.2 | 13.34 | No | 2020-11-18 | E ou F_s2_d2 | 3.3 | 72.1 | 152.6 | 1311 | 151.1 | E ou F | 59.4 | 0.17 | s2 | n | y | d2
TN_2020_2542 |  | 83771922 20215405 | 09-I22721 | FG16OR16 1KV - 0.6/1 KV 4G2.5 | 12.17 | 13 | Vilanova | PVC | CD | 69.3 | 16.2 | No | 2020-11-18 | B2_s2_d0 | 0.86 | 12.4 | 28.6 | 651 | 124.6 | B2 | 230 | 0.72 | s2 | n | n | d0
TN_2020_2543 |  |  | 5096509 | 3.U/UTP6 4P CCA 3.X | 5.77 | 25 | Vilanova | LSHFSKIN+S6650SHEATH0.65MM | CD | 69.2 | 19.58 | No | 2020-11-18 | B2_s1_d0 | 0.51 | 5.8 | 12 | 564 | 108.7 | B2 | 35.2 | 0.04 | s1 | n | n | d0
TN_2020_2544 |  |  | 5096506 | 3.U/UTP6 4P CCA 3.26 | 5.72 | 25 | Vilanova | LSHFSKIN+S533SHEATH0.55MM | CD | 65.9 | 21.95 | No | 2020-11-18 | B2_s1_d0 | 1.01 | 5.5 | 16.4 | 537 | 98.7 | B2 | 7.8 | 0.02 | s1 | n | n | d0
TN_2020_2547 |  | 80176 20352260 | 795976S | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.96 | 13 | Vilanova | E:0.7_14BA+1602 | CD | 74.7 | 13.8 | No | 2020-11-19 | D_s1_d2 | 2.32 | 44.1 | 56.6 | 975 | 89.1 | D | 45.9 | 0.08 | s1 | n | y | d2
TN_2020_2548 |  | 79466 20349178 | 812110D | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.54 | 13 | Vilanova | TPR-49+1602 | CD | 72.9 | 13.65 | No | 2020-11-19 | D_s1_d1 | 2.16 | 32.2 | 41.9 | 1212 | 72.8 | D | 45.3 | 0.09 | s1 | y | n | d1
TN_2020_2549 |  | 79465 20349177 | 812092J | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.52 | 13 | Vilanova | TPR-49+1602 | CD | 71.3 | 17.91 | No | 2020-11-19 | D_s2_d2 | 3.3 | 54.6 | 105 | 1395 | 107.4 | D | 59.7 | 0.14 | s2 | n | y | d2
TN_2020_2550 |  | 80172 20352259 | 806316F | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.25 | 14 | Vilanova | 14BA+1602 | CD | 66.5 | 21.85 | No | 2020-11-19 | D_s1_d2 | 2.07 | 32.2 | 43.5 | 1266 | 64.4 | D | 43.8 | 0.09 | s1 | n | y | d2
TN_2020_2551 |  | 80167 20352258 | 796028Y | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.95 | 15 | Vilanova | 14BA+1602 | CD | 58.2 | 25.84 | No | 2020-11-19 | C_s1_d1 | 1.99 | 27.1 | 38.7 | 903 | 67.8 | C | 48.5 | 0.09 | s1 | y | n | d1
TN_2020_2552 |  | 79465 20349177 | 812092J | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.52 | 14 | Vilanova | TPR-49+1602 | CD | 49.4 | 26.07 | No | 2020-11-19 | E ou F_s2_d2 | 3.3 | 75 | 147.5 | 1200 | 163.9 | E ou F | 62.9 | 0.17 | s2 | n | y | d2
TN_2020_2553 |  | 80176 20352260 | 795976S | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.96 | 13 | Vilanova | E:0.7_14BA+1602 | CD | 47 | 25.05 | No | 2020-11-19 | D_s1_d2 | 3.3 | 51.3 | 85.1 | 1494 | 88.3 | D | 40.4 | 0.11 | s1 | n | y | d2
TN_2020_2554 |  | 80172 20352259 | 806316F | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.25 | 14 | Vilanova | 14BA+1602 | CD | 47.3 | 22.34 | No | 2020-11-19 | C_s1_d2 | 1.72 | 24.9 | 36.4 | 969 | 55.4 | C | 22.4 | 0.07 | s1 | n | y | d2
TN_2020_2555 |  | 80167 20352258 | 796028Y | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.95 | 15 | Vilanova | 14BA+1602 | CD | 51.7 | 19.55 | No | 2020-11-19 | D_s1_d1 | 2.12 | 31.1 | 42.5 | 894 | 85 | D | 43 | 0.08 | s1 | y | n | d1
TN_2020_2556 |  | 79466 20349178 | 812110D | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.54 | 13 | Vilanova | TPR-49+1602 | CD | 56.5 | 17.57 | No | 2020-11-19 | E ou F_s1_d2 | 3.3 | 70.7 | 147.3 | 1368 | 138 | E ou F | 49.2 | 0.18 | s1 | n | y | d2
TN_2020_2557 |  |  | 5096507 | 3.U/UTP6 4P CCA 3.27 | 5.87 | 25 | Vilanova | LSHFSKIN+S533SHEATH0.65MM | CD | 58.8 | 13 | No | 2020-11-20 | B2_s1_d0 | 1.11 | 5.9 | 17.4 | 573 | 96.3 | B2 | 5.3 | 0.02 | s1 | n | n | d0
TN_2020_2558 |  | 75350 20320357 | 5096501 (816498Y) | XAZ1 1X300 PT - PROTOTIPO A | 34.01 | 5 | Vilanova | PRS-03;TPR-38STEELTAPE;PETTAPE;TPR-55 | CD | 58.5 | 12.44 | No | 2020-11-20 | B2_s1_d2 | 0.78 | 14.8 | 23.8 | 1212 | 31.3 | B2 | 23.2 | 0.06 | s1 | n | y | d2
TN_2020_2559 |  | 75351 20320358 | 5096502 (816498Y) | XAZ1 1X300 PT - PROTOTIPO B | 33.68 | 5 | Vilanova | PRS-03;TPR-38STEELTAPE;LANTORTAPE;TPR-55 | CD | 63.8 | 13.6 | No | 2020-11-20 | B2_s1_d2 | 0.64 | 12.6 | 16.3 | 1101 | 48 | B2 | 12.5 | 0.02 | s1 | n | y | d2
TN_2020_2560 |  | 80114 20339524 | 5096503 (816498Y) | G 1X300 VD | 26.01 | 6 | Vilanova | TPR-32 | CD | 52.9 | 14.72 | No | 2020-11-20 | B2_s1_d1 | 0.46 | 6.4 | 8 | 579 | 29.2 | B2 | 11.3 | 0.02 | s1 | y | n | d1
20110001 |  | 18420 | CE6756 A/ESS-881 | 1000-1X6MM²-SH-NF F55-625-255 | 8.3 | 19 | Paron | ID3100FR/SV3300FR+0400FEIT+5300SEIT | -- | 42.2 | 22 | No | 2020-11-18 | B2_s1_d1 | 0.45 | 3 | 7.7 | 582 | 43 | B2 | 6 | 0.01 | s1 | y | n | d1
20110002 |  | 18420 | CE6756 B/ESS-1162 | 1000-1X6MM²-SH-NF F55-625-255 | 8.3 | 19 | Paron | IX1400+0400FEIT+5300SEIT | -- | 43.3 | 22.2 | No | 2020-11-18 | C_s1_d2 | 1.15 | 17.1 | 37.1 | 768 | 81 | C | 48 | 0.07 | s1 | y | y | d2
20110003 |  | 18420 | CE6756 C/ESS-1163 | 1000-1X6MM²-SH-NF F55-625-255 | 8.4 | 19 | Paron | IX1400+04ANFEIT+5300SEIT | -- | 40 | 23.5 | No | 2020-11-18 | C_s1_d2 | 0.95 | 13.1 | 31.4 | 684 | 89 | C | 9 | 0.05 | s1 | y | y | d2
20110004 |  | 18420 | ESS1173AA/CE6762B | 750-3G1.5-SH-NF F 55-625-255 | 11 | 14 | Paron | IX1400+04ANFEIT+56ACSEIT | -- | 37.3 | 24 | No | 2020-11-18 | B2_s1_d0 | 0.65 | 8.4 | 15.6 | 882 | 64 | B2 | 28 | 0.06 | s1 | n | n | d0
20110005 |  | 18420 | ESS1172AA/CE6762A | 750-3G1.5-SH-NF F 55-625-255 | 11 | 14 | Paron | IX1400+04ANFEIT+5300SEIT | -- | 38.4 | 23.3 | No | 2020-11-18 | B2_s1_d0 | 0.55 | 7.7 | 14.8 | 945 | 45 | B2 | 12 | 0.04 | s1 | n | n | d0
TN_2020_2561 |  | 80620 20352260 | 824307L | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12 | 13 | Vilanova | 16BA+160HD | CD | 60.5 | 10.07 | No | 2020-11-22 | C_s1_d2 | 1.27 | 19.7 | 32.3 | 813 | 65.5 | C | 22.4 | 0.04 | s1 | n | y | d2
TN_2020_2562 |  | 80177 20352260 | 824302F | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.96 | 13 | Vilanova | 1420+16HD | CD | 61.2 | 9.65 | No | 2020-11-22 | D_s1_d2 | 1.92 | 31.6 | 47.6 | 975 | 73.1 | D | 34.2 | 0.05 | s1 | n | y | d2
TN_2020_2563 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 58.1 | 13.52 | No | 2020-11-22 | C_s1_d2 | 1.19 | 18.1 | 29.6 | 924 | 50.6 | C | 34.2 | 0.06 | s1 | n | y | d2
TN_2020_2564 |  | 80618 2035260 | 795975R | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.98 | 13 | Vilanova | 0400+1602 | CD | 55.7 | 18.13 | No | 2020-11-22 | E ou F_s2_d2 | 3.3 | 78.7 | 150.4 | 1500 | 129 | E ou F | 57.8 | 0.26 | s2 | n | y | d2
TN_2020_2565 |  | 80619 20352260 | 824300D | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.07 | 13 | Vilanova | 0400+160HD | CD | 52.4 | 20.28 | No | 2020-11-22 | C_s1_d1 | 1.76 | 28.9 | 45.2 | 789 | 92.8 | C | 17.3 | 0.03 | s1 | y | n | d1
TN_2020_2567 |  | 80178 20352260 | 824305J | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.55 | 12 | Vilanova | E:0.7_1420+E:1.24_16HD | CD | 65.7 | 10.79 | No | 2020-11-23 | C_s1_d1 | 1.3 | 22.4 | 37.1 | 858 | 67 | C | 26.3 | 0.05 | s1 | y | n | d1
TN_2020_2568 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 65.4 | 10.8 | No | 2020-11-23 | C_s1_d1 | 1.04 | 18.3 | 30.9 | 834 | 58 | C | 21 | 0.04 | s1 | y | n | d1
TN_2020_2569 |  | 80177 20352260 | 824302F | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.96 | 13 | Vilanova | 1420+16HD | CD | 62.1 | 14.37 | No | 2020-11-23 | D_s1_d2 | 2.27 | 40 | 57.2 | 990 | 90.2 | D | 45.1 | 0.07 | s1 | n | y | d2
TN_2020_2570 |  | 80620 20352260 | 824307L | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12 | 13 | Vilanova | 16BA+160HD | CD | 59.4 | 20.74 | No | 2020-11-23 | C_s1_d2 | 1.67 | 27.2 | 39.9 | 933 | 74.6 | C | 38.7 | 0.06 | s1 | n | y | d2
TN_2020_2571 |  | 80619 20352260 | 824300D | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.07 | 13 | Vilanova | 0400+160HD | CD | 54.8 | 21.6 | No | 2020-11-23 | C_s1_d1 | 1.38 | 22.3 | 34 | 792 | 77.2 | C | 21.6 | 0.04 | s1 | y | n | d1
TN_2020_2573 |  | 80178 20352260 | 824305J | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.55 | 12 | Vilanova | E:0.7_1420+E:1.24_16HD | CD | 67.2 | 10.68 | No | 2020-11-24 | C_s1_d1 | 1.11 | 17.8 | 28.3 | 843 | 52.9 | C | 21 | 0.04 | s1 | y | n | d1
TN_2020_2574 |  | 80618 2035260 | 795975R | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.98 | 13 | Vilanova | 0400+1602 | CD | 67.7 | 10.74 | No | 2020-11-24 | D_s1_d2 | 3.3 | 57.7 | 115.2 | 1500 | 105.9 | D | 43.7 | 0.1 | s1 | n | y | d2
TN_2020_2575 |  | 5093510 | 436 | EUPEN XVB 5G16 0.6/ 1 KV CCA S3 D2 A3 GRIS | 21.19 | 7 | Vilanova | COMPETITORSAMPLE | CD | 64.9 | 15.81 | No | 2020-11-24 | C_s2_d0 | 1.11 | 18.4 | 30.2 | 1500 | 77.7 | C | 227.8 | 0.45 | s2 | n | n | d0
TN_2020_2576 |  | 5096511 | 437 | NEXANS XVB 5G16 0.6/ 1 KVCCA S3 D2 A3 GRIS | 22.35 | 7 | Vilanova | COMPETITORSAMPLE | CD | 62.8 | 20.31 | No | 2020-11-24 | C_s2_d0 | 1.48 | 19.8 | 37.3 | 1176 | 71.5 | C | 201.6 | 0.4 | s2 | n | n | d0
TN_2020_2577 |  | 80115 20339525 | 5096505 (816498Y) | G 1X500 VD | 33.6 | 5 | Vilanova | TPR-32 | CD | 56.2 | 20.34 | No | 2020-11-24 | B2_s1_d2 | 0.52 | 8.6 | 13.3 | 921 | 36.8 | B2 | 14.6 | 0.02 | s1 | n | y | d2
TN_2020_2578 |  | 80619 20352260 | 824300D | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.07 | 13 | Vilanova | 0400+160HD | CD | 73.8 | 13.04 | No | 2020-11-25 | C_s1_d1 | 1.28 | 21.8 | 38 | 792 | 77.3 | C | 32.2 | 0.06 | s1 | y | n | d1
TN_2020_2579 |  | 80619 20352260 | 824300D | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.07 | 13 | Vilanova | 0400+160HD | CD | 73.3 | 13.71 | No | 2020-11-25 | C_s1_d1 | 1.05 | 18.5 | 33.4 | 816 | 66.8 | C | 30.4 | 0.05 | s1 | y | n | d1
TN_2020_2580 |  | 80619 20352260 | 824300D | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.07 | 13 | Vilanova | 0400+160HD | CD | 71.3 | 16.64 | No | 2020-11-25 | B2_s1_d2 | 0.92 | 14.5 | 23.8 | 762 | 51.8 | B2 | 19.7 | 0.03 | s1 | n | y | d2
TN_2020_2581 |  | 5096512 | 438 | EUPEN XGB 4X25 0.6/ 1 KV CCA S1 D2 A1 VERDE | 24.01 | 7 | Vilanova | COMPETITORSAMPLE | CD | 68.5 | 19.78 | No | 2020-11-25 | B2_s1_d0 | 0.43 | 5 | 8.6 | 591 | 29.4 | B2 | 11.8 | 0.01 | s1 | n | n | d0
TN_2020_2582 |  |  | 5096695 | U/UTP5E P4 CCA | 5.42 | 30 | Vilanova | LSHFINSULATION+CONGUARDS66500.6MM | CD | 66.9 | 18.57 | No | 2020-11-25 | B2_s1_d0 | 0.62 | 4.5 | 15.9 | 474 | 136.8 | B2 | 4.7 | 0.03 | s1 | n | n | d0
TN_2020_2583 |  | 78803 20346321 | 728481C | CCTSST (H) FR 0.3 4X1.4 | 16.29 | 9 | Vilanova | 1420FEES+TPR55 | CD | 76.3 | 13.4 | No | 2020-11-26 | B2_s1_d2 | 0.68 | 12 | 16.7 | 1179 | 38.1 | B2 | 23.3 | 0.04 | s1 | n | y | d2
TN_2020_2584 |  | 75866 | 728484F | CCTSST (X) FR 0.1 1X4X1.4 | 16.4 | 9 | Vilanova | 1420FEES+TPR55 | CD | 76.2 | 13.86 | No | 2020-11-26 | B2_s1_d2 | 0.61 | 13.5 | 18.1 | 1083 | 49.2 | B2 | 16.9 | 0.03 | s1 | n | y | d2
TN_2020_2585 |  |  | HBT 222231 | CE6755/ESS1169 3X240+95 | 59.93 | 4 | Vilanova | INS:1X1400FRBEDDING:1200FPFRNATURALISHEATH:1000GPFRBLACKOSHEATH:2800SPFRBLACK | CD | 65.7 | 18.88 | No | 2020-11-26 | B2_s3_d2 | 0.66 | 8.4 | 11.4 | 555 | 66.1 | B2 | 548.9 | 1.29 | s3 | n | y | d2
TN_2020_2586 |  |  | HBT 222229 | CE6754/ESS1168 3X150+70 | 50.41 | 4 | Vilanova | INS:1X1400FRBEDDING:1200FPFRNATURALISHEATH:1000GPFRBLACKOSHEATH:2800SPFRBLACK | CD | 71.2 | 20.06 | No | 2020-11-26 | B2_s3_d2 | 0.67 | 9 | 10.8 | 801 | 50.7 | B2 | 459.6 | 0.82 | s3 | n | y | d2
CEL-0714-20-1 |  | 71127 | 543464X | AFUMEX CLASS RZ1-K (AS) 1KV 1X240 | 27.74 | 6 | CEIS | SXLPE+1420FEES+1602SEES | CD | 63 | 24 | No | 2020-11-20 | B2_s1_d1 | 0.8 | 13.08 | 23.6 | 1497 | 38.77 | B2 | 5.36 | 0.01 | s1 | y | n | d1
TN_2020_2587 |  | 80334 20193980 | 5096513 | AFUMEX CLASS H07Z1-K PRYSMIAN750V 1X1.5 NEGRE | 2.9 | 165 | Vilanova | 1602+1510 | CD | 79.4 | 16 | No | 2020-11-27 | C_s2_d0 | 1.87 | 19.5 | 44.3 | 708 | 113.4 | C | 67.6 | 0.15 | s2 | n | n | d0
TN_2020_2588 |  | 83830692 20302944 | 5096517 | EXZHELLENT COMPACT RZ1-K 5G1.5 | 11.42 | 14 | Vilanova | 0400+TPR-54AMBATH10HF | CD | 75 | 17.04 | No | 2020-11-27 | B2_s1_d0 | 1.11 | 14.2 | 23.4 | 783 | 48.5 | B2 | 28.4 | 0.07 | s1 | n | n | d0
TN_2020_2589 |  | 83830692 20302944 | 5096517 | EXZHELLENT COMPACT RZ1-K 5G1.5 | 11.42 | 14 | Vilanova | 0400+TPR-54AMBATH10HF | CD | 75 | 17.6 | No | 2020-11-27 | B2_s1_d0 | 0.44 | 9.3 | 14.5 | 924 | 43.9 | B2 | 13.3 | 0.02 | s1 | n | n | d0
TN_2020_2590 |  |  | 5096514 | ALENTEC U/UTP6 4X2X2.3 | 6.44 | 25 | Vilanova | LSHF | CD | 75 | 12.89 | No | 2020-11-30 | B2_s1_d1 | 0.57 | 4.5 | 12.9 | 495 | 84.2 | B2 | 8.2 | 0.03 | s1 | y | n | d1
TN_2020_2591 |  |  | 5096515 | U/UTP6 REVERSE SILVERLANE | 6.44 | 25 | Vilanova | LSHF | CD | 75 | 12.99 | No | 2020-11-30 | B2_s1_d1 | 0.91 | 5.8 | 19.6 | 534 | 123.1 | B2 | 9.4 | 0.03 | s1 | y | n | d1
TN_2020_2592 |  | 80739 20352259 | 812030S | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.41 | 14 | Vilanova | 0.50400+1.2416HD | CD | 75 | 16.88 | No | 2020-11-30 | B2_s1_d1 | 0.55 | 7.8 | 14.2 | 810 | 44.3 | B2 | 24.7 | 0.04 | s1 | y | n | d1
TN_2020_2593 |  | 80173 20352259 | 824311R | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.32 | 14 | Vilanova | 0.51420+1.2416HD | CD | 75 | 21.35 | No | 2020-11-30 | C_s1_d1 | 1.1 | 17.2 | 34.6 | 825 | 66.1 | C | 37.1 | 0.07 | s1 | y | n | d1
TN_2020_2594 |  | 80173 20352259 | 824311R | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.32 | 14 | Vilanova | 0.51420+1.2416HD | CD | 75 | 22.08 | No | 2020-11-30 | C_s1_d2 | 1.11 | 16.6 | 34.5 | 855 | 62.4 | C | 31.5 | 0.07 | s1 | n | y | d2
TN_2020_2595 |  | 80739 20352259 | 812030S | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.41 | 14 | Vilanova | 0.50400+1.2416HD | CD | 75 | 11.57 | No | 2020-12-01 | B2_s1_d1 | 0.75 | 11.4 | 22.3 | 861 | 51.4 | B2 | 14.3 | 0.04 | s1 | y | n | d1
TN_2020_2596 |  | 80173 20352259 | 824311R | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.32 | 14 | Vilanova | 0.51420+1.2416HD | CD | 75 | 11.72 | No | 2020-12-01 | C_s1_d2 | 1.51 | 23.6 | 38.9 | 885 | 72.2 | C | 31.4 | 0.06 | s1 | n | y | d2
TN_2020_2597 |  | 80739 20352259 | 812030S | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.41 | 14 | Vilanova | 0.50400+1.2416HD | CD | 70 | 14.53 | No | 2020-12-01 | B2_s1_d1 | 0.69 | 9.9 | 18.9 | 840 | 43.6 | B2 | 18.2 | 0.03 | s1 | y | n | d1
TN_2020_2598 |  | 79292 20235174 | 802943P | HEPRZ1(AS) 26/45KV 1X300K AL+H75 | 51.68 | 4 | Vilanova | 14202.5MM+61AA3.2MM | CD | 70 | 17.42 | No | 2020-12-01 | B2_s1_d0 | 0.88 | 12.4 | 17.6 | 1500 | 25.9 | B2 | 8.8 | 0.02 | s1 | n | n | d0
TN_2020_2601 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 75 | 11.73 | No | 2020-12-02 | B2_s1_d2 | 0.77 | 14.1 | 25.8 | 846 | 47.2 | B2 | 32.7 | 0.06 | s1 | n | y | d2
TN_2020_2602 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 70 | 12.06 | No | 2020-12-02 | C_s1_d1 | 1.19 | 19.3 | 30.2 | 942 | 50.8 | C | 27.1 | 0.07 | s1 | y | n | d1
TN_2020_2603 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 70 | 13.24 | No | 2020-12-02 | C_s1_d2 | 1.21 | 19.5 | 32.5 | 936 | 52.5 | C | 26.8 | 0.09 | s1 | n | y | d2
TN_2020_2604 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 70 | 17.32 | No | 2020-12-02 | C_s1_d1 | 1.66 | 26 | 38.1 | 1212 | 65.4 | C | 42.3 | 0.1 | s1 | y | n | d1
TN_2020_2608 |  |  | 5096960 8096962 5096971 | AFUMEX CLASS 750V H07Z-1-K (AS) TYPE 2 1X25 CCAS1BD1 | 8.97 | 17 | Vilanova | REFENCESAMPLE | CD | 70 | 8.32 | No | 2020-12-03 | B2_s1_d0 | 0.36 | 4.9 | 10.2 | 633 | 40.7 | B2 | 5.5 | 0.01 | s1 | n | n | d0
TN_2020_2609 |  |  | 5096968 5096970 | AFUMEX CLASS 750V H07Z-1-K (AS) TYPE 2 1X25 CCAS1BD1 | 8.97 | 17 | Vilanova | REFENCESAMPLE | CD | 70 | 8.63 | No | 2020-12-03 | B2_s1_d0 | 0.34 | 4.7 | 9 | 546 | 49.7 | B2 | 6.8 | 0.01 | s1 | n | n | d0
TN_2020_2610 |  | 20078005 | 588957W | HEPRZ1(AS) 132KV 1X800K AL+H280 EPROTENAX | 94.8 | 2 | Vilanova | DMZ-26000SEES+LE0563@70%+DMZ-E@30% | CD | 70 | 10.01 | No | 2020-12-03 | B2_s1_d2 | 0.76 | 11.6 | 16.3 | 1497 | 30.8 | B2 | 6.4 | 0.01 | s1 | n | y | d2
TN_2020_2611 |  |  | 5096963 | AFUMEX CLASS 750V H07Z-1-K (AS) TYPE 2 1X25 CCAS1BD1 | 8.97 | 17 | Vilanova | REFENCESAMPLE | CD | 70 | 14.97 | No | 2020-12-03 | B2_s1_d0 | 0.56 | 4.2 | 10.2 | 624 | 40.8 | B2 | 17.1 | 0.02 | s1 | n | n | d0
TN_2020_2612 |  | 80128 20328397 | 831810S | H07Z1-K 750V (AS) 1X240 | 24.15 | 7 | Vilanova | TPR-56 | CD | 70 | 18.01 | No | 2020-12-03 | B2_s1_d1 | 0.42 | 5.5 | 8.8 | 648 | 26.1 | B2 | 6.3 | 0.01 | s1 | y | n | d1
TN_2020_2613 |  | 20173170 | 733675Y | RHZ1-RA+2OL (AS) 66KV 1X1000K AL+H135 | 74.71 | 3 | Vilanova | 61AASEES+CABELEC381770%+DMZ-330% | CD | 75 | 11.48 | No | 2020-12-10 | B2_s1_d0 | 0.66 | 9.1 | 12.3 | 1125 | 23 | B2 | 2.8 | 0.01 | s1 | n | n | d0
TN_2020_2614 |  | 20193677 83931485 | 825569H | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.86 | 13 | Vilanova | PE+KRAFT+1420+1602 | CD | 75 | 11.64 | No | 2020-12-10 | D_s1_d2 | 3.3 | 47.5 | 117 | 1500 | 97.5 | D | 38.9 | 0.09 | s1 | n | y | d2
TN_2020_2615 |  | 80774 20329100 | 637164V | TSLI(F) 145KV 1X400 AI2 H70 | 75.9 | 3 | Vilanova | 61AASEES+CABELEC381770%+DMZ-E30% | CD | 70 | 12.41 | No | 2020-12-10 | B2_s1_d0 | 0.69 | 11.4 | 15.3 | 1059 | 24.4 | B2 | 10.7 | 0.04 | s1 | n | n | d0
TN_2020_2616 |  | 20193661 83166709 | 601377W | AFUMEX CLASS 1KV RZ1-K (AS) 4X10 | 17.5 | 8 | Vilanova | 1420+1602 | CD | 70 | 14.31 | No | 2020-12-10 | B2_s1_d2 | 0.97 | 12.9 | 26.6 | 1488 | 26.1 | B2 | 7.7 | 0.03 | s1 | n | y | d2
TN_2020_2617 |  | 20302916 | 818349K | EXZH COMPACT RZ1-K (AS) CCA 1KV 4X10 | 15.87 | 9 | Vilanova | PE/TPR+OLI+TPR-49+TPR-54 | CD | 70 | 18.52 | No | 2020-12-10 | B2_s1_d2 | 0.9 | 10.1 | 21.8 | 1464 | 18.8 | B2 | 16.2 | 0.03 | s1 | n | y | d2
TN_2020_2618 |  | 20302899 | 738435X | EXZH COMPACT RZ1-K (AS) CCA 1KV 3G1.5 | 9.62 | 15 | Vilanova | PE/TPR+OLI+TPR-49+TPR-54 | CD | 75 | 11.81 | No | 2020-12-11 | C_s1_d2 | 1.5 | 16.2 | 28.5 | 921 | 59.1 | C | 32.8 | 0.12 | s1 | n | y | d2
TN_2020_2619 |  | 20302921 | 792744D | EXZH COMPACT RZ1-K (AS) CCA 1KV 5G1.5 | 12.4 | 13 | Vilanova | PE/TPR+OLI+TPR-49+TPR-54 | CD | 75 | 12.24 | No | 2020-12-11 | C_s1_d0 | 1.53 | 18.8 | 26.1 | 1134 | 45.1 | C | 30.7 | 0.1 | s1 | n | n | d0
TN_2020_2620 |  | 20193654 83797265 | 779158L | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.36 | 15 | Vilanova |  | CD | 75 | 12.09 | No | 2020-12-11 | D_s1_d0 | 2.12 | 27.5 | 43.5 | 915 | 76.1 | D | 37.5 | 0.08 | s1 | n | n | d0
TN_2020_2621 |  | 203028141 | 5096521 | EXZHELLENT CLASS H07Z1-K 750V 1.5 | 2.92 | 165 | Vilanova | 1602/TPR-53 | CD | 75 | 17.34 | No | 2020-12-11 | D_s1_d0 | 3.3 | 49.2 | 107.6 | 975 | 159.3 | D | 20.8 | 0.05 | s1 | n | n | d0
TN_2020_2622 |  | 20193653 83956864 | T9 F90294 | AFUMEX CLASS 1KV RZ1-K (AS) 2X16 | 16.8 | 9 | Vilanova | 16AASEIT+0300FEIT | CD | 75 | 14.46 | No | 2020-12-11 | B2_s1_d1 | 0.31 | 3.1 | 5.2 | 660 | 17 | B2 | 1.9 | 0 | s1 | y | n | d1
TN_2020_2623 |  | 20193653 83956864 | T9 F90294 | AFUMEX CLASS 1KV RZ1-K (AS) 2X16 | 16.8 | 9 | Vilanova | 16AASEIT+0300FEIT | CD | 75 | 19.05 | No | 2020-12-11 | B2_s1_d0 | 0.43 | 5.6 | 9.6 | 1380 | 15.7 | B2 | 17.8 | 0.04 | s1 | n | n | d0
TN_2020_2624 |  | 80486 20343785 | 823337G | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 BEDDING FREE | 9.4 | 17 | Vilanova | TPR-54AMBINNEOSCLAYG-1 | CD | 75 | 18.17 | No | 2020-12-11 | D_s2_d2 | 3.3 | 57.1 | 119.4 | 1497 | 99.7 | D | 72.3 | 0.3 | s2 | n | y | d2
TN_2020_2625 |  | 80484 20343748 | 823358E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 10.9 | 14 | Vilanova | TPR-54AMBINNEOSCLAYG-1 | CD | 75 | 14.89 | No | 2020-12-11 | D_s2_d2 | 3.3 | 63.6 | 169.1 | 1488 | 142.4 | D | 80.8 | 0.33 | s2 | n | y | d2
TN_2020_2626 |  | 80483 20343748 | 823301T | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 10.84 | 14 | Vilanova | TPR-54AMBINNEOSCLAYSIL-1 | CD | 75 | 14.29 | No | 2020-12-11 | D_s1_d1 | 3.3 | 34.8 | 49.6 | 1017 | 69.7 | D | 45.2 | 0.1 | s1 | y | n | d1
TN_2020_2627 |  | 80485 20343785 | 823335E | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 BEDDING FREE | 9.41 | 17 | Vilanova | TPR-54AMBINNEOSCLAYSIL-1 | CD | 75 | 14.72 | No | 2020-12-11 | D_s2_d2 | 3.3 | 59.8 | 128 | 1458 | 110.5 | D | 88.1 | 0.34 | s2 | n | y | d2
TN_2020_2628 |  | 80809 20352258 | 838316N | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.24 | 15 | Vilanova | 04000.5MM+16HD | CD | 70 | 10.3 | No | 2020-11-13 | B2_s1_d2 | 0.83 | 9 | 21.6 | 783 | 44.7 | B2 | 15.3 | 0.04 | s1 | n | y | d2
TN_2020_2629 |  | 80496 20349178 | 824578F | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.35 | 14 | Vilanova | 04000.5MM+16HD | CD | 70 | 10.31 | No | 2020-11-13 | B2_s1_d0 | 0.59 | 6.8 | 13.6 | 774 | 34.9 | B2 | 11.7 | 0.02 | s1 | n | n | d0
TN_2020_2630 |  | 80809 20352258 | 838316N | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.24 | 15 | Vilanova | 04000.5MM+16HD | CD | 70 | 17.49 | No | 2020-11-13 | B2_s1_d1 | 0.72 | 7.1 | 20.7 | 717 | 49.7 | B2 | 10 | 0.02 | s1 | y | n | d1
TN_2020_2631 |  | 80496 20349178 | 824578F | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.35 | 14 | Vilanova | 04000.5MM+16HD | CD | 70 | 10.73 | No | 2020-11-13 | B2_s1_d2 | 0.82 | 8.8 | 22 | 909 | 37.1 | B2 | 23.1 | 0.06 | s1 | n | y | d2
TN_2020_2633 |  |  | 5096966 | AFUMEX CLASS 750V H07Z-1-K (AS) TYPE 2 1X25 CCAS1BD1 | 8.81 | 17 | Vilanova | REFENCESAMPLE | CD | 70 | 18.33 | No | 2020-12-16 | B2_s1_d0 | 0.31 | 1.2 | 4.4 | 516 | 20.3 | B2 | 0.3 | 0 | s1 | n | n | d0
TN_2020_2634 |  |  | 5096969 | AFUMEX CLASS 750V H07Z-1-K (AS) TYPE 2 1X25 CCAS1BD1 | 8.81 | 17 | Vilanova | REFENCESAMPLE | CD | 70 | 14.23 | No | 2020-12-16 | B2_s1_d0 | 0.4 | 2.4 | 7.8 | 606 | 30.8 | B2 | 2.5 | 0.01 | s1 | n | n | d0
TN_2020_2635 |  |  |  | AFUMEX CLASS 750V H07Z-1-K (AS) TYPE 2 1X25 CCAS1BD1 | 8.81 | 17 | Vilanova | REFENCESAMPLE | CD | 70 | 13.44 | No | 2020-12-16 | B2_s1_d0 | 0.37 | 1.8 | 5.6 | 552 | 22.6 | B2 | 1.2 | 0 | s1 | n | n | d0
TN_2020_2636 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 70 | 13.16 | No | 2020-12-17 | B2_s1_d1 | 0.95 | 12 | 19 | 894 | 36.3 | B2 | 16.8 | 0.03 | s1 | y | n | d1
TN_2020_2637 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 70 | 13.41 | No | 2020-12-17 | B2_s1_d1 | 1.09 | 12.7 | 22.1 | 855 | 41.4 | B2 | 22.7 | 0.05 | s1 | y | n | d1
TN_2020_2638 |  | 20302822 | 5096522 | EXZHELLENT CLASS H07Z1-K 750V 2.5 NE | 3.58 | 105 | Vilanova | 1602/TPR-53 | CD | 70 | 13.57 | No | 2020-12-17 | C_s2_d0 | 1.92 | 13.1 | 25.3 | 741 | 73.1 | C | 64.3 | 0.16 | s2 | n | n | d0
TN_2020_2639 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 70 | 17.39 | No | 2020-12-17 | C_s1_d0 | 1.33 | 17.4 | 33.9 | 846 | 69.2 | C | 39.7 | 0.12 | s1 | n | n | d0
TN_2020_2640 |  | 80809 20352258 | 838316N | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.24 | 15 | Vilanova | 04000.5MM+16HD | CD | 70 | 16.83 | No | 2020-12-17 | B2_s1_d1 | 0.39 | 6.3 | 16.3 | 753 | 42.8 | B2 | 6.2 | 0.02 | s1 | y | n | d1
TN_2020_2641 |  | 80493 20349178 | 824578F | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.35 | 24 | Vilanova | 04000.5MM+16HD | CD | 70 | 16.86 | No | 2020-12-17 | B2_s1_d1 | 0.32 | 4.3 | 12 | 741 | 28.3 | B2 | 8.2 | 0.03 | s1 | y | n | d1
TN_2020_2642 |  | 80484 20343748 | 823358E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 10.9 | 14 | Vilanova | TPR-54AMBINNEOSCLAYG-1 | CD | 85 | 14 | No | 2020-12-18 | D_s2_d1 | 2.56 | 32.5 | 45.4 | 1236 | 63.4 | D | 51.6 | 0.1 | s2 | y | n | d1
TN_2020_2643 |  | 80486 20343785 | 823337G | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 BEDDING FREE | 9.4 | 17 | Vilanova | TPR-54AMBINNEOSCLAYG-1 | CD | 85 | 14.28 | No | 2020-12-18 | D_s2_d1 | 3.3 | 52 | 102.9 | 1500 | 97.8 | D | 72.5 | 0.15 | s2 | y | n | d1
TN_2020_2644 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 85 | 14.74 | No | 2020-12-18 | C_s1_d0 | 1.31 | 17.4 | 32.6 | 837 | 63 | C | 29.6 | 0.1 | s1 | n | n | d0
TN_2020_2645 |  | 80485 20343785 | 823335E | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 BEDDING FREE | 9.41 | 17 | Vilanova | TPR-54AMBINNEOSCLAYSIL-1 | CD | 80 | 15.2 | No | 2020-12-18 | D_s2_d2 | 3.1 | 37.8 | 50.2 | 1494 | 72.9 | D | 54.2 | 0.09 | s2 | n | y | d2
TN_2020_2646 |  | 20193987 | 5096523 | AFUMEX CLASS 750V H07Z1-K (AS) 2.5 | 3.39 | 120 | Vilanova | 1602/1510 | CD | 85 | 15.58 | No | 2020-12-18 | C_s2_d0 | 1.84 | 15.2 | 33.1 | 714 | 95.2 | C | 57.5 | 0.13 | s2 | n | n | d0
TN_2020_2647 |  | 84017485 20193690 | 840095X | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 12.12 | 13 | Vilanova | 0400+1602 | CD | 70 | 17.05 | No | 2020-12-18 | C_s1_d2 | 1.17 | 15.6 | 23.9 | 963 | 40.2 | C | 34.7 | 0.09 | s1 | n | y | d2
TN_2020_2648 |  | 83997679 20193679 | 840132M | AFUMEX CLASS 1KV RZ1-K (AS) 5G4 | 14.85 | 10 | Vilanova | 0400+1602 | CD | 84 | 17.78 | No | 2020-12-18 | C_s1_d2 | 1.3 | 24.3 | 37.1 | 1059 | 48.9 | C | 22.1 | 0.04 | s1 | n | y | d2
TN_2020_2649 |  | 80810 20352260 | 821049V | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.95 | 13 | Vilanova | PP+0400+16HD | CD | 84 | 17.15 | No | 2020-12-18 | C_s1_d1 | 1.36 | 20.5 | 40.4 | 801 | 83.9 | C | 26.9 | 0.04 | s1 | y | n | d1
TN_2020_2650 |  | 84017470 20193656 | 840134P | AFUMEX CLASS 1KV RZ1-K (AS) 3G4 | 12.72 | 12 | Vilanova | 0400+1602 | CD | 84 | 16.05 | No | 2020-12-18 | B2_s1_d1 | 0.69 | 11.2 | 20 | 963 | 35.2 | B2 | 20.5 | 0.03 | s1 | y | n | d1
TN_2020_2651 |  | 84017470 20193656 | 840134P | AFUMEX CLASS 1KV RZ1-K (AS) 3G4 | 12.72 | 12 | Vilanova | 0400+1602 | CD | 75 | 12.86 | No | 2020-12-20 | B2_s1_d1 | 0.67 | 10.3 | 18.5 | 900 | 37.9 | B2 | 23.7 | 0.05 | s1 | y | n | d1
TN_2020_2652 |  | 83997679 20193679 | 840132M | AFUMEX CLASS 1KV RZ1-K (AS) 5G4 | 14.85 | 10 | Vilanova | 0400+1602 | CD | 75 | 13.03 | No | 2020-12-20 | C_s1_d2 | 1.19 | 18.3 | 27 | 1104 | 35.7 | C | 18.3 | 0.05 | s1 | n | y | d2
TN_2020_2653 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 70 | 14.57 | No | 2020-12-20 | C_s1_d2 | 1.12 | 16.9 | 30.4 | 864 | 54.2 | C | 23.1 | 0.06 | s1 | n | y | d2
TN_2020_2654 |  | 84017485 20193690 | 840095X | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 12.12 | 13 | Vilanova | 0400+1602 | CD | 70 | 17.62 | No | 2020-12-20 | C_s2_d2 | 1.46 | 20.1 | 34.3 | 990 | 52.8 | C | 50.4 | 0.1 | s2 | n | y | d2
TN_2020_2655 |  | 80810 20352260 | 821049V | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.95 | 13 | Vilanova | PP+0400+16HD | CD | 70 | 20.15 | No | 2020-12-20 | C_s1_d2 | 1.21 | 18.5 | 36 | 798 | 79.6 | C | 39.7 | 0.08 | s1 | n | y | d2
TN_2020_2657 |  | 80493 20349178 | 824578F | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.35 | 24 | Vilanova | 04000.5MM+16HD | CD | 75 | 10.62 | No | 2020-12-21 | B2_s1_d2 | 0.69 | 10.8 | 23.4 | 882 | 44.3 | B2 | 18 | 0.04 | s1 | n | y | d2
TN_2020_2658 |  |  | 5096691 | F/UTP5E P6 CCA | 6.03 | 25 | Vilanova | LSHFINSULATION+CONGUARDS66500.6MM | CD | 75 | 10.65 | No | 2020-12-21 | B2_s1_d0 | 0.32 | 2.4 | 11.3 | 447 | 83.4 | B2 | 4.7 | 0.02 | s1 | n | n | d0
TN_2020_2659 |  |  | 5096693 | F/UTP5E P5 CCA | 6.49 | 25 | Vilanova | CONGUARDS6650SHEATH0.80MM | CD | 70 | 13.41 | No | 2020-12-21 | B2_s1_d0 | 1.2 | 7.3 | 24.4 | 513 | 135.4 | B2 | 20.8 | 0.06 | s1 | n | n | d0
TN_2020_2660 |  |  | 5096692 | U/UTP5E P6 CCA | 5.22 | 30 | Vilanova | CONGUARDS6650SHEATH0.65MM | CD | 70 | 16.89 | No | 2020-12-21 | D_s1_d0 | 2.69 | 12.8 | 29 | 549 | 149.9 | D | 47.8 | 0.1 | s1 | n | n | d0
TN_2020_2661 |  |  | 5096696 | F/UTP5E P4 CCA | 6.3 | 25 | Vilanova | CONGUARDS6650SHEATH0.65MM | CD | 70 | 18.58 | No | 2020-12-21 | B2_s1_d0 | 0.31 | 2.6 | 10.5 | 429 | 83 | B2 | 7.1 | 0.02 | s1 | n | n | d0
TN_2020_2662 |  |  | 5096694 | U/UTP5E P5 CCA | 5.21 | 30 | Vilanova | CONGUARDS6650SHEATH0.80MM | CD | 60 | 17.81 | No | 21/12/202 | B2_s1_d1 | 1.01 | 5.3 | 15.8 | 555 | 99.6 | B2 | 10.2 | 0.03 | s1 | y | n | d1
TN_2020_2663 |  | 79338 20348075 | 795124R | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 11 | 14 | Vilanova | TPR-54 | CD | 70 | 16.77 | No | 2020-12-21 | D_s2_d2 | 3.3 | 61.4 | 194.3 | 1500 | 161.9 | D | 106.3 | 0.44 | s2 | n | y | d2
TN_2020_2665 |  | 80180 20352260 | 824601F | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.94 | 13 | Vilanova | 0400+16HDHYDRO | CD | 70 | 11.37 | No | 2020-12-22 | C_s1_d1 | 1.11 | 16.9 | 31.5 | 834 | 63.1 | C | 35.3 | 0.08 | s1 | y | n | d1
TN_2020_2666 |  | 80180 20352260 | 829710J | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.28 | 13 | Vilanova | 0400+16HDHYDRO | CD | 70 | 11.4 | No | 2020-12-22 | B2_s1_d2 | 0.74 | 10.5 | 20.3 | 939 | 39.4 | B2 | 18.1 | 0.03 | s1 | n | y | d2
TN_2020_2667 |  | 80179 20352260 | 829704C | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.95 | 13 | Vilanova | 0400+16HDECO | CD | 70 | 13.37 | No | 2020-12-22 | B2_s1_d1 | 0.94 | 13.3 | 27.5 | 816 | 55.5 | B2 | 26.9 | 0.07 | s1 | y | n | d1
TN_2020_2668 |  | 80180 20352260 | 824601F | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.94 | 13 | Vilanova | 0400+16HDHYDRO | CD | 70 | 17.71 | No | 2020-12-22 | B2_s1_d1 | 1.03 | 14 | 27.3 | 852 | 49.5 | B2 | 36 | 0.05 | s1 | y | n | d1
TN_2020_2669 |  | 80180 20352260 | 829710J | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.28 | 13 | Vilanova | 0400+16HDHYDRO | CD | 70 | 19.8 | No | 2020-12-22 | C_s1_d2 | 1.08 | 15.8 | 31.1 | 864 | 58.1 | C | 32.7 | 0.06 | s1 | n | y | d2
TN_2020_2670 |  | 84089224 20193658 | T1-H88280 | AFUMEX CLASS 1KV RZ1-K (AS) 3G10 | 15.41 | 10 | Vilanova | 0300FEIT+16AASEIT | CD | 70 | 21 | No | 2020-12-22 | B2_s1_d1 | 0.41 | 5.8 | 9.9 | 1242 | 20.5 | B2 | 4.2 | 0.01 | s1 | y | n | d1
TN_2020_2671 |  | 84089224 20193658 | T1-H88280 | AFUMEX CLASS 1KV RZ1-K (AS) 3G10 | 15.41 | 10 | Vilanova | 0300FEIT+16AASEIT | CD | 70 | 20.44 | No | 2020-12-22 | B2_s1_d1 | 0.33 | 4.7 | 6.7 | 1443 | 18.8 | B2 | 0.7 | 0 | s1 | y | n | d1
TN_2020_2672 |  | 80179 20352260 | 829704C | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.95 | 13 | Vilanova | 0400+16HDECO | CD | 70 | 18.41 | No | 2020-12-22 | C_s1_d2 | 1.12 | 15.6 | 28.5 | 813 | 60.2 | C | 17.2 | 0.03 | s1 | n | y | d2
TN_2020_2673 |  | 79336 20343748 | 795123P | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 10.52 | 14 | Vilanova | TPR-54 | CD | 70 | 16.4 | No | 2020-12-22 | D_s2_d2 | 3.3 | 42.4 | 77.9 | 1497 | 73.9 | D | 78.6 | 0.17 | s2 | n | y | d2
TN_2020_2675 |  | 84009551 20193677 | 840165Y | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.69 | 12 | Vilanova | 0400+1602 | CD | 70 | 14 | No | 2020-12-23 | D_s1_d2 | 2.07 | 32.1 | 44.1 | 1143 | 68.2 | D | 40.4 | 0.1 | s1 | n | y | d2
TN_2020_2676 |  | 84009551 20193677 | 840165Y | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.69 | 12 | Vilanova | 0400+1602 | CD | 70 | 14.85 | No | 2020-12-23 | C_s1_d2 | 1.92 | 28.5 | 41.1 | 1062 | 70.1 | C | 32.7 | 0.08 | s1 | n | y | d2
TN_2021_2677 |  | 79935 20343785 | 789476B | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 BEDDING FREE | 9.01 | 17 | Vilanova | TPR-54 | CD | 70 | 4.69 | No | 2021-01-08 | B2_s1_d1 | 0.68 | 11.6 | 21 | 789 | 64.3 | B2 | 24 | 0.09 | s1 | y | n | d1
TN_2021_2678 |  | 79935 20343785 | 789476B | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 BEDDING FREE | 9.01 | 17 | Vilanova | TPR-54 | CD | 70 | 5.61 | No | 2021-01-08 | C_s1_d0 | 1.53 | 13.5 | 18.4 | 672 | 60.6 | C | 40.9 | 0.07 | s1 | n | n | d0
TN_2021_2679 |  | 79336 20343748 | 795123P | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 10.52 | 14 | Vilanova | TPR-54 | CD | 70 | 6.6 | No | 2021-01-08 | B2_s1_d2 | 0.62 | 9.7 | 21.3 | 696 | 53.9 | B2 | 24.6 | 0.05 | s1 | n | y | d2
TN_2021_2680 |  | 80774 20329100 | 637164V | TSLI(F) 145KV 1X400 AI2 H70 | 75.9 | 3 | Vilanova | 61AASEES+CABELEC381770%+DMZ-E30% | CD | 70 | 7.48 | No | 2021-01-08 | C_s1_d2 | 0.92 | 15.5 | 21.1 | 1092 | 35.1 | C | 25.4 | 0.08 | s1 | n | y | d2
TN_2021_2681 |  | 79338 20348075 | 795124R | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 11 | 14 | Vilanova | TPR-54 | CD | 70 | 8.56 | No | 2021-01-08 | D_s2_d2 | 3.3 | 41.9 | 76.5 | 1494 | 66.5 | D | 93 | 0.19 | s2 | n | y | d2
TN_2021_2682 |  | 79935 20343785 | 789476B | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 BEDDING FREE | 9.01 | 17 | Vilanova | TPR-54 | CD | 70 | 10.3 | No | 2021-01-08 | C_s1_d1 | 1.75 | 17 | 21.6 | 759 | 76.6 | C | 29.7 | 0.06 | s1 | y | n | d1
TN_2021_2683 |  | 79336 20343748 | 795123P | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 10.52 | 14 | Vilanova | TPR-54 | CD | 70 | 9.54 | No | 2020-01-08 | C_s1_d2 | 1.94 | 24.1 | 30.8 | 1032 | 60.2 | C | 49.7 | 0.08 | s1 | n | y | d2
TN_2021_2684 |  | 79338 20348075 | 795124R | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 BEDDING FREE | 11 | 14 | Vilanova | TPR-54 | CD | 70 | 9.01 | No | 2020-01-08 | D_s2_d1 | 2.14 | 30.2 | 49.8 | 1482 | 59.8 | D | 52.7 | 0.11 | s2 | y | n | d1
TN_2021_2685 |  | 20302899 | 738435X | EXZH COMPACT RZ1-K (AS) CCA 1KV 3G1.5 | 9.62 | 15 | Vilanova | PE/TPR+OLI+TPR-49+TPR-54 | CD | 80 | 5.65 | No | 2021-01-09 | B2_s1_d0 | 0.56 | 8.8 | 15.2 | 681 | 48.4 | B2 | 10.9 | 0.03 | s1 | n | n | d0
TN_2021_2686 |  | 20302921 | 792744D | EXZH COMPACT RZ1-K (AS) CCA 1KV 5G1.5 | 12.4 | 13 | Vilanova | PE/TPR+OLI+TPR-49+TPR-54 | CD | 80 | 6.18 | No | 2021-01-09 | B2_s1_d0 | 0.75 | 11.5 | 22.6 | 780 | 49.8 | B2 | 28.7 | 0.05 | s1 | n | n | d0
TN_2021_2687 |  | 20193654 83797265 | 779158L | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.36 | 15 | Vilanova | PE+KRAFT+1420+1602 | CD | 80 | 7.83 | No | 2021-01-09 | D_s1_d0 | 2.07 | 27.9 | 37.6 | 1041 | 69.5 | D | 44.5 | 0.1 | s1 | n | n | d0
TN_2021_2688 |  | 20173170 | 733675Y | RHZ1-RA+2OL (AS) 66KV 1X1000K AL+H135 | 74.71 | 3 | Vilanova | 61AASEES+CABELEC381770%+DMZ-330% | CD | 80 | 8.26 | No | 2021-01-09 | B2_s1_d0 | 0.63 | 9.9 | 12.3 | 1092 | 30.1 | B2 | 2.4 | 0.01 | s1 | n | n | d0
TN_2021_2689 |  | 203028141 | 5096521 | EXZHELLENT CLASS H07Z1-K 750V 1.5 | 2.92 | 165 | Vilanova | 1602/TPR-53 | CD | 70 | 6.41 | No | 2021-01-11 | D_s2_d0 | 3.3 | 51.4 | 83.5 | 1062 | 147.3 | D | 56.1 | 0.1 | s2 | n | n | d0
TN_2021_2690 |  | 20193661 83166709 | 601377W | AFUMEX CLASS 1KV RZ1-K (AS) 4X10 | 17.5 | 8 | Vilanova | 1420+1602 | CD | 70 | 6.38 | No | 2021-01-11 | B2_s1_d2 | 0.76 | 11.5 | 22.3 | 1380 | 27 | B2 | 10.1 | 0.03 | s1 | n | y | d2
TN_2021_2691 |  | 20193987 | 5096523 | AFUMEX CLASS 750V H07Z1-K (AS) 2.5 | 3.39 | 120 | Vilanova | 1602/1510 | CD | 70 | 7.38 | No | 2021-01-11 | B2_s1_d0 | 1.1 | 7.7 | 18.9 | 606 | 74.5 | B2 | 34.6 | 0.12 | s1 | n | n | d0
TN_2021_2692 |  | 20302916 | 818349K | EXZH COMPACT RZ1-K (AS) CCA 1KV 4X10 | 15.87 | 9 | Vilanova | PE/TPR+OLI+TPR-49+TPR-54 | CD | 60 | 10.6 | No | 2021-01-11 | B2_s1_d1 | 0.68 | 9.4 | 13.6 | 1218 | 20 | B2 | 15.6 | 0.02 | s1 | y | n | d1
TN_2021_2693 |  | 20193677 83931485 | 825569H | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.86 | 13 | Vilanova | PE+KRAFT+1420+1602 | CD | 60 | 13.09 | No | 2021-01-11 | D_s1_d0 | 2.9 | 39.5 | 62.7 | 1497 | 80 | D | 43.2 | 0.08 | s1 | n | n | d0
TN_2021_2694 |  |  | 5096666 | 4.F/UTP6 CCA PROTO D (0.55) | 7.03 | 21 | Vilanova | BAINHACONGUARDS66500.55 | CD | 70 | 4.69 | No | 2021-01-12 | D_s2_d1 | 3.3 | 37.9 | 167.8 | 849 | 313.5 | D | 117.2 | 0.47 | s2 | y | n | d1
TN_2021_2695 |  |  | 5096668 | F/UTP5E 4P 24AWG LSHF / LSHRFR | 7.66 | 19 | Vilanova | BAINHADUBLATPR-32+CONGUARDS66500.75 | CD | 60 | 7.44 | No | 2021-01-12 | C_s1_d1 | 1.8 | 19.2 | 43.4 | 612 | 144.3 | C | 48.1 | 0.1 | s1 | y | n | d1
TN_2021_2696 |  |  | 5096696 | F/UTP 5E 4P 24AWG | 6.3 | 25 | Vilanova | CONGUARDS6650SHEATH0.65MM | CD | 60 | 10.54 | No | 2021-01-12 | B2_s1_d1 | 0.69 | 3.2 | 15.2 | 462 | 100.3 | B2 | 14.9 | 0.05 | s1 | y | n | d1
TN_2021_2697 |  |  | 5096508 | U/UTP 6 4P 24AWG | 5.75 | 25 | Vilanova | LSHFSKIN+S6650SHEATH0.55MM | CD | 60 | 13.46 | No | 2021-01-12 | B2_s1_d0 | 1.27 | 4.2 | 14.1 | 594 | 72.9 | B2 | 17.3 | 0.05 | s1 | n | n | d0
TN_2021_2698 |  |  | 5096667 | 4.F/UTP6 CCA PROTO E (0.55) | 7.6 | 19 | Vilanova | BAINHACONGUARDS66500.65 | CD | 70 | 6.26 | No | 2021-01-13 | D_s2_d2 | 3.3 | 39.3 | 144.4 | 903 | 242.7 | D | 129.1 | 0.45 | s2 | n | y | d2
TN_2021_2699 |  |  | 5096666 | F/UTP 6 4P 23AWG | 7.03 | 21 | Vilanova | BAINHACONGUARDS66500.55 | CD | 60 | 8.93 | No | 2021-01-13 | C_s1_d1 | 1.78 | 12.6 | 30.6 | 564 | 141.1 | C | 34.3 | 0.07 | s1 | y | n | d1
TN_2021_2700 |  | 20173170 | 733675Y | RHZ1-RA+2OL (AS) 66KV 1X1000K AL+H135 | 74.71 | 3 | Vilanova | 61AASEES+CABELEC381770%+DMZ-330% | CD | 60 | 12.42 | No | 2021-01-13 | B2_s1_d0 | 0.63 | 8 | 11.5 | 840 | 24 | B2 | 13.7 | 0.03 | s1 | n | n | d0
TN_2021_2701 |  | 80774 20329100 | 637164V | TSLI(F) 145KV 1X400 AI2 H70 | 75.9 | 3 | Vilanova | 61AASEES+CABELEC381770%+DMZ-E30% | CD | 60 | 15.47 | No | 2021-01-13 | C_s1_d1 | 0.87 | 15.6 | 21 | 1152 | 33 | C | 17.5 | 0.05 | s1 | y | n | d1
TN_2021_2702 |  | 20302822 | 5096522 | EXZHELLENT CLASS H07Z1-K 750V 2.5 NE | 3.58 | 105 | Vilanova | 1602/TPR-53 | CD | 70 | 7.22 | No | 2021-01-14 | D_s2_d0 | 2.12 | 18 | 30.3 | 849 | 71 | D | 69.4 | 0.16 | s2 | n | n | d0
TN_2021_2703 |  | 20303007 80024 | 735737P | PRYSUN SOLAR INT +SOLAR EXT 6MM2 | 6.23 | 25 | Vilanova | VICOM | CD | 70 | 7.5 | No | 2021-01-14 | D_s2_d2 | 3.3 | 32.5 | 49.4 | 648 | 154.2 | D | 52 | 0.07 | s2 | n | y | d2
TN_2021_2704 |  | 20303007 80024 | 735737P | PRYSUN SOLAR INT +SOLAR EXT 6MM2 | 6.23 | 25 | Vilanova | VICOM | CD | 60 | 9.85 | No | 2021-01-14 | D_s1_d2 | 3.3 | 23.5 | 35.3 | 681 | 105.5 | D | 36.4 | 0.05 | s1 | n | y | d2
TN_2021_2705 |  | 20221312 | T6-F82189 5096538 | FG18OM16 AFUMEX GOLD 1KV 3X2.5 | 14.21 | 11 | Vilanova |  | CD | 60 | 13.41 | No | 2021-01-14 | B2_s1_d2 | 0.54 | 5.6 | 9 | 939 | 42.3 | B2 | 12.5 | 0.02 | s1 | n | y | d2
TN_2021_2706 |  | 20154478 | T6-F82189 5096535 | FG18OM16 AFUMEX GOLD 1KV 3X1.5 | 13.79 | 11 | Vilanova |  | CD | 60 | 15.69 | No | 2021-01-14 | B2_s1_d2 | 0.44 | 5.7 | 11 | 1500 | 59.1 | B2 | 7.7 | 0.02 | s1 | n | y | d2
TN_2021_2707 | Portugal | 84000751 20294067 | 837730B | TXXI 1KV 1X300 DCA-S2.D2.A2 | 28.58 | 6 | Vilanova | INSULATION:PRS-03;SHEATH:TPR-55 | CD | 70 | 19.15 | No | 2021-01-14 | B2_s1_d0 | 0.35 | 7.2 | 13.9 | 1494 | 21.3 | B2 | 8 | 0.01 | s1 | n | n | d0
TN_2021_2708 |  | 75866 20220758 | 832343W | CCTSST FR 0.1 1X4X1.4 | 16.51 | 9 | Vilanova | TPR-DOUBLESTEELTAPE+1420FEES+TPR55 | CD | 60 | 17.2 | No | 2021-01-14 | B2_s1_d2 | 0.46 | 9.4 | 14.6 | 1320 | 21.5 | B2 | 6.2 | 0.02 | s1 | n | y | d2
TN_2021_2709 |  | 83971386 20310444 | 843402S | TXXI 1KV 1X240 DCA-S2.D2.A2 | 24.89 | 7 | Vilanova | INSULATION:PRS-03;SHEATH:TPR-55 | CD | 60 | 12.16 | No | 2021-01-14 | B2_s1_d0 | 0.52 | 6 | 12.7 | 1497 | 16.9 | B2 | 2.3 | 0.01 | s1 | n | n | d0
TN_2021_2710 |  | 75866 20220758 | 728484F | CCTSST FR 0.1 1X4X1.4 | 16.1 | 9 | Vilanova | TPR38-DOUBLESTEELTAPE+1402FEES+TPR55 | CD | 60 | 10.3 | No | 2021-01-14 | B2_s1_d2 | 0.44 | 6.8 | 11.5 | 1158 | 15.1 | B2 | 7.5 | 0.03 | s1 | n | y | d2
TN_2021_2711 |  | 75866 20220758 | 832343W | CCTSST FR 0.1 1X4X1.4 | 16.51 | 9 | Vilanova | TPR-DOUBLESTEELTAPE+1420FEES+TPR55 | CD | 70 | 7.18 | No | 2021-01-15 | B2_s1_d2 | 0.56 | 10.3 | 17.5 | 1206 | 23.4 | B2 | 10.3 | 0.02 | s1 | n | y | d2
TN_2021_2712 |  | 75866 20220758 | 728484F | CCTSST FR 0.1 1X4X1.4 | 16.1 | 9 | Vilanova | TPR38-DOUBLESTEELTAPE+1402FEES+TPR55 | CD | 70 | 7.09 | No | 2021-01-15 | B2_s1_d2 | 0.38 | 5 | 8.3 | 1500 | 14.8 | B2 | 5.3 | 0.01 | s1 | n | y | d2
TN_2021_2713 |  | 20335406 77946 | 845133Y | EATI-25S-TI 1X2X1.6 | 20.97 | 7 | Vilanova | HDPEVPE-05LDPEVPE-01TPR-38AFUMEXCPRDMZ-E | CD | 60 | 8.28 | No | 2021-01-15 | D_s2_d2 | 2.61 | 48 | 134.2 | 1473 | 115 | D | 63 | 0.18 | s2 | n | y | d2
TN_2021_2714 |  | 20338435 77945 | 791869C | EATI-2S-TI 2X2X1.05 | 18.15 | 8 | Vilanova | HDPEVPE-05LDPEVPE-01TPR-38AFUMEXCPRDMZ-E | CD | 60 | 9.94 | No | 2021-01-15 | D_s2_d2 | 1.87 | 41.1 | 72.1 | 1497 | 82.3 | D | 54.2 | 0.13 | s2 | n | y | d2
TN_2021_2715 |  | 20352328 80238 | 832340T | AFUMEX CLASS RZ1-K 5G1.5 | 10.64 | 14 | Vilanova | LLDPECONSILANO+SKINTIPO30+FR8101 | CD | 70 | 10.71 | No | 2021-01-18 | D_s2_d2 | 3.3 | 68.4 | 142.4 | 1332 | 138.1 | D | 139.4 | 0.39 | s2 | n | y | d2
TN_2021_2716 |  | 20352328 80238 | 728481C | AFUMEX CLASS RZ1-K 5G1.5 | 11.33 | 14 | Vilanova | LLDPECONSILANO+SKINTIPO30+0400FEIT+FR8101 | CD | 70 | 10.39 | No | 2021-01-18 | B2_s1_d0 | 0.79 | 8.8 | 19 | 690 | 65.8 | B2 | 16.2 | 0.04 | s1 | n | n | d0
TN_2021_2717 |  | 20352328 80238 | 832340T | AFUMEX CLASS RZ1-K 5G1.5 | 10.64 | 14 | Vilanova | LLDPECONSILANO+SKINTIPO30+FR8101 | CD | 60 | 11.1 | No | 2021-01-18 | B2_s1_d1 | 1.46 | 13.9 | 23.5 | 720 | 61.6 | B2 | 24.5 | 0.04 | s1 | y | n | d1
TN_2021_2718 |  | 20352328 80238 | 728481C | AFUMEX CLASS RZ1-K 5G1.5 | 11.33 | 14 | Vilanova | LLDPECONSILANO+SKINTIPO30+0400FEIT+FR8101 | CD | 60 | 12.94 | No | 2021-01-18 | B2_s1_d1 | 0.6 | 7.9 | 18.1 | 654 | 51.2 | B2 | 12.4 | 0.03 | s1 | y | n | d1
TN_2021_2719 |  | 20352328 80238 | 832340T | AFUMEX CLASS RZ1-K 5G1.5 | 10.64 | 14 | Vilanova | LLDPECONSILANO+SKINTIPO30+FR8101 | CD | 60 | 14.78 | No | 2021-01-18 | E ou F_s2_d2 | 3.3 | 70.8 | 173.1 | 1356 | 163.9 | E ou F | 137 | 0.4 | s2 | n | y | d2
TN_2021_2720 |  | 80699 20233819 | 839861T | AFUMEX EASY 1KV RZ1-K 5G50 | 31.71 | 6 | Vilanova | XLPEVISICO+SINRELLENO+1620SEES | CD | 70 | 14.73 | No | 2021-01-18 | D_s1_d2 | 1.14 | 17.4 | 61.3 | 1500 | 51.1 | D | 23.5 | 0.06 | s1 | n | y | d2
TN_2021_2721 |  | 80238 20352328 | 728481C | AFUMEX CLASS RZ1-K 5G1.5 | 11.33 | 14 | Vilanova | LLDPECONSILANO+SKINTIPO30+0400FEIT+FR8101 | CD | 70 | 14.14 | No | 2021-01-18 | B2_s1_d0 | 1.12 | 12.2 | 20.9 | 711 | 64.4 | B2 | 19.1 | 0.04 | s1 | n | n | d0
TN_2021_2722 |  | 77946 20335406 | 845133Y | EATI-25S-TI 1X2X1.6 | 20.97 | 7 | Vilanova | HDPEVPE-05LDPEVPE-01TPR-38AFUMEXCPRDMZ-E | CD | 70 | 14.18 | No | 2021-01-18 | D_s2_d2 | 2.12 | 43.8 | 99.6 | 1500 | 84.9 | D | 66.3 | 0.16 | s2 | n | y | d2
TN_2021_2723 |  |  | 5096964 | AFUMEX CLASS 750V H07Z-1-K (AS) TYPE 2 1X25 CCAS1BD1 | 8.72 | 17 | Vilanova | REFENCESAMPLE | CD | 70 | 10.1 | No | 2021-01-19 | B2_s1_d0 | 0.27 | 1.8 | 4.6 | 642 | 16.5 | B2 | 7 | 0.01 | s1 | n | n | d0
TN_2021_2724 |  |  | 5096969 | AFUMEX CLASS 750V H07Z-1-K (AS) TYPE 2 1X25 CCAS1BD1 | 8.8 | 17 | Vilanova | REFENCESAMPLE | CD | 70 | 12.67 | No | 2021-01-19 | B2_s1_d0 | 0.37 | 2.7 | 7.3 | 612 | 25 | B2 | 9.2 | 0.01 | s1 | n | n | d0
TN_2021_2725 |  | 20352328 80238 | 832340T | AFUMEX CLASS RZ1-K 5G1.5 | 10.64 | 14 | Vilanova | LLDPECONSILANO+SKINTIPO30+FR8101 | CD | 70 | 15.51 | No | 2021-01-19 | E ou F_s2_d2 | 3.3 | 87.9 | 228.6 | 1146 | 270.7 | E ou F | 148.7 | 0.43 | s2 | n | y | d2
TN_2021_2726 |  | 80699 20233819 | 839861T | AFUMEX EASY 1KV RZ1-K 5G50 | 32.08 | 6 | Vilanova | XLPEVISICO+SINRELLENO+1620SEES | CD | 70 | 14.31 | No | 2021-01-19 | D_s1_d2 | 2.12 | 33 | 119.3 | 1488 | 100.4 | D | 28.4 | 0.12 | s1 | n | y | d2
TN_2021_2727 |  |  | 5096539 | TOP SOLAR H1Z2Z2 1X6 NG 1.5 KV | 5.93 | 25 | Vilanova | COMPETITORSAMPLE | CD | 70 | 12.68 | No | 2021-01-19 | C_s1_d2 | 1.79 | 11.1 | 22.2 | 744 | 86.8 | C | 19.3 | 0.05 | s1 | n | y | d2
TN_2021_2728 |  | 80238 20352328 | 832340T | AFUMEX CLASS RZ1-K 5G1.5 | 10.64 | 14 | Vilanova | LLDPECONSILANO+SKINTIPO30+FR8101 | CD | 70 | 12.58 | No | 2021-01-19 | D_s2_d2 | 3.3 | 50 | 131.1 | 1500 | 109.2 | D | 94 | 0.29 | s2 | n | y | d2
TN_2021_2729 |  |  | 5096540 | TOP SOLAR H1Z2Z2 1X6 RJ 1.5 KV | 5.89 | 25 | Vilanova | COMPETITORSAMPLE | CD | 70 | 11.71 | No | 2021-01-20 | C_s1_d2 | 1.85 | 17.1 | 26.6 | 693 | 137.4 | C | 26.1 | 0.04 | s1 | n | y | d2
CEL-1072_20-1 |  | 79292 20235174 | 802943P | HEPRZ1(AS) 26/45KV 1X300K AL+H75 | 51.68 | 4 | CEIS | 14202.5MM+61AA3.2MM | CD | 70 | 17.42 | No | 2020-12-01 | B2_s1_d0 | 0.7 | 12.8 | 16.18 | 1500 | 28.55 | B2 | 3.62 | 0.02 | s1 | n | n | d0
TN_2021_2730 |  | 20045041 | OF391 | VOLTALENE RHZ1-RA+2OL(AS) 220KV 1X630K AL+H25 | 100.07 | 2 | Vilanova | 60ACTRAMO1Y3 | CD | 73.5 | 10.84 | No | 2021-01-25 | C_s1_d2 | 1.04 | 28.2 | 55.9 | 1497 | 46.7 | C | 1.8 | 0.02 | s1 | n | y | d2
TN_2021_2737 |  | 20045041 | OF391 | VOLTALENE RHZ1-RA+2OL(AS) 220KV 1X630K AL+H25 | 100.07 | 2 | Vilanova | 60ACTRAMO2Y4 | CD | 74.7 | 11.47 | No | 2021-01-22 | D_s1_d2 | 1.48 | 41.3 | 103.8 | 1485 | 87.6 | D | 8.5 | 0.05 | s1 | n | y | d2
TN_2021_2738 |  | 80699 20233819 | 839861T | AFUMEX EASY 1KV RZ1-K 5G50 | 31.71 | 6 | Vilanova | XLPEVISICO+SINRELLENO+1620SEES | CD | 60.9 | 12.03 | No | 2021-01-25 | C_s1_d2 | 0.71 | 12 | 33.6 | 1500 | 29.3 | C | 8.1 | 0.02 | s1 | n | y | d2
TN_2021_2739 |  |  | 5096539 | TOP SOLAR H1Z2Z2 1X6 NG 1.5 KV | 5.93 | 25 | Vilanova | COMPETITORSAMPLE | CD | 61.2 | 13.05 | No | 2021-01-25 | B2_s1_d2 | 0.54 | 6 | 16.4 | 498 | 102.7 | B2 | 15.8 | 0.04 | s1 | n | y | d2
TN_2021_2740 |  |  | 5096540 | TOP SOLAR H1Z2Z2 1X6 RJ 1.5 KV | 5.89 | 25 | Vilanova | COMPETITORSAMPLE | CD | 62 | 13.83 | No | 2021-01-25 | C_s1_d2 | 1.86 | 17.1 | 28.6 | 648 | 115.5 | C | 25.5 | 0.04 | s1 | n | y | d2
TN_2021_2741 |  | 80699 20233819 | 839861T | AFUMEX EASY 1KV RZ1-K 5G50 | 31.71 | 6 | Vilanova | XLPEVISICO+SINRELLENO+1620SEES | CD | 59.7 | 14.55 | No | 2021-01-25 | D_s1_d2 | 0.99 | 19.5 | 71.9 | 1500 | 60 | D | 14.6 | 0.07 | s1 | n | y | d2
TN_2021_2744 |  |  | 5096539 | TOP SOLAR H1Z2Z2 1X6 NG 1.5 KV | 5.93 | 25 | Vilanova | COMPETITORSAMPLE | CD | 63.8 | 9.57 | No | 2021-01-26 | C_s1_d2 | 2 | 14.7 | 23.1 | 630 | 136 | C | 25.3 | 0.04 | s1 | n | y | d2
TN_2021_2745 |  |  | 5096525 | 5. F/UTP6A CCA 5.4 | 7.14 | 21 | Vilanova | SHEATH:CONGUARDS66500.6MM | CD | 60 | 9.62 | No | 2021-01-27 | B2_s1_d1 | 0.52 | 6.1 | 17.9 | 504 | 128 | B2 | 18.7 | 0.07 | s1 | y | n | d1
TN_2021_2746 |  |  | 5096529 | 5. F/UTP6A CCA 5.6 | 7.66 | 19 | Vilanova | SHEATH:CONGUARDS66500.8MM | CD | 58.6 | 9.69 | No | 2021-01-27 | C_s1_d1 | 1.16 | 11.7 | 33.1 | 549 | 159.2 | C | 31.5 | 0.08 | s1 | y | n | d1
TN_2021_2747 |  |  | 5096528 | 5. F/UTP6A CCA 5.5 | 7.09 | 21 | Vilanova | SHEATH:CONGUARDS66500.7MM | CD | 64.7 | 13.15 | No | 2021-01-27 | B2_s1_d1 | 0.59 | 7.4 | 29.8 | 537 | 132.5 | B2 | 18.7 | 0.09 | s1 | y | n | d1
TN_2021_2752 |  |  | 5096527 | 14. U/UTP6A CCA 14.3 | 7.44 | 25 | Vilanova | SHEATH:CONGUARDS66500.8MM | CD | 73.4 | 12.28 | No | 2021-01-28 | C_s1_d1 | 0.42 | 8.8 | 33.6 | 540 | 164.5 | C | 30.7 | 0.15 | s1 | y | n | d1
TN_2021_2753 |  |  | 5096530 | 8. U/UTP6A DCA 8.1 | 7.23 | 21 | Vilanova | SHEATH:TPR-320.6MM | CD | 71.3 | 12.23 | No | 2021-01-28 | D_s2_d2 | 3.3 | 62 | 343.8 | 753 | 759 | D | 130.4 | 0.56 | s2 | n | y | d2
TN_2021_2754 |  |  | 5096526 | 14. F/UTP6A CCA 14.2 | 7.23 | 21 | Vilanova | SHEATH:CONGUARDS66500.7MM | CD | 74.6 | 16.81 | No | 2021-01-28 | C_s1_d1 | 0.6 | 7.7 | 26.2 | 540 | 164.6 | C | 14.8 | 0.07 | s1 | y | n | d1
TN_2021_2755 |  |  | 5096531 | 8. U/UTP6A DCA 8.2 | 7.77 | 19 | Vilanova | SHEATH:TPR-320.7MM | CD | 50.7 | 24.86 | No | 2021-01-29 | D_s2_d2 | 3.3 | 55.4 | 354.8 | 693 | 905.6 | D | 120.2 | 0.58 | s2 | n | y | d2
TN_2021_2756 |  |  | 5096531 | 8. U/UTP6A DCA 8.2 | 7.77 | 19 | Vilanova | SHEATH:TPR-320.7MM | CD | 48.8 | 24.9 | No | 2021-01-29 | D_s2_d2 | 3.3 | 57.2 | 372.7 | 660 | 1054.1 | D | 121.5 | 0.6 | s2 | n | y | d2
TN_2021_2757 |  |  | 5096532 | JETLAN 7 CAT7 LSHF IEC 4X2X23 AWG | 7.75 | 19 | Vilanova | VPC-02+VPE-05+TPR32 | CD | 48.1 | 22.33 | No | 2021-01-29 | D_s2_d2 | 3.3 | 48.5 | 331.1 | 675 | 883 | D | 89.9 | 0.47 | s2 | n | y | d2
TN_2021_2758 |  |  | 5096532 | JETLAN 7 CAT7 LSHF IEC 4X2X23 AWG | 7.75 | 19 | Vilanova | VPC-02+VPE-05+TPR32 | CD | 48.1 | 20.07 | No | 2021-01-29 | D_s2_d2 | 3.3 | 48 | 314.5 | 675 | 844.2 | D | 99.7 | 0.47 | s2 | n | y | d2
TN_2021_2759 |  |  | 5096530 | 8. U/UTP6A DCA 8.1 | 7.23 | 21 | Vilanova | SHEATH:TPR-320.6MM | CD | 50.1 | 18.88 | No | 2021-01-29 | D_s2_d2 | 3.3 | 58.5 | 353.3 | 681 | 931.3 | D | 127.3 | 0.56 | s2 | n | y | d2
TN_2021_2762 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 49 | 15.72 | No | 2021-02-01 | B2_s1_d2 | 0.72 | 13.1 | 24.1 | 846 | 44.4 | B2 | 17.9 | 0.03 | s1 | n | y | d2
TN_2021_2763 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 60.5 | 14.07 | No | 2021-02-02 | B2_s1_d2 | 0.7 | 11.4 | 21.1 | 855 | 45.9 | B2 | 18 | 0.04 | s1 | n | y | d2
TN_2021_2764 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 58.4 | 21.1 | No | 2021-02-02 | C_s1_d0 | 1.26 | 18.8 | 32.9 | 882 | 68.4 | C | 49.4 | 0.12 | s1 | n | n | d0
TN_2021_2765 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 54.5 | 21.38 | No | 2021-02-02 | B2_s1_d1 | 0.61 | 9.1 | 15.2 | 924 | 35.9 | B2 | 20.9 | 0.03 | s1 | y | n | d1
TN_2021_2766 |  |  | 5096528 | 5.F/UTP6A CCA 5.5 | 6.79 | 21 | Vilanova | SHEATH:CONGUARDS66500.7MMBOB2 | CD | 48.6 | 25.02 | No | 2021-02-02 | C_s1_d1 | 0.59 | 5.6 | 24.9 | 483 | 165.1 | C | 25.2 | 0.12 | s1 | y | n | d1
TN_2021_2767 |  |  | 5096527 | 14.U/UTP6A CCA 14.3 | 7.5 | 21 | Vilanova | SHEATH:CONGUARDS66500.8MMBOB1 | CD | 46.9 | 25.77 | No | 2021-02-02 | B2_s1_d1 | 0.71 | 5.7 | 28 | 534 | 136.2 | B2 | 22.7 | 0.11 | s1 | y | n | d1
TN_2021_2768 |  |  | 5096526 | 14.U/UTP6A CCA14.2 | 7.47 | 21 | Vilanova | SHEATH:CONGUARDS66500.7MMBOB2 | CD | 49.3 | 23.31 | No | 2021-02-02 | C_s1_d1 | 0.51 | 5.8 | 28.3 | 507 | 165.7 | C | 23.4 | 0.11 | s1 | y | n | d1
TN_2021_2769 |  |  | 5096525 | 5.F/UTP6A CCA5.4 | 6.52 | 21 | Vilanova | SHEATH:CONGUARDS66500.6MMBOB2 | CD | 52.2 | 18.06 | No | 2021-02-02 | B2_s1_d0 | 0.39 | 4.2 | 19.9 | 438 | 145.4 | B2 | 17.4 | 0.1 | s1 | n | n | d0
TN_2021_2770 |  |  | 5096529 | 5.F/UTP6A CCA 5.6 | 7.66 | 19 | Vilanova | SHEATH:CONGUARDS66500.8MMBOB2 | CD | 53.4 | 16.7 | No | 2021-02-02 | B2_s1_d1 | 0.53 | 3.7 | 14.2 | 447 | 102.6 | B2 | 16 | 0.03 | s1 | y | n | d1
TN_2021_2771 |  | 20352332 80226 | 861029B | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.12 | 8 | Vilanova | CINTACU20%+MICA50%+RELLENO1420+CUBIERTA1602 | CD | 64.7 | 12.67 | No | 2021-02-03 | D_s2_d2 | 3.3 | 63.9 | 150.8 | 1497 | 140.2 | D | 69.7 | 0.15 | s2 | n | y | d2
TN_2021_2772 |  | 20352332 80226 | 861029B | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.12 | 8 | Vilanova | CINTACU20%+MICA50%+RELLENO1420+CUBIERTA1602 | CD | 62.1 | 12.9 | No | 2021-02-03 | D_s2_d2 | 2.8 | 53.5 | 112.7 | 1497 | 108.1 | D | 69.8 | 0.15 | s2 | n | y | d2
TN_2021_2773 |  | 78593 20343987 | 796632E | KX-RHOZ1MZ1 500V 24X2X1.3 CCA S1B D1 A1 2RH | 36.82 | 5 | Vilanova | GFR-380+SWA+GFR-380 | CD | 52.8 | 18.91 | No | 2021-02-03 | B2_s1_d1 | 0.56 | 6 | 7.4 | 528 | 42.4 | B2 | 17.4 | 0.02 | s1 | y | n | d1
TN_2021_2774 |  | 80697 20233820 | 249965B | AFUMEX CLASS 1KV RZ1-K DCA 4X120 | 45.95 | 4 | Vilanova | XLPEVISICO+SINRELLENO+1620SEES | CD | 48.5 | 24.1 | No | 2021-02-03 | B2_s1_d2 | 0.65 | 6.6 | 16.6 | 1497 | 18.8 | B2 | 5.6 | 0.01 | s1 | n | y | d2
TN_2021_2775 |  | 80697 20233820 | 249965B | AFUMEX CLASS 1KV RZ1-K DCA 4X120 | 45.95 | 4 | Vilanova | XLPEVISICO+SINRELLENO+1620SEES | CD | 44.6 | 23.13 | No | 2021-02-03 | B2_s1_d2 | 0.64 | 7.9 | 12.6 | 1488 | 24.6 | B2 | 5.3 | 0.01 | s1 | n | y | d2
TN_2021_2778 |  |  | 5096358 | U/UTP 5E 4PR 24AWG CCA S1A D2 A1 | 5.18 | 30 | Vilanova | CONGUARDS6650 | CD | 64 | 13.03 | No | 2021-02-04 | C_s1_d1 | 1.75 | 9.1 | 19.8 | 564 | 137 | C | 21.5 | 0.04 | s1 | y | n | d1
TN_2021_2779 |  | 5093510 | 436 | EUPEN XVB 5G16 0.6/ 1 KV CCA S3 D2 A3 GRIS | 21.19 | 7 | Vilanova | COMPETITORSAMPLE | CD | 63.6 | 13.41 | No | 2021-02-04 | B2_s2_d1 | 0.97 | 11.3 | 21.9 | 1392 | 58.3 | B2 | 149.2 | 0.34 | s2 | y | n | d1
TN_2021_2780 |  | 5096511 | 437 | NEXANS XVB 5G16 0.6/ 1 KVCCA S3 D2 A3 GRIS | 22.35 | 7 | Vilanova | COMPETITORSAMPLE | CD | 66.8 | 15.74 | No | 2021-02-04 | C_s2_d0 | 1.68 | 19.5 | 30.3 | 1422 | 98.4 | C | 187.7 | 0.44 | s2 | n | n | d0
TN_2021_2781 |  | 5096512 | 438 | EUPEN XGB 4X25 0.6/ 1 KV CCA S1 D2 A1 VERDE | 24.01 | 7 | Vilanova | COMPETITORSAMPLE | CD | 66.9 | 16.15 | No | 2021-02-04 | B2_s1_d0 | 0.34 | 4.5 | 7.5 | 600 | 29.9 | B2 | 8.6 | 0.01 | s1 | n | n | d0
TN_2021_2782 |  | OP80662 20229590 | 863243H | RHZ1-2OL (AS) 20KV 1X150/16 AL | 40.94 | 5 | Vilanova | 2.4MM1420+3.2MM61AAAX03LT6100-ES-SG | CD | 67 | 19.54 | No | 2021-02-04 | B2_s1_d2 | 0.68 | 11 | 14.5 | 744 | 46.9 | B2 | 15.3 | 0.02 | s1 | n | y | d2
TN_2021_2785 |  | 20193656 84024169 | 851273X | AFUMEX CLASS 1KV RZ1-K (AS) 3G4 | 12.39 | 13 | Vilanova | 0400+1602 | CD | 73.8 | 13.5 | No | 2021-02-05 | C_s2_d2 | 1.56 | 27.1 | 45.5 | 1074 | 60.5 | C | 63.2 | 0.16 | s2 | n | y | d2
TN_2021_2786 |  | 20193694 84017490 | 851193K | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.09 | 13 | Vilanova | 0400+1602 | CD | 71.4 | 13.6 | No | 2021-02-05 | D_s1_d1 | 2.02 | 32.6 | 48.9 | 1146 | 68.3 | D | 38.1 | 0.07 | s1 | y | n | d1
TN_2021_2787 |  | 20193694 84017490 | 851193K | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.09 | 13 | Vilanova | 0400+1602 | CD | 69.7 | 13.48 | No | 2021-02-05 | C_s2_d2 | 1.88 | 29.3 | 40.4 | 1146 | 68.7 | C | 51.3 | 0.08 | s2 | n | y | d2
TN_2021_2788 |  | 20193656 84024169 | 851273X | AFUMEX CLASS 1KV RZ1-K (AS) 3G4 | 12.39 | 13 | Vilanova | 0400+1602 | CD | 67.5 | 15.98 | No | 2021-02-05 | C_s1_d2 | 1.26 | 21.2 | 40.2 | 1050 | 54.9 | C | 33.9 | 0.09 | s1 | n | y | d2
TN_2021_2789 |  | 20193694 84017490 | 851193K | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.09 | 13 | Vilanova | 0400+1602 | CD | 64 | 20.76 | No | 2021-02-05 | D_s1_d2 | 2.9 | 45.6 | 66.4 | 1380 | 87.7 | D | 32.7 | 0.08 | s1 | n | y | d2
TN_2021_2790 |  | 890675 | 14J7252 | CCTSST(X) FR 0.1 14X4X0.9 | 33.84 | 5 | Vilanova | TPR38+1420FEES+TPR55 | CD | 54.8 | 11.88 | No | 2021-02-08 | B2_s1_d0 | 0.51 | 6.1 | 10.7 | 828 | 32 | B2 | 15.8 | 0.02 | s1 | n | n | d0
TN_2021_2791 |  | 20193656 84024169 | 851273X | AFUMEX CLASS 1KV RZ1-K (AS) 3G4 | 12.39 | 13 | Vilanova | 0400+1602 | CD | 54.6 | 12.41 | No | 2021-02-08 | B2_s1_d2 | 0.9 | 14.9 | 23 | 948 | 45.5 | B2 | 38.9 | 0.11 | s1 | n | y | d2
TN_2021_2792 |  | 890675 | 14J7744 | CCTSST(X) FR 0.1 25X4X0.9 | 38.83 | 5 | Vilanova | TPR38+1420FEES+TPR55 | CD | 54.2 | 13.85 | No | 2021-02-08 | B2_s1_d0 | 0.62 | 6.9 | 12.6 | 765 | 43.8 | B2 | 0 | 0 | s1 | n | n | d0
TN_2021_2793 |  | 78593 20343987 | 796632E | KX-RHOZ1MZ1 500V 24X2X1.3 CCA S1B D1 A1 2RH | 36.82 | 5 | Vilanova | GFR-380+SWA+GFR-380 | CD | 52.5 | 14.78 | No | 2021-02-08 | B2_s1_d1 | 0.57 | 7.4 | 9.7 | 1491 | 34.3 | B2 | 2.1 | 0.01 | s1 | y | n | d1
TN_2021_2794 |  | OP80662 20229590 | 863243H | RHZ1-2OL (AS) 20KV 1X150/16 AL | 40.94 | 5 | Vilanova | 2.4MM1420+3.2MM61AAAX03LT6100-ES-SG | CD | 49.5 | 13.34 | No | 2021-02-08 | B2_s1_d1 | 0.8 | 13.5 | 19.6 | 1500 | 44.5 | B2 | 10.7 | 0.03 | s1 | y | n | d1
CEL-1137_20-1 |  | 20173170 | 733675Y | RHZ1-RA+2OL (AS) 66KV 1X1000K AL+H135 | 74.71 | 3 | CEIS | 61AASEES+CABELEC381770%+DMZ-330% | CD | 35 | 25 | No | 2021-02-05 | B2_s1_d0 | 0.8 | 4.85 | 6.19 |  | 11.21 | B2 | 3.5 | 0 | s1 | n | n | d0
TN_2021_2797 |  | 20320360 75352 | 817476L | XAZ1 750V 1X300 CCA S1B D1 A1 FOR PROTO C | 34.06 | 5 | Vilanova | PRS-03+TPR-38AFUMEXCPRDMZ-E | CD | 64.9 | 11.3 | No | 2021-02-10 | B2_s1_d2 | 0.69 | 12.1 | 16.8 | 1248 | 32.3 | B2 | 7.5 | 0.04 | s1 | n | y | d2
TN_2021_2798 |  | 20320360 75352 | 817476L | XAZ1 750V 1X300 CCA S1B D1 A1 FOR PROTO C | 34.06 | 5 | Vilanova | PRS-03+TPR-38AFUMEXCPRDMZ-E | CD | 62,,5 | 12.14 | No | 2021-02-10 | B2_s1_d2 | 0.7 | 13.3 | 16.9 | 1119 | 39.4 | B2 | 20.1 | 0.04 | s1 | n | y | d2
TN_2020_2777 |  | 20338103 | OF 1160 | RHZ1-RA+2OL(AS) 220KV 1X2000CUMK+H250 127/220 KV | 126 | 2 | Vilanova | TRAM4I5SHEATHDMZ-2+SKINSC003A | CD | 65.6 | 12.43 | No | 2021-02-10 | B2_s1_d2 | 1.22 | 11.9 | 16.8 | 1134 | 24 | B2 | 6.4 | 0.03 | s1 | n | y | d2
21020004 |  | 18566 | CE6782C | HINKLEY POINT 1X50 15KV ALU-EC-SH (ALU-POINT) | 29.4 | 6 | Paron | LE4205R+CE7600FR+SW3100FR | -- | 35.1 | 22.5 | No | 2021-02-04 | B2_s1_d2 | 0.45 | 7.3 | 22.8 | 1500 | 23.5 | B2 | 18.4 | 0.09 | s1 | y | y | d2
21020006 |  | 18566 | CE6782C | HINKLEY POINT 1X50 15KV ALU-EC-SH (ALU-POINT) | 29.4 | 6 | Paron | LE4205R+CE7600FR+SW3100FR | -- | 39.3 | 22.3 | No | 2021-02-04 | B2_s1_d2 | 0.5 | 8.6 | 25.4 | 1500 | 21.1 | B2 | 24.4 | 0.11 | s1 | y | y | d2
21020007 |  | 18566 | CE67777A | HINKLEY POINT 1*6 1KV CU-SH-CE6777A | 11 | 14 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 27.5 | 18.1 | No | 2021-02-09 | B2_s1_d0 | 0.35 | 6.8 | 13.1 | 915 | 40.8 | B2 | 10.2 | 0.02 | s1 | n | n | d0
21020008 |  | 18566 | CE6782A | HINKLEY POINT 1X50 15KV ALU-EC-SH (ALU-TRAPEZE) | 29.4 | 6 | Paron | LE4205R+CE7600FR+SW3100FR | -- | 26.5 | 20 | No | 2021-02-09 | B2_s1_d2 | 0.65 | 8.8 | 25.7 | 1500 | 21.6 | B2 | 19.1 | 0.09 | s1 | y | y | d2
21020009 |  | 18566 | CE6782A | HINKLEY POINT 1X50 15KV ALU-EC-SH (ALU-TRAPEZE) | 29.4 | 6 | Paron | LE4205R+CE7600FR+SW3100FR | -- | 28 | 17.5 | No | 2021-02-09 | B2_s1_d2 | 0.45 | 6.5 | 18.2 | 1500 | 15.3 | B2 | 17.1 | 0.06 | s1 | y | y | d2
TN_2021_2799 |  | 80774 20329100 | 637164V | TSLI(F) 145KV 1X400 AI2 H70 | 75.9 | 3 | Vilanova | 61AASEES+CABELEC381770%+DMZ-E30%TRAM3.1I6 | CD | 51.4 | 14.18 | No | 2021-02-11 | B2_s1_d0 | 0.65 | 10.6 | 13.8 | 903 | 33.6 | B2 | 15.9 | 0.03 | s1 | n | n | d0
TN_2021_2800 |  | 60080944 | 5096764 | JTL F/FTP/4P LSZH B500 DCA S2D2A1 4X2X23 AWG | 7.77 | 19 | Vilanova | LSOH | CD | 51.7 | 17.49 | No | 2021-02-11 | D_s2_d2 | 3.3 | 47.6 | 339.3 | 690 | 875.7 | D | 100.2 | 0.48 | s2 | n | y | d2
TN_2021_2801 |  | 80746 20353805 | 864561R | HEPRHZ1-2OL 10KV 1X300 MM2 | 44.9 | 4 | Vilanova | 0400FEIT1.46MM+61AASEES2.96MM | CD | 50.4 | 20 | No | 2021-02-11 | B2_s1_d0 | 0.86 | 13.2 | 17.7 | 969 | 40.8 | B2 | 13.7 | 0.04 | s1 | n | n | d0
20110006 |  | 18506 | -- | 750-2X2.15MM2-SH-NF F 55-625-255 | 10.4 | 15 | Paron |  | -- | 40 | 21.2 | No | 2020-11-27 | B2_s1_d1 | 0.8 | 10.8 | 12.4 | 513 | 60.9 | B2 | 22.6 | 0.03 | s1 | y | n | d1
20120008 |  | 18506 | -- | 750-2X2.15MM2-SH-NF F 55-625-255 | 10.4 | 15 | Paron |  | -- | 39.4 | 22.9 | No | 2020-12-11 | B2_s1_d1 | 0.65 | 10 | 13.1 | 756 | 62 | B2 | 12.6 | 0.02 | s1 | y | n | d1
21010012 |  | 18506 | -- | 750-2X2.15MM2-SH-NF F 55-625-255 | 10.4 | 15 | Paron |  | -- | 31.4 | 22.7 | No | 2021-01-20 | B2_s1_d1 | 0.7 | 9 | 11.8 | 504 | 59.5 | B2 | 17.5 | 0.02 | s1 | y | n | d1
21010014 |  | 18506 | -- | 750-2X2.15MM2-SH-NF F 55-625-255 | 10.4 | 15 | Paron |  | -- | 36.2 | 18.5 | No | 2020-01-22 | B2_s1_d1 | 0.35 | 8.8 | 11.3 | 534 | 62.5 | B2 | 9.5 | 0.01 | s1 | y | n | d1
20110007 |  | 18506 | -- | 1800-S-1X240MM²-SH-NF F 55-625-255 | 31.2 | 6 | Paron |  | -- | 41.4 | 21.2 | No | 2020-11-27 | B2_s1_d1 | 0.35 | 6.8 | 8.5 | 1161 | 27.1 | B2 | 6.5 | 0.01 | s1 | y | n | d1
20110005 |  | 18506 | -- | 1800-S-1X240MM²-SH-NF F 55-625-255 | 31.2 | 6 | Paron |  | -- | 34.2 | 18.7 | No | 2020-12-09 | B2_s1_d1 | 0.4 | 5.1 | 6.2 | 849 | 20.6 | B2 | 4.2 | 0.01 | s1 | y | n | d1
20120007 |  | 18506 | -- | 1800-S-1X240MM²-SH-NF F 55-625-255 | 31.2 | 6 | Paron |  | -- | 36.2 | 20.5 | No | 2020-12-09 | B2_s1_d0 | 0.3 | 3.8 | 5.3 | 630 | 18.7 | B2 | 1.8 | 0 | s1 | n | n | d0
20100010 |  | 18506 | -- | 1800-S-1X240MM²-SH-NF F 55-625-255 | 31.2 | 6 | Paron |  | -- | 27.7 | 22.3 | No | 2021-01-20 | B2_s1_d2 | 0.45 | 7.7 | 8.9 | 972 | 35.7 | B2 | 4.3 | 0.01 | s1 | y | y | d2
21010011 |  | 18506 | -- | 1800-S-1X240MM²-SH-NF F 55-625-255 | 31.2 | 6 | Paron |  | -- | 30 | 22.9 | No | 2021-01-20 | B2_s1_d1 | 0.45 | 5.9 | 7.4 | 945 | 24.9 | B2 | 3.1 | 0 | s1 | y | n | d1
20110008 |  | 18506 | -- | 1000-S-1X240MM²-SH-NF F 55-625-255 | 31.2 | 6 | Paron |  | -- | 45.3 | 20.95 | No | 2020-11-27 | B2_s1_d1 | 0.3 | 4.3 | 6.1 | 612 | 22.3 | B2 | 5.6 | 0.01 | s1 | y | n | d1
21010018 |  | 18506 | -- | 1000-S-1X240MM²-SH-NF F 55-625-255 | 31.8 | 6 | Paron |  | -- | 44.2 | 22.5 | No | 2021-01-28 | B2_s1_d0 | 0.5 | 7.2 | 8 | 594 | 37.2 | B2 | 4.3 | 0.01 | s1 | n | n | d0
21010019 |  | 18506 | -- | 1000-S-1X240MM²-SH-NF F 55-625-255 | 31.8 | 6 | Paron |  | -- | 42.1 | 24.4 | No | 2021-01-28 | B2_s1_d0 | 0.3 | 4.3 | 5.7 | 615 | 24.4 | B2 | 1.8 | 0 | s1 | n | n | d0
20120001 |  | 18506 | -- | FR-N1X1G1 1X95MM² | 19.2 | 8 | Paron |  | -- | 41.3 | 20.9 | No | 2020-12-02 | B2_s1_d0 | 0.3 | 4.1 | 5.2 | 660 | 21.4 | B2 | 4 | 0.01 | s1 | n | n | d0
20120002 |  | 18506 | -- | FR-N1X1G1 5G25MM² | 27.2 | 6 | Paron |  | -- | 41.5 | 20.4 | No | 2020-12-02 | B2_s1_d0 | 0.25 | 4.2 | 4.5 | 1110 | 19.9 | B2 | 3.2 | 0 | s1 | n | n | d0
20120011 |  | 18506 | -- | FR-N1X1G1 5G25MM² | 27.2 | 6 | Paron |  | -- | 46.1 | 22.8 | No | 2020-12-11 | B2_s1_d0 | 0.35 | 6.8 | 7.2 | 639 | 38.3 | B2 | 3.4 | 0 | s1 | n | n | d0
20120003 |  | 18506 | -- | 750-4G35-SH-NF F 55-625-255 | 28.4 | 6 | Paron |  | -- | 43.3 | 19.8 | No | 2020-12-02 | B2_s1_d0 | 0.35 | 4.3 | 5.9 | 1500 | 16.8 | B2 | 4.8 | 0.01 | s1 | n | n | d0
20120010 |  | 18506 | -- | 750-4G35-SH-NF F 55-625-255 | 28.4 | 6 | Paron |  | -- | 41.3 | 23.4 | No | 2020-12-11 | B2_s1_d1 | 0.35 | 4 | 5.2 | 1161 | 14.7 | B2 | 3.4 | 0 | s1 | y | n | d1
21020002 |  | 18506 | -- | 750-4G35-SH-NF F 55-625-255 | 28.4 | 6 | Paron |  | -- | 47.2 | 22 | No | 2021-02-02 | B2_s1_d0 | 0.4 | 1.8 | 3.2 | 540 | 6.2 | B2 | 1.8 | 0 | s1 | n | n | d0
21020001 |  | 18506 | -- | 750-4G35-SH-NF F 55-625-255 | 28.53 | 6 | Paron |  | -- | 46.4 | 22.2 | No | 2021-02-02 | B2_s1_d0 | 0.35 | 1.4 | 2.5 | 1500 | 0 | B2 | 3 | 0.01 | s1 | n | n | d0
21020003 |  | 18579 | -- | 1000-SS-1X95MM²-SH-NF F 55-625-255 (CL6) | 25.6 | 6 | Paron |  | -- | 42.4 | 23.6 | No | 2021-02-02 | B2_s1_d2 | 0.35 | 3.1 | 5 | 822 | 11.1 | B2 | 6.3 | 0.02 | s1 | y | y | d2
21020003 |  | 18579 | -- | 1000-SS-1X95MM²-SH-NF F 55-625-255 (CL6) | 25.6 | 6 | Paron |  | -- | 37.4 | 23 | No | 2021-02-04 | B2_s1_d0 | 0.3 | 5.3 | 7.4 | 1392 | 21.3 | B2 | 8.6 | 0.03 | s1 | n | n | d0
21010013 |  | 18579 | -- | 1000-SS-1X95MM²-SH-NF F 55-625-255 (CL6) | 25.6 | 6 | Paron |  | -- | 37.5 | 18.2 | No | 2021-01-22 | B2_s1_d0 | 0.25 | 5.6 | 8.2 | 903 | 20.4 | B2 | 10 | 0.02 | s1 | n | n | d0
21010015 |  | 18579 | -- | 1000-SS-1X95MM²-SH-NF F 55-625-255 (CL6) | 25.6 | 6 | Paron |  | -- | 34.1 | 20.6 | No | 2021-01-22 | B2_s1_d0 | 0.2 | 3.7 | 6.8 | 861 | 16.5 | B2 | 2.5 | 0.01 | s1 | n | n | d0
TN_2021_2802 |  | 82065 20352260 | 821670V | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.86 | 13 | Vilanova | 1420+16HH | CD | 49.6 | 19.88 | No | 2021-02-11 | C_s1_d2 | 1.67 | 29.9 | 44.2 | 1176 | 77.4 | C | 36.1 | 0.06 | s1 | n | y | d2
TN_2021_2803 |  | 84089145 20193654 | 855455T | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.92 | 15 | Vilanova | 0.30400+1.241602 | CD | 45.6 | 19.63 | No | 2021-02-11 | D_s1_d2 | 2.03 | 24.6 | 32.8 | 906 | 73.8 | D | 43.4 | 0.11 | s1 | n | y | d2
TN_2021_2804 |  | 80168 20352258 | 821649X | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.14 | 15 | Vilanova | 1420+16HH | CD | 48 | 16.65 | No | 2021-02-11 | C_s1_d2 | 1.12 | 16.7 | 29.6 | 879 | 70.9 | C | 27.2 | 0.05 | s1 | n | y | d2
TN_2021_2805 |  | 80169 20352258 | 821661K | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.74 | 14 | Vilanova | 0400+16HH | CD | 49.4 | 15.92 | No | 2021-02-11 | B2_s1_d2 | 0.54 | 8.6 | 26.2 | 621 | 81.5 | B2 | 18.9 | 0.06 | s1 | n | y | d2
TN_2021_2806 |  | 20193654 84089145 | 856662E | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.26 | 15 | Vilanova | 0.50400+1.416HH | CD | 60.9 | 17.28 | No | 2021-02-12 | C_s2_d2 | 1.63 | 22.3 | 33.3 | 846 | 62.2 | C | 64.7 | 0.16 | s2 | n | y | d2
TN_2021_2807 |  | 20193654 84089145 | 855461Z | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.06 | 15 | Vilanova | 0.30400+1.241602 | CD | 60.6 | 16.97 | No | 2021-02-12 | D_s1_d2 | 2.6 | 38.1 | 48.3 | 978 | 92.2 | D | 41.3 | 0.07 | s1 | n | y | d2
TN_2021_2808 |  | 20193654 84089145 | 855461Z | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.06 | 15 | Vilanova | 0.30400+1.241602 | CD | 61.3 | 17.79 | No | 2021-02-12 | C_s1_d2 | 1.99 | 26 | 36.6 | 816 | 77.4 | C | 46.1 | 0.1 | s1 | n | y | d2
TN_2021_2809 |  | 84089145 20193654 | 855455T | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.92 | 15 | Vilanova | 0.30400+1.241602 | CD | 64.3 | 16.4 | No | 2021-02-12 | C_s1_d1 | 1.5 | 15.4 | 26.1 | 780 | 62.2 | C | 15.4 | 0.07 | s1 | y | n | d1
TN_2021_2810 |  | 80168 20352258 | 821649X | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.14 | 15 | Vilanova | 1420+16HH | CD | 55.4 | 17.38 | No | 2021-02-12 | C_s1_d2 | 1.44 | 24 | 48.1 | 849 | 100.2 | C | 48 | 0.09 | s1 | n | y | d2
TN_2021_2811 |  | 81737 20352260 | 821647V | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.13 | 13 | Vilanova | 0400+16HH | CD | 57.5 | 16.17 | No | 2021-02-12 | C_s1_d2 | 0.99 | 18.4 | 27.3 | 900 | 73.2 | C | 34.5 | 0.07 | s1 | n | y | d2
TN_2021_2812 |  | 84089145 20193650 | 856730D | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.21 | 15 | Vilanova | 0.50400+1.2416HH | CD | 66 | 15.36 | No | 2021-02-12 | C_s2_d2 | 1.63 | 22.8 | 34.2 | 855 | 78.7 | C | 70.9 | 0.19 | s2 | n | y | d2
TN_2021_2813 |  | 81737 20352260 | 821647V | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.13 | 13 | Vilanova | 0400+16HH | CD | 72.8 | 11.86 | No | 2021-02-14 | B2_s1_d2 | 0.72 | 11.9 | 26.2 | 684 | 69 | B2 | 40.4 | 0.07 | s1 | n | y | d2
TN_2021_2814 |  | 80169 20352258 | 821661K | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.74 | 14 | Vilanova | 0400+16HH | CD | 71.9 | 12.15 | No | 2021-02-14 | C_s1_d2 | 0.8 | 10.5 | 32.9 | 636 | 98.3 | C | 33.7 | 0.08 | s1 | n | y | d2
TN_2021_2815 |  | 84089145 20193650 | 856730D | AFUMEX CLASS 1KV RZ1-K AS3G1.5 | 10.21 | 15 | Vilanova | 0.50400+1.2416HH | CD | 71 | 12.28 | No | 2021-02-14 | C_s2_d1 | 1.79 | 26.3 | 40.2 | 870 | 80.6 | C | 65.1 | 0.16 | s2 | y | n | d1
TN_2021_2816 |  | 20193654 84089145 | 856662E | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.26 | 15 | Vilanova | 0.50400+1.416HH | CD | 68.7 | 12.43 | No | 2021-02-14 | C_s2_d1 | 1.5 | 21.6 | 36.2 | 879 | 68.1 | C | 58.8 | 0.16 | s2 | y | n | d1
TN_2021_2817 |  | 82065 20352260 | 821670V | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.86 | 13 | Vilanova | 1420+16HH | CD | 71.1 | 12.02 | No | 2021-02-14 | C_s1_d2 | 1.47 | 26.8 | 45.3 | 945 | 78.5 | C | 32.5 | 0.06 | s1 | n | y | d2
TN_2021_2818 |  | 80168 20352258 | 821649X | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.14 | 15 | Vilanova | 1420+16HH | CD | 69.6 | 10.05 | No | 2021-02-15 | C_s1_d2 | 1.37 | 22.3 | 43.4 | 894 | 76.6 | C | 17.1 | 0.05 | s1 | n | y | d2
TN_2021_2819 |  | 20193654 84089145 | 855461Z | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.06 | 15 | Vilanova | 0.30400+1.241602 | CD | 69.1 | 10.26 | No | 2021-02-15 | D_s1_d1 | 2.15 | 30.9 | 41.9 | 1071 | 85.4 | D | 47.2 | 0.09 | s1 | y | n | d1
TN_2021_2820 |  | 20045041 | OF391 | VOLTALENE RHZ1-RA+2OL(AS) 220KV 1X630K AL+H25 | 99.33 | 2 | Vilanova | COB:61AASEES+SKIN30%DMZ-E+70%LE0567T22I3 | CD | 69.2 | 11.15 | No | 2021-02-15 | B2_s1_d0 | 0.61 | 8.8 | 11.6 | 831 | 28.8 | B2 | 10.7 | 0.02 | s1 | n | n | d0
TN_2021_2821 |  | 84089145 20193654 | 855455T | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.92 | 15 | Vilanova | 0.30400+1.241602 | CD | 69.5 | 11.24 | No | 2021-02-15 | D_s1_d2 | 2.17 | 25 | 35.8 | 867 | 80.4 | D | 44.7 | 0.08 | s1 | n | y | d2
TN_2021_2822 |  | 75866 | 728484F | CCTSST FR 0.1 1X4X1.4 | 16.14 | 9 | Vilanova | 1420FEES+TPR55 | CD | 75.2 | 13.14 | No | 2021-02-16 | B2_s1_d2 | 0.39 | 5.7 | 7.7 | 1155 | 25 | B2 | 16.7 | 0.02 | s1 | n | y | d2
TN_2021_2823 |  | 890672 | 14J7744 | CCTSST(X) FR 0.1 25X4X0.9 | 38.83 | 5 | Vilanova | TPR38+1420FEES+TPR55 | CD | 74.3 | 13.29 | No | 2021-02-16 | B2_s1_d0 | 0.69 | 7 | 13.9 | 711 | 43 | B2 | 10.6 | 0.02 | s1 | n | n | d0
TN_2021_2824 |  | 890675 | 14J7252 | CCTSST(X) FR 0.1 14X4X0.9 | 33.84 | 5 | Vilanova | TPR38+1420FEES+TPR55 | CD | 72.9 | 13.83 | No | 2021-02-16 | B2_s1_d0 | 0.61 | 6.7 | 11.9 | 666 | 37.8 | B2 | 4.1 | 0.01 | s1 | n | n | d0
TN_2021_2825 |  | 60094177 | 5096358 | U/UTP 5E 4PR 24AWG CCA S1A D2 A1 | 5.18 | 30 | Vilanova | CONGUARDS6650 | CD | 71.4 | 15.29 | No | 2021-02-16 | B2_s1_d0 | 0.75 | 5 | 13.7 | 399 | 138.2 | B2 | 7.1 | 0.03 | s1 | n | n | d0
TN_2021_2826 |  | 80774 20329100 | 637164V | TSLI(F) 145KV 1X400 AI2 H70 | 75.9 | 3 | Vilanova | 61AASEES+CABELEC381770%+DMZ-E30%TRAM4.5I25ALMIG | CD | 68.8 | 15.32 | No | 2021-02-16 | B2_s1_d0 | 0.79 | 14.6 | 18.1 | 1101 | 35.5 | B2 | 13.5 | 0.04 | s1 | n | n | d0
TN_2021_2828 |  | 78593 20343987 | 796632E | KX-RHOZ1MZ1 500V 24X2X1.3 CCA S1B D1 A1 2RH | 36.82 | 5 | Vilanova | GFR-380+SWA+GFR-380 | CD | 74.5 | 10.94 | No | 2021-02-17 | B2_s1_d1 | 0.68 | 7.5 | 12.1 | 1413 | 39.7 | B2 | 11.4 | 0.03 | s1 | y | n | d1
TN_2021_2829 |  | 80662 20229590 | 863243H | RHZ1-2OL (AS) 20KV 1X150/16 AL | 40.94 | 5 | Vilanova | 2.4MM1420+3.2MM61AAAX03LT6100-ES-SG | CD | 74.5 | 15.08 | No | 2021-02-17 | C_s1_d1 | 0.78 | 18.9 | 22.7 | 1011 | 51.9 | C | 6.1 | 0.02 | s1 | y | n | d1
TN_2021_2830 |  | 20045041 | OF391 | VOLTALENE RHZ1-RA+2OL(AS) 220KV 1X630K AL+H25 | 99.33 | 2 | Vilanova | COB:61AASEES+SKIN30%DMZ-E+70%LE0567T1I4 | CD | 71.8 | 18.41 | No | 2021-02-17 | B2_s1_d0 | 0.61 | 7 | 10.8 | 792 | 26.6 | B2 | 7.4 | 0.01 | s1 | n | n | d0
TN_2020_2831 |  | 20338103 | OF 1160 | RHZ1-RA+2OL(AS) 220KV 1X2000CUMK+H250 127/220 KV | 126 | 2 | Vilanova | TRAM2I3SHEATHDMZ-2+SKINSC003A | CD | 67.6 | 15.08 | No | 2021-02-17 | C_s1_d2 | 1.07 | 17.9 | 21.1 | 1401 | 37.4 | C | 11.1 | 0.02 | s1 | n | y | d2
TN_2021_2832 |  | 80774 20329100 | 637164V | TSLI(F) 145KV 1X400 AI2 H70 | 75.9 | 3 | Vilanova | 61AASEES+CABELEC381770%+DMZ-E30%TRAM4.2I52ALMIG | CD | 74.2 | 12.75 | No | 2021-02-18 | B2_s1_d0 | 0.73 | 11.3 | 14 | 1065 | 30.5 | B2 | 10.5 | 0.02 | s1 | n | n | d0
21020010 |  | 18566 | 6779A | HINKLEY POINT 4X2.5 1KV CU | 13.53 | 11 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 33.5 | 16.9 | No | 2021-02-15 | B2_s1_d1 | 0.2 | 6 | 8.3 | 1041 | 25.6 | B2 | 10.4 | 0.03 | s1 | y | n | d1
21020011 |  | 18566 | 6779A | HINKLEY POINT 4X2.5 1KV CU | 13.53 | 11 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 31.3 | 19.1 | No | 2021-02-15 | B2_s1_d1 | 0.3 | 7.8 | 14.1 | 1026 | 27.9 | B2 | 15.3 | 0.04 | s1 | y | n | d1
TN_2021_2833 |  | 80169 20352258 | 821661K | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.74 | 14 | Vilanova | 0400+16HH | CD | 72.8 | 12.8 | No | 2021-02-18 | B2_s1_d2 | 0.73 | 10 | 19.4 | 648 | 56.3 | B2 | 29.6 | 0.05 | s1 | n | y | d2
TN_2021_2834 |  | 82065 20352260 | 821670V | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.29 | 13 | Vilanova | 1420+16HH | CD | 72.1 | 13.88 | No | 2021-02-18 | C_s1_d2 | 1.32 | 22.8 | 37.8 | 828 | 78.6 | C | 32 | 0.05 | s1 | n | y | d2
TN_2021_2835 |  | 20193654 84089145 | 856662E | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.26 | 15 | Vilanova | 0.50400+1.416HH | CD | 68.8 | 16.81 | No | 2021-02-18 | C_s2_d2 | 1.53 | 21.1 | 37.4 | 897 | 64.9 | C | 68.9 | 0.16 | s2 | n | y | d2
21020012 |  | 18566 | CE67777A | HINKLEY POINT 1*6 1KV CU-SH-CE6777A | 11 | 14 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 40.7 | 18.4 | No | 2021-02-18 | B2_s1_d0 | 0.4 | 6 | 8.8 | 915 | 37.6 | B2 | 12.9 | 0.02 | s1 | n | n | d0
21020013 |  | 18566 | CE67778A | HINKLEY POINT 1*150 1KV ALU CE6778A | 24.37 | 7 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 41.7 | 18.1 | No | 2021-02-18 | B2_s1_d0 | 0.3 | 5.3 | 6.6 | 549 | 31.6 | B2 | 10.4 | 0.01 | s1 | n | n | d0
21020014 |  | 18566 | CE67778A | HINKLEY POINT 1*150 1KV ALU CE6778A | 24.37 | 7 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 42 | 19.1 | No | 2021-02-18 | B2_s1_d0 | 0.3 | 4.3 | 6.6 | 531 | 28.9 | B2 | 7.7 | 0.01 | s1 | n | n | d0
TN_2021_2838 |  | 84089145 20193650 | 856730D | AFUMEX CLASS 1KV RZ1-K AS3G1.5 | 10.21 | 15 | Vilanova | 0.50400+1.2416HH | CD | 76 | 10.91 | No | 2021-02-19 | C_s2_d1 | 1.38 | 19.8 | 29 | 795 | 67.3 | C | 61.8 | 0.17 | s2 | y | n | d1
TN_2021_2839 |  | 81737 20352260 | 821647V | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.13 | 13 | Vilanova | 0400+16HH | CD | 74.6 | 12.04 | No | 2021-02-19 | C_s1_d2 | 0.93 | 15.7 | 26.6 | 771 | 64.8 | C | 33.6 | 0.06 | s1 | n | y | d2
TN_2021_2841 |  | 80554 20353602 | 09-I22622 | FG16OM16 1X10MM2 - 0.6/1 KV | 8.23 | 19 | Vilanova | BEDDINGFREE+56ACSEIT | CD | 79.6 | 14.75 | No | 2021-02-22 | D_s2_d2 | 3.3 | 60.9 | 136.7 | 1188 | 155.5 | D | 134.9 | 0.28 | s2 | n | y | d2
TN_2021_2842 |  | 80551 20340529 | 09-I22670 | FG16OM16 5X1.5MM2 - 0.6/1 KV | 12.64 | 12 | Vilanova | 0300FDIT0.5MM+56ACSEIT | CD | 79.2 | 14.88 | No | 2021-02-22 | B2_s1_d1 | 0.7 | 11.5 | 26.5 | 906 | 44.4 | B2 | 20.4 | 0.04 | s1 | y | n | d1
TN_2021_2843 |  | 80552 20353490 | 09-I22625 | FG16OM16 4X1.5MM2 - 0.6/1 KV | 10.53 | 14 | Vilanova | 0300FDIT0.1MM+56ACSEIT | CD | 79.1 | 14.52 | No | 2021-02-22 | C_s1_d1 | 0.97 | 16.5 | 33 | 783 | 71.8 | C | 28.9 | 0.05 | s1 | y | n | d1
TN_2021_2844 |  | 80553 20353601 | 09-I22661 | FG16OM16 1X10MM2 - 0.6/1 KV | 9.07 | 17 | Vilanova | 0300FDIT0.35MM+56ACSEIT | CD | 78.3 | 14.59 | No | 2021-02-22 | B2_s1_d1 | 0.46 | 7.5 | 14.4 | 747 | 66.2 | B2 | 1.1 | 0.01 | s1 | y | n | d1
TN_2021_2845 |  | 80551 20340529 | 09-I22670 | FG16OM16 5X1.5MM2 - 0.6/1 KV | 12.64 | 12 | Vilanova | 0300FDIT0.5MM+56ACSEIT | CD | 78.1 | 14.7 | No | 2021-02-22 | C_s1_d1 | 0.79 | 15.4 | 30.7 | 879 | 51.8 | C | 16.3 | 0.03 | s1 | y | n | d1
21020017 |  | 18603 | Mat 9419 | CEI 60840-RTE-1600AL PR-26-AL230/400 (400KV) | 124.5 | 2 | Paron | XLPE+TUBEAL+6000SEES+SKINSC | -- | 34.7 | 23.2 | No | 2021-02-22 | B2_s1_d0 | 0.8 | 7.2 | 11.1 | 774 | 24.7 | B2 | 9.4 | 0.02 | s1 | n | n | d0
21020015 |  | 18566 | DBP165355 | HINKLEY POINT 1*185 1KV ALU-SH-CE6778B | 27.03 | 6 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 32.4 | 23.2 | No | 2021-02-22 | B2_s1_d1 | 0.35 | 4.3 | 7.7 | 1500 | 38.3 | B2 | 5.8 | 0.01 | s1 | y | n | d1
21020016 |  | 18566 | DBP165355 | HINKLEY POINT 1*185 1KV ALU-SH-CE6778B | 27.03 | 6 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 32.1 | 24 | No | 2021-02-22 | B2_s1_d1 | 0.35 | 4.4 | 7.5 | 1494 | 24 | B2 | 5.7 | 0.01 | s1 | y | n | d1
TN_2021_2848 |  | 80552 20353490 | 09-I22625 | FG16OM16 4X1.5MM2 - 0.6/1 KV | 10.53 | 14 | Vilanova | 0300FDIT0.1MM+56ACSEIT | CD | 82.7 | 12.89 | No | 2021-02-23 | B2_s1_d2 | 0.69 | 10.7 | 26.2 | 753 | 59 | B2 | 24.8 | 0.04 | s1 | n | y | d2
TN_2021_2849 |  | 80553 20353601 | 09-I22661 | FG16OM16 1X10MM2 - 0.6/1 KV | 9.07 | 17 | Vilanova | 0300FDIT0.35MM+56ACSEIT | CD | 81.5 | 13.08 | No | 2021-02-23 | B2_s1_d0 | 0.69 | 7.9 | 22.7 | 672 | 62.8 | B2 | 12.5 | 0.03 | s1 | n | n | d0
TN_2021_2850 |  | 80554 20353602 | 09-I22622 | FG16OM16 1X10MM2 - 0.6/1 KV | 8.23 | 19 | Vilanova | BEDDINGFREE+56ACSEIT | CD | 80.6 | 18.41 | No | 2021-02-23 | D_s2_d2 | 3.3 | 60.6 | 150.9 | 945 | 234.6 | D | 99.5 | 0.3 | s2 | n | y | d2
TN_2021_2856 |  | 80649 20350703 | 09-I22662 | ARG16R16 1X16MM2 - 0.6/1 KV | 10.53 | 14 | Vilanova | 1.2MMSHEATH54ABSPIT | CD | 78.5 | 13.95 | No | 2021-02-24 | C_s2_d0 | 0.53 | 9.3 | 17.9 | 606 | 197.4 | C | 87.9 | 0.37 | s2 | n | n | d0
TN_2021_2857 |  | 80652 20350706 | 10-H91901 | ARG16R16 1X240MM2 - 0.6/1 KV | 25.11 | 7 | Vilanova | 1.2MMSHEATH54ABSPIT | CD | 76.4 | 14.22 | No | 2021-02-24 | D_s2_d2 | 1.43 | 30.7 | 50.8 | 981 | 92.7 | D | 332.1 | 0.6 | s2 | n | y | d2
TN_2021_2858 |  | 80650 20350705 | 09-I22647 | ARG16R16 1X16MM2 - 0.6/1 KV | 10.11 | 15 | Vilanova | 0.9MMSHEATH54ABSPIT | CD | 72.4 | 16.56 | No | 2021-02-24 | B2_s2_d1 | 0.55 | 8.5 | 16.6 | 648 | 116.7 | B2 | 72.9 | 0.23 | s2 | y | n | d1
TN_2021_2859 |  | 80651 20350704 | 10-H91902 | ARG16R16 1X240MM2 - 0.6/1 KV | 25.89 | 6 | Vilanova | 1.7MMSHEATH54ABSPIT | CD | 72.2 | 18.74 | No | 2021-02-24 | C_s2_d2 | 1.08 | 22.1 | 41.7 | 1095 | 110.3 | C | 257.5 | 0.59 | s2 | n | y | d2
TN_2021_2864 | Abrera | 83931482 20193654 | 814822B | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.14 | 15 | Vilanova | 1420+1602 | CD | 74.4 | 12.36 | No | 2021-02-25 | D_s1_d1 | 2.26 | 36.7 | 50.3 | 1077 | 95.7 | D | 43.2 | 0.09 | s1 | y | n | d1
TN_2021_2865 |  | 84024181 20193679 | 855603D | AFUMEX CLASS 1KV RZ1-K (AS) 5G4 | 14.71 | 10 | Vilanova | 0.50400+1.241602 | CD | 73.3 | 12.4 | No | 2021-02-25 | C_s1_d2 | 1.25 | 24.7 | 36.8 | 1050 | 54.4 | C | 24.6 | 0.06 | s1 | n | y | d2
TN_2021_2866 |  | 84107135 20193658 | 857305D | AFUMEX CLASS 1KV RZ1-K (AS) 3G10 | 15.3 | 10 | Vilanova | 0400+1602 | CD | 70.4 | 16.45 | No | 2021-02-25 | C_s1_d2 | 1.25 | 22.9 | 37.8 | 1125 | 45.9 | C | 13.3 | 0.03 | s1 | n | y | d2
TN_2021_2867 |  | 84024181 20193679 | 855449L | AFUMEX CLASS 1KV RZ1-K (AS) 5G4 | 13.98 | 11 | Vilanova | 0.30400+1.241602 | CD | 67.6 | 19.12 | No | 2021-02-25 | D_s1_d2 | 3.3 | 67.5 | 158.2 | 1476 | 137.1 | D | 46.1 | 0.11 | s1 | n | y | d2
TN_2021_2868 |  | 80341 20302921 | 845615X | EZHELLENT COMPACT RZ1-K (AS) 5G1.5 | 11.74 | 13 | Vilanova | TPR+COTTON+0400+TPR-54 | CD | 62.3 | 20.97 | No | 2021-02-25 | B2_s1_d0 | 0.56 | 11.9 | 18.6 | 723 | 44 | B2 | 9.4 | 0.02 | s1 | n | n | d0
TN_2021_2869 |  | 20359193 82103 | 845281J | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.02 | 14 | Vilanova | 1.241602/TPR-54 | CD | 72.6 | 12.19 | No | 2021-02-28 | D_s2_d2 | 3.3 | 48.7 | 97.3 | 1500 | 87.7 | D | 95.9 | 0.24 | s2 | n | y | d2
TN_2021_2870 |  | 20359194 82102 | 845277E | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.16 | 17 | Vilanova | 1.241602/TPR-54 | CD | 70.6 | 12.39 | No | 2021-02-28 | E ou F_s2_d2 | 3.3 | 75.3 | 165.8 | 1308 | 164.4 | E ou F | 119 | 0.35 | s2 | n | y | d2
TN_2021_2871 |  | 84024181 20193679 | 855603D | AFUMEX CLASS 1KV RZ1-K (AS) 5G4 | 14.71 | 10 | Vilanova | 0.50400+1.241602 | CD | 69.3 | 15.44 | No | 2021-02-28 | C_s1_d2 | 1.4 | 24.2 | 37.3 | 1416 | 45.6 | C | 18.6 | 0.04 | s1 | n | y | d2
TN_2021_2872 |  | 84024181 20193679 | 855449L | AFUMEX CLASS 1KV RZ1-K (AS) 5G4 | 13.98 | 11 | Vilanova | 0.30400+1.241602 | CD | 59.3 | 17.21 | No | 2021-02-28 | D_s1_d2 | 3.3 | 44 | 82.6 | 1494 | 76.1 | D | 31.8 | 0.1 | s1 | n | y | d2
TN_2021_2873 |  | 84107135 20193658 | 857305D | AFUMEX CLASS 1KV RZ1-K (AS) 3G10 | 15.3 | 10 | Vilanova | 0400+1602 | CD | 56.7 | 17.31 | No | 2021-02-28 | C_s1_d1 | 1.1 | 17.5 | 32.2 | 1230 | 36.8 | C | 20.9 | 0.04 | s1 | y | n | d1
TN_2021_2877 |  | 80341 20302921 | 845615X | EZHELLENT COMPACT RZ1-K (AS) 5G1.5 | 11.74 | 13 | Vilanova | TPR+COTTON+0400+TPR-54 | CD | 67 | 13.13 | No | 2021-03-02 | B2_s1_d1 | 0.7 | 11.1 | 22.4 | 837 | 45.6 | B2 | 20 | 0.04 | s1 | y | n | d1
TN_2021_2878 |  | 84024181 20193679 | 855449L | AFUMEX CLASS 1KV RZ1-K (AS) 5G4 | 13.98 | 11 | Vilanova | 0.30400+1.241602 | CD | 65.3 | 13.24 | No | 2021-03-02 | D_s1_d2 | 3.3 | 43.6 | 88.9 | 1500 | 80.7 | D | 33.6 | 0.1 | s1 | n | y | d2
TN_2021_2879 |  | 84024181 20193679 | 855603D | AFUMEX CLASS 1KV RZ1-K (AS) 5G4 | 14.71 | 10 | Vilanova | 0.50400+1.241602 | CD | 72 | 14.24 | No | 2021-03-02 | C_s1_d2 | 1.67 | 29.5 | 43 | 1323 | 56.6 | C | 29.6 | 0.06 | s1 | n | y | d2
TN_2021_2880 |  | 20359193 82103 | 845281J | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.02 | 14 | Vilanova | 1.241602/TPR-54 | CD | 72.1 | 15.25 | No | 2021-03-02 | E ou F_s2_d2 | 3.3 | 82.6 | 193.3 | 1335 | 192.1 | E ou F | 176.4 | 0.54 | s2 | n | y | d2
TN_2021_2881 |  | 20359194 82102 | 845277E | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.16 | 17 | Vilanova | 1.241602/TPR-54 | CD | 70.9 | 16.51 | No | 2021-03-02 | E ou F_s2_d2 | 3.3 | 78.4 | 202.5 | 1347 | 194.3 | E ou F | 113.8 | 0.43 | s2 | n | y | d2
210300001 |  | 18597 | EL0YVTS | MC-72/12 95/125-SH-K209B-2Z1 GENERAL CABLE 6 -09/11/2020-B2CAS1AD1.A1.CE | 16.52 | 9 | Paron | VPE913+RUBANPOLY+FRP+TPR248+RUBANACIER+TPS246 | -- | 28 | 20.6 | No | 2021-03-01 | B2_s1_d1 | 0.55 | 9.9 | 15.8 | 930 | 25.2 | B2 | 23.5 | 0.04 | s1 | y | n | d1
210300002 |  | 18597 | EL0YVTS | MC-72/12 95/125-SH-K209B-2Z1 GENERAL CABLE 6 -09/11/2020-B2CAS1AD1.A1.CE | 16.52 | 9 | Paron | VPE913+RUBANPOLY+FRP+TPR248+RUBANACIER+TPS246 | -- | 29.3 | 20.3 | No | 2021-03-01 | B2_s1_d1 | 0.45 | 7.3 | 10.9 | 903 | 20.2 | B2 | 13.8 | 0.03 | s1 | y | n | d1
210300003 |  | 18597 | GL0PGVS | GENERAL CABLE 6 HERSATENE 1911 2020 NF C33-226 50 AL 12/20 (24KV) EC =0.15 C1 ISH | 28.92 | 6 | Paron | TPS246–GAINERISHILOFABRIQUÉEÀMTCÀMONTEREAU+CATALYSEUR+COLORANT | -- | 28 | 22.4 | No | 2021-03-01 | B2_s1_d2 | 0.55 | 10.9 | 24.8 | 1500 | 20.7 | B2 | 16.4 | 0.05 | s1 | y | y | d2
TN_2021_2882 |  | 20359193 82103 | 845281J | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.02 | 14 | Vilanova | 1.241602/TPR-54 | CD | 74.5 | 12.79 | No | 2021-03-03 | D_s2_d2 | 3.3 | 37.8 | 62.4 | 1425 | 60.1 | D | 71.9 | 0.19 | s2 | n | y | d2
TN_2021_2883 |  | 20359194 82102 | 845277E | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 9.16 | 17 | Vilanova | 1.241602/TPR-54 | CD | 72.5 | 13.19 | No | 2021-03-03 | E ou F_s2_d2 | 3.3 | 85.5 | 212.1 | 1218 | 231.6 | E ou F | 125.9 | 0.36 | s2 | n | y | d2
TN_2021_2884 |  | 80341 20302921 | 845615X | EZHELLENT COMPACT RZ1-K (AS) 5G1.5 | 11.74 | 13 | Vilanova | TPR+COTTON+0400+TPR-54 | CD | 71.4 | 14.44 | No | 2021-03-03 | B2_s1_d1 | 0.69 | 11 | 21.3 | 810 | 42.7 | B2 | 16.1 | 0.03 | s1 | y | n | d1
TN_2021_2885 |  | 84107135 20193658 | 857305D | AFUMEX CLASS 1KV RZ1-K (AS) 3G10 | 15.3 | 10 | Vilanova | 0400+1602 | CD | 69 | 18.81 | No | 2021-03-03 | C_s1_d1 | 0.89 | 16.6 | 29.6 | 1242 | 31.5 | C | 17.8 | 0.04 | s1 | y | n | d1
TN_2021_2886 |  | 20303241 84067617 | 845083U | EXZHELLENT CLASS RZ1 (AS) 1KV 1X50 | 14.04 | 11 | Vilanova | CUBIERTATPR-37 | CD | 74.2 | 11.41 | No | 2021-03-04 | B2_s1_d2 | 0.54 | 10.6 | 15.2 | 1170 | 47.3 | B2 | 13.9 | 0.04 | s1 | n | y | d2
TN_2021_2889 | Abrera | 20193675 83956944 | 838261D | AFUMEX CLASS 1KV RZ1-K (AS) 4G10 | 16.96 | 9 | Vilanova | 1420+1602 | CD | 73.4 | 12.37 | No | 2021-03-04 | B2_s1_d0 | 0.46 | 5.9 | 11 | 1455 | 20.3 | B2 | 8.6 | 0.02 | s1 | n | n | d0
TN_2021_2890 |  | 20307850 84134772 | 876967A | EXAVB CCA S3 D2 A3 1KV 4G25 | 29.08 | 6 | Vilanova | CUBIERTAPVC-13 | CD | 73.5 | 15.21 | No | 2021-03-04 | B2_s2_d1 | 0.82 | 13.8 | 27.6 | 1491 | 36.7 | B2 | 313.8 | 0.39 | s2 | y | n | d1
TN_2021_2891 | Abrera | 20302921 88940722 | 838020S | EZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 11.73 | 13 | Vilanova | 0400+TPR-54 | CD | 68.5 | 16.68 | No | 2021-03-04 | B2_s1_d0 | 0.36 | 6.6 | 11.3 | 792 | 43.6 | B2 | 6.8 | 0.01 | s1 | n | n | d0
TN_2021_2892 | Abrera | 20193677 84009551 | 865713T | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.45 | 13 | Vilanova | 1420+1602 | CD | 68 | 17 | No | 2021-03-04 | D_s1_d0 | 2.07 | 33.5 | 53 | 1353 | 64.5 | D | 23.2 | 0.07 | s1 | n | n | d0
TN_2021_2897 | Abrera | 20302916 84171957 | 837906T | EZHELLENT COMPACT RZ1-K (AS) 1KV 4X10 | 16.21 | 9 | Vilanova | 0400+TPR-54 | CD | 71.7 | 11.42 | No | 2021-03-05 | B2_s1_d2 | 0.57 | 9 | 13.9 | 1410 | 25.9 | B2 | 4.9 | 0.01 | s1 | n | y | d2
TN_2021_2898 | Abrera | 20302899 83566120 | 738407S | EZHELLENT COMPACT RZ1-K (AS) 1KV 3G1.5 | 9.88 | 15 | Vilanova | 0400+TPR-54 | CD | 69 | 14.7 | No | 2021-03-05 | B2_s1_d0 | 0.79 | 9.4 | 18.3 | 843 | 45 | B2 | 14.3 | 0.04 | s1 | n | n | d0
TN_2021_2899 | Abrera | 20193677 84009551 | 865713T | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.45 | 13 | Vilanova | 1420+1602 | CD | 67.8 | 15.79 | No | 2021-03-05 | D_s1_d2 | 2.22 | 40 | 56.1 | 1203 | 86.6 | D | 39.7 | 0.08 | s1 | n | y | d2
TN_2021_2900 | Abrera | 20193675 83956944 | 838261D | AFUMEX CLASS 1KV RZ1-K (AS) 4G10 | 16.96 | 9 | Vilanova | 1420+1602 | CD | 66.6 | 17.04 | No | 2021-03-05 | B2_s1_d0 | 0.44 | 5 | 9.4 | 1500 | 24.9 | B2 | 3.9 | 0.01 | s1 | n | n | d0
TN_2021_2901 | Abrera | 20302916 84171957 | 837906T | EZHELLENT COMPACT RZ1-K (AS) 1KV 4X10 | 16.21 | 9 | Vilanova | 0400+TPR-54 | CD | 74.4 | 12.47 | No | 2021-03-08 | B2_s1_d0 | 0.39 | 5.6 | 6.8 | 1320 | 26.1 | B2 | 0 | 0 | s1 | n | n | d0
TN_2021_2902 | Abrera | 20302921 88940722 | 838020S | EZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 11.73 | 13 | Vilanova | 0400+TPR-54 | CD | 74.2 | 12.69 | No | 2021-03-08 | B2_s1_d0 | 0.48 | 8.3 | 17.6 | 789 | 38.2 | B2 | 11.8 | 0.04 | s1 | n | n | d0
TN_2021_2903 | Abrera | 83931482 20193654 | 814822B | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.14 | 15 | Vilanova | 1420+1602 | CD | 75 | 13.68 | No | 2021-03-08 | D_s1_d1 | 2.43 | 42.5 | 58.7 | 801 | 117.1 | D | 38.1 | 0.07 | s1 | y | n | d1
TN_2021_2904 | Abrera | 20302899 83566120 | 738407S | EZHELLENT COMPACT RZ1-K (AS) 1KV 3G1.5 | 9.88 | 15 | Vilanova | 0400+TPR-54 | CD | 74.2 | 14.76 | No | 2021-03-08 | B2_s1_d0 | 0.47 | 7.9 | 15.6 | 765 | 49.5 | B2 | 9 | 0.02 | s1 | n | n | d0
21030007 |  | 18566 | CBP167557 | HINKLEY POINT 4*50 1 KV ALU- SH- CE6780A | 29.83 | 6 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 35.7 | 18 | No | 2021-03-08 | B2_s1_d0 | 0.3 | 3.1 | 4.9 | 657 | 17.3 | B2 | 6.6 | 0.01 | s1 | n | n | d0
21030008 |  | 18566 | DBP165354 | HINKLEY POINT 1*185 1KV CU-SH- CE6777B | 27.13 | 6 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 29.6 | 18.1 | No | 2021-03-08 | B2_s1_d0 | 0.4 | 1.9 | 5.6 | 522 | 20.3 | B2 | 4.2 | 0.01 | s1 | n | n | d0
21030009 |  | 18566 | DBP165354 | HINKLEY POINT 1*185 1KV CU-SH- CE6777B | 27.13 | 6 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 29.1 | 18.5 | No | 2021-03-08 | B2_s1_d0 | 0.4 | 2.7 | 6 | 573 | 27 | B2 | 15.2 | 0.02 | s1 | n | n | d0
21030011 |  | 18566 | CBP167557 | HINKLEY POINT 4*50 1 KV ALU- SH- CE6780A | 29.83 | 6 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 30.2 | 20.7 | No | 2021-03-10 | B2_s1_d0 | 0.25 | 3.5 | 5.5 | 594 | 21 | B2 | 7 | 0.01 | s1 | n | n | d0
21030010 |  | 18566 | FBM188061 | HINKLEY POINT 2X185 1KV CU-6779B | 40.47 | 5 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 29.3 | 20.3 | No | 2021-03-10 | B2_s1_d0 | 0.6 | 3.6 | 5.9 | 693 | 17 | B2 | 13 | 0.02 | s1 | n | n | d0
21030012 |  | 18566 | FBM188061 | HINKLEY POINT 2X185 1KV CU-6779B | 40.47 | 5 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 45.6 | 21.2 | No | 2021-03-11 | B2_s1_d0 | 0.5 | 4.6 | 6.7 | 807 | 21 | B2 | 16 | 0.02 | s1 | n | n | d0
21030004 |  | 18597 | HL0C99S | GENERAL CABLE 6 HERSATENE 210-2020-25KV-630MM² CU- CONCENTRIC-LSOH | 74.39 | 3 | Paron | TPS246–GAINERISHILOFABRIQUÉEÀMTCÀMONTEREAU+CATALYSEUR+COLORANT | -- | 42.5 | 19 | No | 2021-03-04 | B2_s1_d0 | 0.3 | 5.2 | 6.3 | 924 | 14.8 | B2 | 8.9 | 0.01 | s1 | n | n | d0
21030005 |  | 18597 | GL0MR1S | GENERAL CABLE 6 HERSATENE 55 2020 NF C33-226-240 A12/20 (24) KV EC=0.15-C1-ISH | 37.45 | 5 | Paron | TPS246–GAINERISHILOFABRIQUÉEÀMTCÀMONTEREAU+CATALYSEUR+COLORANT | -- | 40.6 | 19.8 | No | 2021-03-04 | B2_s1_d1 | 0.55 | 6.5 | 11.6 | 1413 | 18.9 | B2 | 13.5 | 0.02 | s1 | y | n | d1
21030006 |  | 18597 | HL09R1S | HTA-K20-12/20 (24) KV-AL-240MM² - EC-0.15-10/2020 SILEC-221 B2CA.S1A.D1.A1 | 37.45 | 5 | Paron | TPS246–GAINERISHILOFABRIQUÉEÀMTCÀMONTEREAU+CATALYSEUR+COLORANT | -- | 40.9 | 19.2 | No | 2021-03-04 | B2_s1_d0 | 0.45 | 6.3 | 10.4 | 1467 | 20.7 | B2 | 8.1 | 0.02 | s1 | n | n | d0
21030015 | Paron | 18566 |  | HINKLEY POINT 3*185 1 KV ALU -SH -CE 6780A | 49.53 | 4 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 28.9 | 20.6 | No | 2021-03-04 | B2_s1_d0 | 0.45 | 4 | 6.7 | 681 | 19 | B2 | 10 | 0.01 | s1 | n | n | d0
21030014 |  | 18600 | -- | C155543 – B00126981 - 2FO – 2000M – ACP750 201061 | 4.1 | 75 | Paron |  | -- | 40.3 | 21.6 | No | 2021-03-11 | B2_s1_d0 | 0.75 | 8.6 | 23.3 | 606 | 93 | B2 | 6 | 0.02 | s1 | n | n | d0
21030013 |  | 18600 | -- | C155544 – B00127385 - 1FO – 2000M – ACP750 240715 | 4.1 | 75 | Paron |  | -- | 48.4 | 20 | No | 2021-03-11 | B2_s1_d0 | 0.6 | 7.2 | 19.9 | 534 | 88 | B2 | 5 | 0.01 | s1 | n | n | d0
21030016 | Paron | 18566 |  | HINKLEY POINT 3*185 1 KV ALU -SH -CE 6780A | 49.53 | 4 | Paron | IX2200FR+0400FEIT+SW3100FR | -- | 37.8 | 19.9 | No | 2021-03-12 | B2_s1_d0 | 0.6 | 5.1 | 7.2 | 663 | 20 | B2 | 10 | 0.01 | s1 | n | n | d0
21030017 | Paron | 18566 |  | HINKLEY POINT 1*800 15 KV CU-EC-SH-CE6810B | 58 | 4 | Paron | HFDC4202+CE7600FR+SW3100FR | -- | 39 | 19.5 | No | 2021-03-12 | B2_s1_d0 | 0.45 | 3.1 | 4.3 | 996 | 11 | B2 | 8 | 0.01 | s1 | n | n | d0
21030018 | Paron | 18566 |  | HINKLEY POINT 1*800 15 KV CU-EC-SH-CE6810B | 58 | 4 | Paron | HFDC4202+CE7600FR+SW3100FR | -- | 39 | 19.5 | No | 2021-03-12 | B2_s1_d0 | 0.45 | 4.9 | 6.2 | 678 | 17 | B2 | 9 | 0.01 | s1 | n | n | d0
TN_2021_2906 | SANTANDER | 121 | FBA-20K2207-1 | 24F UT VTVT MEGOLON | 11.48 | 14 | Vilanova | PC/PBTUTVTVTFILLED+MEGOLON+MEGOLON | CD | 53.9 | 10.4 | No | 2021-03-15 | D_s2_d0 | 3.3 | 44.4 | 65.7 | 837 | 130.1 | D | 87.5 | 0.19 | s2 | n | n | d0
TN_2021_2907 | SANTANDER | 120 60093726 | FE130A 21K0046-1 | 24F UT VTVT AFUMEX | 11.73 | 13 | Vilanova | PC/PBTUTVTVTFILLED+AFUMEXCPR+AFUMEXCPR | CD | 50.1 | 11.25 | No | 2021-03-15 | E ou F_s2_d1 | 3.3 | 82.5 | 127.3 | 1029 | 201.3 | E ou F | 100 | 0.13 | s2 | y | n | d1
TN_2021_2908 | SANTANDER | 115 60094434 | E130 20K0320-1 | 48F LT-FR VT V2 AFO443 | 10.41 | 15 | Vilanova | PBT-FR+GELFRFILLED-FRAFUMEXCPR | CD | 44.5 | 16.84 | No | 2021-03-15 | D_s2_d0 | 2.7 | 31.2 | 54.6 | 711 | 141.3 | D | 69.2 | 0.12 | s2 | n | n | d0
TN_2021_2909 | SANTANDER | 116 60094340 | AA 20K1827-1 | 16F LT-FR KT AFO444 | 10.68 | 14 | Vilanova | PBT-FR+GELFRFILLED-FRAFUMEXCPR | CD | 45.7 | 17.65 | No | 2021-03-15 | D_s2_d2 | 2.18 | 30.8 | 53 | 882 | 111.3 | D | 65 | 0.09 | s2 | n | y | d2
TN_2021_2910 | SANTANDER | 117 60094341 | E130 20K0115-1 | 64F LT-FR KT AFO445 | 12.57 | 12 | Vilanova | PBT-FR+GELFRFILLED-FRAFUMEXCPR | CD | 44.2 | 20.3 | No | 2021-03-15 | C_s2_d2 | 1.53 | 22.9 | 59.2 | 753 | 148.7 | C | 105.3 | 0.35 | s2 | n | y | d2
TN_2021_2911 | SANTANDER | 119 | FBA-20K2431-1 | 12F UT VTVT MEGOLON | 10.65 | 14 | Vilanova | PC/PBTUTVTVTFILLED+MEGOLON+MEGOLON | CD | 43.5 | 21.96 | No | 2021-03-15 | D_s1_d0 | 2.1 | 33.5 | 57.1 | 726 | 151.4 | D | 39.3 | 0.06 | s1 | n | n | d0
TN_2021_2912 | SANTANDER | 111 60091337 | E153 6734-1 | 48F LT-FR VT V1 AFO424 | 10.07 | 15 | Vilanova | PBT-FR+GELFRFILLED-FRAFUMEXCPR | CD | 47.7 | 18.12 | No | 2021-03-15 | D_s2_d0 | 3.3 | 51 | 70.9 | 834 | 161.1 | D | 86.4 | 0.14 | s2 | n | n | d0
21030019 | Paron | 18566 |  | HINKLEY POINT 48*0.5 500V CU-BLG-SH-CE6783 A | 25.5 | 6 | Paron | IX2200FR+3100GVFR+SW3100FR | -- | 45.5 | 18.1 | No | 2021-03-15 | B2_s1_d0 | 0.25 | 2.5 | 3.9 | 582 | 13 | B2 | 5 | 0.01 | s1 | n | n | d0
21030020 | Paron | 18566 |  | HINKLEY POINT 48*0.5 500V CU-BLG-SH-CE6783 A | 25.5 | 6 | Paron | IX2200FR+3100GVFR+SW3100FR | -- | 42.8 | 18.9 | No | 2021-03-15 | B2_s1_d0 | 0.25 | 1.8 | 1.8 | 765 | 7 | B2 | 3 | 0 | s1 | n | n | d0
TN_2021_2913 | SANTANDER | 118 60093725 | FE130 20K0531-1 | 12F UT VTVT AFUMEX | 11.38 | 14 | Vilanova | PC/PBTUTVTVTFILLED+AFUMEXCPR+AFUMEXCPR | CD | 51.3 | 16.18 | No | 2021-03-15 | E ou F_s1_d0 | 3.3 | 81.8 | 121.7 | 1152 | 181.1 | E ou F | 44.2 | 0.09 | s1 | n | n | d0
TN_2021_2914 | Abrera | 83037 20352260 | 888188X | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.74 | 13 | Vilanova | 0.51420+2000 | CD | 49.1 | 12.22 | No | 2021-03-16 | D_s2_d2 | 3.3 | 57.3 | 124.7 | 1500 | 103.9 | D | 67.7 | 0.14 | s2 | n | y | d2
TN_2021_2915 | Abrera | 83038 203522260 | 888132L | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.88 | 13 | Vilanova | 0.50400+2000 | CD | 46.9 | 18.34 | No | 2021-03-16 | C_s1_d1 | 1.34 | 17.7 | 26.4 | 846 | 54.7 | C | 39.6 | 0.08 | s1 | y | n | d1
TN_2021_2916 | Abrera | 83035 203522260 | 887121M | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.71 | 13 | Vilanova | 0.50420+16HI | CD | 44.4 | 21.13 | No | 2021-03-16 | C_s1_d2 | 1.43 | 20.6 | 33.3 | 1047 | 62.5 | C | 29.8 | 0.05 | s1 | n | y | d2
TN_2021_2917 | Abrera | 83036 203522260 | 888162U | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.85 | 13 | Vilanova | 0.50400+16HI | CD | 43.8 | 21.52 | No | 2021-03-16 | C_s1_d2 | 0.92 | 14.4 | 36 | 792 | 73.8 | C | 14.7 | 0.04 | s1 | n | y | d2
TN_2021_2918 | Abrera | 88613 20361424 | 888133M | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.76 | 13 | Vilanova | 0.30400+1.4WT2205 | CD | 44 | 21.03 | No | 2021-03-16 | C_s1_d1 | 1.32 | 18.2 | 36.7 | 810 | 76.9 | C | 27 | 0.06 | s1 | y | n | d1
TN_2021_2919 | Abrera | 82623 20361428 | 888197G | FG16OM16 3G1.5 | 10.43 | 15 | Vilanova | 1.8WT2205 | CD | 51 | 13.69 | No | 2021-03-17 | E ou F_s2_d2 | 3.3 | 103.3 | 247.2 | 1212 | 281.8 | E ou F | 206.3 | 0.56 | s2 | n | y | d2
TN_2021_2920 | Abrera | 82619 20361425 | 888134N | FG16OM16 5G1.5 | 13 | 12 | Vilanova | 0.50400+1.8WT2205 | CD | 48.3 | 18.96 | No | 2021-03-17 | C_s1_d2 | 1.12 | 17.9 | 41.6 | 864 | 73.9 | C | 30.3 | 0.07 | s1 | n | y | d2
TN_2021_2921 | Abrera | 82821 20362078 | 888189Y | FG16OM16 5G1.5 | 11.71 | 13 | Vilanova | 1.8WT2205 | CD | 48.8 | 20.16 | No | 2021-03-17 | E ou F_s2_d2 | 3.3 | 122.2 | 315.5 | 1068 | 410.8 | E ou F | 242.3 | 0.75 | s2 | n | y | d2
TN_2021_2922 | Abrera | 83037 20352260 | 888188X | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.74 | 13 | Vilanova | 0.51420+2000 | CD | 44.5 | 23.21 | No | 2021-03-17 | E ou F_s2_d2 | 3.3 | 85.9 | 217.4 | 1452 | 188.9 | E ou F | 106.2 | 0.4 | s2 | n | y | d2
TN_2021_2923 | Abrera | 83038 20352260 | 888132L | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.88 | 13 | Vilanova | 0.50400+2000 | CD | 47.4 | 20.37 | No | 2021-03-17 | C_s1_d1 | 0.83 | 15.9 | 31.9 | 789 | 67.3 | C | 41.2 | 0.08 | s1 | y | n | d1
TN_2021_2924 | Abrera | 88613 20361424 | 888133M | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.76 | 13 | Vilanova | 0.30400+1.4WT2205 | CD | 48.3 | 19.9 | No | 2021-03-17 | D_s2_d1 | 3.3 | 50.3 | 80.5 | 1491 | 88.8 | D | 60.7 | 0.13 | s2 | y | n | d1
TN_2021_2925 | Abrera | 83035 20352260 | 887121M | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.71 | 13 | Vilanova | 0.50420+16HI | CD | 54.8 | 16.54 | No | 2021-03-17 | C_s1_d1 | 0.81 | 13.7 | 32 | 759 | 69.6 | C | 18.2 | 0.04 | s1 | y | n | d1
TN_2021_2926 | Abrera | 83036 20352260 | 888162U | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.85 | 13 | Vilanova | 0.50400+16HI | CD | 54.9 | 15.54 | No | 2021-03-17 | C_s1_d1 | 1.13 | 18 | 32.2 | 798 | 66.6 | C | 20.3 | 0.03 | s1 | y | n | d1
21030021 | Paron | 18566 |  | HINKLEY POINT 24P1.0 500V BG NA-SH-CE 6783 C | 32 | 6 | Paron | IX2200FR+3100GVFR+SW3100FR | - | 37.4 | 20.2 | No | 2021-03-16 | B2_s1_d0 | 0.25 | 5.1 | 8 | 663 | 29 | B2 | 8 | 0.01 | s1 | n | n | d0
21030022 | Paron | 18566 |  | HINKLEY POINT 24P1.0 500V BG NA-SH-CE 6783 C | 32 | 6 | Paron | IX2200FR+3100GVFR+SW3100FR | - | 38.6 | 21.3 | No | 2021-03-16 | B2_s1_d0 | 0.25 | 5.6 | 7.2 | 678 | 28 | B2 | 6 | 0.01 | s1 | n | n | d0
21030024 | Paron | 18566 |  | HINKLEY POINT 1*800 15 KV CU -EC-SH-CE 6810 A | 62.07 | 3 | Paron | HFDC4202+CE7600FR+SW3100FR | - | 32.3 | 20.7 | No | 2021-03-16 | B2_s1_d0 | 0.55 | 6.7 | 8.2 | 1317 | 23 | B2 | 9 | 0.01 | s1 | n | n | d0
21030025 | Paron | 18566 |  | HINKLEY POINT 1*800 15 KV CU -EC-SH-CE 6810 A | 62.07 | 3 | Paron | HFDC4202+CE7600FR+SW3100FR | - | 33.2 | 20.8 | No | 2021-03-16 | B2_s1_d0 | 0.55 | 3 | 4.8 | 720 | 14 | B2 | 7 | 0.01 | s1 | n | n | d0
21030026 | Paron | 18566 |  | HINKLEY POINT 2*10 500V CU-BLG-SH-CE6783 B | 15.4 | 9 | Paron | IX2200FR+3100GVFR+SW3100FR | - | 32.1 | 21.8 | No | 2021-03-17 | B2_s1_d0 | 0.3 | 5.1 | 8.8 | 1431 | 15 | B2 | 6 | 0.01 | s1 | n | n | d0
21030027 | Paron | 18566 |  | HINKLEY POINT 2*10 500V CU-BLG-SH-CE6783 B | 15.4 | 9 | Paron | IX2200FR+3100GVFR+SW3100FR | - | 33.7 | 21 | No | 2021-03-17 | B2_s1_d0 | 0.75 | 8.7 | 16.5 | 1185 | 20 | B2 | 39 | 0.07 | s1 | n | n | d0
TN_2021_2927 | Abrera | 82619 20361425 | 888134N | FG16OM16 5G1.5 | 13 | 12 | Vilanova | 0.50400+1.8WT2205 | CD | 54.3 | 10.94 | No | 2021-03-18 | C_s1_d1 | 0.7 | 16.9 | 28.5 | 873 | 69 | C | 16.6 | 0.04 | s1 | y | n | d1
TN_2021_2928 | Abrera | 82821 20362078 | 888189Y | FG16OM16 5G1.5 | 11.71 | 13 | Vilanova | 1.8WT2205 | CD | 47 | 18.34 | No | 2021-03-18 | E ou F_s2_d2 | 3.3 | 116.7 | 262.9 | 1182 | 298.7 | E ou F | 259.7 | 0.66 | s2 | n | y | d2
TN_2021_2929 | Abrera | 82623 20361428 | 888197G | FG16OM16 3G1.5 | 10.43 | 15 | Vilanova | 1.8WT2205 | CD | 39.3 | 21.59 | No | 2021-03-18 | E ou F_s2_d2 | 3.3 | 94.6 | 230.2 | 1341 | 222.9 | E ou F | 202.8 | 0.56 | s2 | n | y | d2
TN_2021_2930 | Abrera | 82427 20302921 | 850929Y | EZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 11.8 | 13 | Vilanova | 0.60400+1.24TPR-54 | CD | 37.7 | 18.94 | No | 2021-03-18 | C_s1_d2 | 1.21 | 18.9 | 24.8 | 789 | 51 | C | 27.2 | 0.05 | s1 | n | y | d2
TN_2021_2934 | Abrera | 84187359 20193692 | 5096393 | AFUMEX CLASS 1KV RZ1-K (AS) 4G1.5 | 11.04 | 13 | Vilanova | 0.50400+1.241602 | CD | 65.9 | 10.77 | No | 2021-03-19 | C_s1_d1 | 1.27 | 20 | 29.1 | 842 | 57.7 | C | 42.4 | 0.11 | s1 | y | n | d1
TN_2021_2935 | Abrera | 84187359 20193692 | 5096393 | AFUMEX CLASS 1KV RZ1-K (AS) 4G1.5 | 11.04 | 13 | Vilanova | 0.50400+1.241602 | CD | 61.7 | 10.83 | No | 2021-03-19 | B2_s1_d1 | 0.72 | 14 | 22.9 | 834 | 43 | B2 | 33 | 0.07 | s1 | y | n | d1
TN_2021_2936 | SANTANDER | 117-B 60094341 | E130 20K0115-2 | 64F LT-FR KT AFO445 | 11.71 | 13 | Vilanova | PBT-FR+GELFRFILLED-FRAFUMEXCPR | CD | 60.1 | 11.29 | No | 2021-03-19 | D_s2_d1 | 1.59 | 31.4 | 76.2 | 711 | 210.5 | D | 141.1 | 0.41 | s2 | y | n | d1
TN_2021_2937 | SANTANDER | 116-B 60094341 | AA 20K1827-2 | 16F LT-FR KT AFO444 | 10.63 | 14 | Vilanova | PBT-FR+GELFRFILLED-FRAFUMEXCPR | CD | 57.1 | 12.44 | No | 2021-03-19 | D_s2_d1 | 2.28 | 35.6 | 64.9 | 834 | 134.3 | D | 63.7 | 0.12 | s2 | y | n | d1
TN_2021_2938 | SANTANDER | 111-B 60091337 | E153 6734-2 | 48F LT-FR VT V1 AFO424 | 10.07 | 15 | Vilanova | PBT-FR+GELFRFILLED-FRAFUMEXCPR | CD | 50.7 | 13.32 | No | 2021-03-19 | D_s2_d0 | 2.37 | 26.8 | 49.3 | 726 | 129.2 | D | 54.9 | 0.1 | s2 | n | n | d0
TN_2021_2939 | Abrera | 84135414 20193681 | 857901B | AFUMEX CLASS 1KV RZ1-K (AS) 5G10 | 18.68 | 8 | Vilanova | 0.314201.401602 | CD | 55.6 | 7.2 | No | 2021-03-20 | C_s1_d2 | 1.06 | 18 | 40.9 | 1422 | 37 | C | 18.5 | 0.05 | s1 | n | y | d2
TN_2021_2940 | Abrera | 82427 20302921 | 850929Y | EZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 11.8 | 13 | Vilanova | 0.60400+1.24TPR-54 | CD | 50.4 | 8.42 | No | 2021-03-20 | C_s1_d1 | 1.19 | 19.8 | 28.3 | 828 | 53.9 | C | 25.3 | 0.06 | s1 | y | n | d1
TN_2021_2941 | SANTANDER | 115-B 60094434 | E130 20K0320-2 | 48F LT-FR VT V2 AFO443 | 10.47 | 15 | Vilanova | PBT-FR+GELFRFILLED-FRAFUMEXCPR | CD | 48.1 | 10.19 | No | 2021-03-20 | D_s2_d0 | 3.1 | 35.4 | 58.7 | 711 | 151.3 | D | 72.9 | 0.13 | s2 | n | n | d0
TN_2021_2942 | Abrera | 84135414 20193681 | 857901B | AFUMEX CLASS 1KV RZ1-K (AS) 5G10 | 18.68 | 8 | Vilanova | 0.314201.401602 | CD | 44.8 | 13.42 | No | 2021-03-20 | C_s1_d2 | 0.96 | 16.4 | 34.7 | 1317 | 36.3 | C | 20.2 | 0.04 | s1 | n | y | d2
TN_2021_2943 | SANTANDER | 120 60093726 | FE130A 21K0046-2 | 24F UT VTVT AFUMEX | 11.74 | 13 | Vilanova | PC/PBTUTVTVTFILLED+AFUMEXCPR+AFUMEXCPR | CD | 44.7 | 11.27 | No | 2021-03-22 | E ou F_s2_d1 | 3.3 | 79.1 | 103.8 | 1200 | 166.9 | E ou F | 93.1 | 0.13 | s2 | y | n | d1
TN_2021_2944 | SANTANDER | 118 60093725 | FE130 20K0531-2 | 12F UT VTVT AFUMEX | 10.75 | 14 | Vilanova | PC/PBTUTVTVTFILLED+AFUMEXCPR+AFUMEXCPR | CD | 39.7 | 17.97 | No | 2021-03-22 | D_s2_d0 | 3.3 | 69.4 | 123.1 | 1035 | 203 | D | 60.9 | 0.1 | s2 | n | n | d0
TN_2021_2945 | SANTANDER | 119 | FBA-20K2431-2 | 12F UT VTV MEGOLON | 10.65 | 14 | Vilanova | PC/PBTUTVTVTFILLED+MEGOLON+MEGOLON | CD | 34.5 | 23.2 | No | 2021-03-22 | C_s1_d0 | 1.71 | 26.1 | 52.4 | 675 | 148.7 | C | 38.5 | 0.07 | s1 | n | n | d0
TN_2021_2946 | SANTANDER | 121 | FBA-20K2207-2 | 24F UT VTVT MEGOLON | 11.49 | 14 | Vilanova | PC/PBTUTVTVTFILLED+MEGOLON+MEGOLON | CD | 33.8 | 20.9 | No | 2021-03-22 | D_s2_d0 | 3.3 | 60.1 | 83.2 | 1470 | 133.4 | D | 69.1 | 0.11 | s2 | n | n | d0
TN_2021_2947 | Abrera | 84009539 20193651 | 856588Z | AFUMEX CLASS 1KV RZ1-K (AS) 2X6 | 12.47 | 13 | Vilanova | 1420+1602 | CD | 34.6 | 20.41 | No | 2021-03-22 | C_s1_d1 | 1.52 | 21.3 | 27.9 | 1284 | 48 | C | 14.7 | 0.06 | s1 | y | n | d1
TN_2021_2948 | Abrera | 84009539 20193651 | 856588Z | AFUMEX CLASS 1KV RZ1-K (AS) 2X6 | 12.47 | 13 | Vilanova | 1420+1602 | CD | 47.6 | 15.93 | No | 2021-03-22 | B2_s1_d0 | 0.71 | 13.7 | 22.5 | 930 | 49.6 | B2 | 23.8 | 0.09 | s1 | n | n | d0
TN_2021_2949 | Abrera | 84009539 20193651 | 856588Z | AFUMEX CLASS 1KV RZ1-K (AS) 2X6 | 12.47 | 13 | Vilanova | 1420+1602 | CD | 52.1 | 15.06 | No | 2021-03-22 | C_s1_d0 | 1.74 | 27.9 | 39.2 | 1254 | 48.3 | C | 20.8 | 0.07 | s1 | n | n | d0
TN_2021_2950 | Abrera | 84187354 20193657 | 857202S | AFUMEX CLASS 1KV RZ1-K (AS) 3G6 | 13.26 | 12 | Vilanova | 0400+1602 | CD | 43.2 | 19.86 | No | 2021-03-23 | C_s1_d2 | 1.39 | 23.5 | 35.1 | 1065 | 52 | C | 26.7 | 0.08 | s1 | n | y | d2
TN_2021_2951 | Abrera | 84187357 20193657 | 857200P | AFUMEX CLASS 1KV RZ1-K (AS) 3G6 | 13.34 | 12 | Vilanova | 1420+1602 | CD | 47.2 | 20.35 | No | 2021-03-23 | D_s1_d2 | 2.14 | 34.5 | 53.7 | 1257 | 68.8 | D | 34.7 | 0.1 | s1 | n | y | d2
TN_2021_2952 | Abrera | 84187354 20193657 | 857202S | AFUMEX CLASS 1KV RZ1-K (AS) 3G6 | 13.26 | 12 | Vilanova | 0400+1602 | CD | 43 | 21.18 | No | 2021-03-23 | C_s1_d1 | 1.13 | 17.3 | 28.3 | 1038 | 38.7 | C | 26.8 | 0.07 | s1 | y | n | d1
TN_2021_2953 | Abrera | 84187357 20193657 | 857200P | AFUMEX CLASS 1KV RZ1-K (AS) 3G6 | 13.34 | 12 | Vilanova | 1420+1602 | CD | 45.4 | 21.18 | No | 2021-03-23 | D_s1_d2 | 1.87 | 32.2 | 46.2 | 1167 | 63 | D | 29.3 | 0.07 | s1 | y | y | d2
CEL 0077-21-1 |  | 80746 20353805 | 864561R | HEPRHZ1-2OL 10KV 1X300 MM2 | 44.9 | 4 | CEIS | 0400FEIT1.46MM+61AASEES2.96MM | CD | 48 | 20.4 | No | 2021-03-04 | B2_s1_d0 | 0.7 | 10.9 | 13.3 | 957 | 29.9 | B2 | 3.5 | 0.01 | s1 | n | n | d0
CEL 1095-20-1 |  | 83931469 20193657 | 802544F | AFUMEX CLASS 1KV RZ1-K (AS) 3G6 | 13.75 | 11 | CEIS | 1420+1602 | CD | 57.6 | 21.42 | No | 2021-03-16 | C_s1_d0 | 1 | 24.6 | 38.33 |  | 64.29 | C | 7.29 | 0.06 | s1 | n | n | d0
TN_2021_2954 | Giovinazzo | 80652 20350706 | 10-H91901 | ARG16R16 1X240MM2 - 0.6/1 KV | 25.11 | 7 | Vilanova | 1.2MMSHEATH54ABSPIT | CD | 49.8 | 18.05 | No | 2021-03-23 | C_s2_d2 | 1 | 24.8 | 44.4 | 1311 | 57.7 | C | 271.8 | 0.49 | s2 | y | y | d2
TN_2021_2955 | Giovinazzo | 80651 20350704 | 10-H91902 | ARG16R16 1X240MM2 - 0.6/1 KV | 25.89 | 6 | Vilanova | 1.7MMSHEATH54ABSPIT | CD | 55.6 | 16.22 | No | 2021-03-23 | C_s2_d2 | 0.92 | 21.8 | 39.7 | 1221 | 70.5 | C | 269.4 | 0.5 | s2 | y | y | d2
TN_2021_2956 | Abrera | 84187354 20193657 | 857202S | AFUMEX CLASS 1KV RZ1-K (AS) 3G6 | 13.26 | 12 | Vilanova | 0400+1602 | CD | 66.9 | 10.46 | No | 2021-03-24 | C_s1_d2 | 1.28 | 23.5 | 35.8 | 996 | 54.7 | C | 30.1 | 0.13 | s1 | n | y | d2
TN_2021_2957 | Abrera | 84187357 20193657 | 857200P | AFUMEX CLASS 1KV RZ1-K (AS) 3G6 | 13.34 | 12 | Vilanova | 1420+1602 | CD | 64.7 | 11.35 | No | 2021-03-24 | D_s1_d2 | 1.71 | 30.1 | 41.5 | 1035 | 62.2 | D | 33.9 | 0.1 | s1 | n | y | d2
TN_2021_2958 | Abrera | 82427 20302921 | 850929Y | EZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 11.8 | 13 | Vilanova | 0.60400+1.24TPR-54 | CD | 58.2 | 18.46 | No | 2021-03-24 | C_s1_d1 | 1.11 | 16.5 | 22.3 | 849 | 42.4 | C | 27.2 | 0.04 | s1 | y | n | d1
TN_2021_2959 | Abrera | 82427 20302921 | 850929Y | EZHELLENT COMPACT RZ1-K (AS) 1KV 5G1.5 | 11.8 | 13 | Vilanova | 0.60400+1.24TPR-54 | CD | 54.3 | 20.75 | No | 2021-03-24 | C_s1_d2 | 1.02 | 17.2 | 28.4 | 843 | 54.7 | C | 27.9 | 0.06 | s1 | n | y | d2
TN_2021_2960 | Abrera | 82612 20361249 | 829717S | AFUMEX CLASS RZ1-K (AS) 5G1.5 | 11.6 | 13 | Vilanova | 0.30400+1.4WT2203 | CD | 53.3 | 21.16 | No | 2021-03-24 | E ou F_s2_d2 | 3.3 | 100.2 | 250.8 | 1299 | 251.1 | E ou F | 159.3 | 0.61 | s2 | n | y | d2
TN_2021_2962 | Abrera | 82618 20362095 | 829716R | FG16OM16 5G1.5 | 12.82 | 12 | Vilanova | 0.50400+1.8WT2203 | CD | 63.9 | 11.48 | No | 2021-03-25 | B2_s1_d1 | 0.67 | 13.9 | 24.6 | 876 | 58.6 | B2 | 11 | 0.03 | s1 | y | n | d1
TN_2021_2963 | Abrera | 82622 20361413 | 829719U | FG16OM16 3G1.5 | 10.16 | 15 | Vilanova | 1.8WT2203 | CD | 61.3 | 11.73 | No | 2021-03-25 | E ou F_s2_d2 | 3.3 | 104.5 | 271.8 | 1140 | 328.7 | E ou F | 188.9 | 0.58 | s2 | n | y | d2
TN_2021_2964 | Abrera | 82822 20361411 | 829715P | FG16OM16 5G1.5 | 11.69 | 13 | Vilanova | 1.8WT2203 | CD | 60.4 | 16.58 | No | 2021-03-25 | E ou F_s2_d2 | 3.3 | 123.9 | 362 | 1233 | 398.4 | E ou F | 201 | 0.7 | s2 | n | y | d2
TN_2021_2965 | Abrera | 82618 20362095 | 829716R | FG16OM16 5G1.5 | 12.82 | 12 | Vilanova | 0.50400+1.8WT2203 | CD | 60.3 | 19.22 | No | 2021-03-25 | B2_s1_d1 | 0.55 | 14.8 | 25.3 | 804 | 63.2 | B2 | 5.9 | 0.03 | s1 | y | n | d1
TN_2021_2966 | Abrera | 82622 20361413 | 829719U | FG16OM16 3G1.5 | 10.16 | 15 | Vilanova | 1.8WT2203 | CD | 61.1 | 19.78 | No | 2021-03-25 | E ou F_s2_d2 | 3.3 | 103 | 300.1 | 1080 | 386.1 | E ou F | 184.4 | 0.6 | s2 | n | y | d2
TN_2021_2970 | Abrera | 82612 20361249 | 829717S | AFUMEX CLASS RZ1-K (AS) 5G1.5 | 11.6 | 13 | Vilanova | 0.30400+1.4WT2203 | CD | 58.7 | 11.64 | No | 2021-03-29 | C_s1_d0 | 1.44 | 19 | 33.4 | 801 | 77.2 | C | 28.1 | 0.07 | s1 | n | n | d0
TN_2021_2971 | Abrera | 83037 20352260 | 888188X | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.74 | 13 | Vilanova | 0.51420+2000 | CD | 54.8 | 11.82 | No | 2021-03-29 | E ou F_s2_d2 | 3.3 | 74.4 | 155.4 | 1437 | 137.6 | E ou F | 87.5 | 0.27 | s2 | n | y | d2
TN_2021_2972 | Abrera | 83035 20352260 | 887121M | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.71 | 13 | Vilanova | 0.50420+16HI | CD | 52.1 | 15.24 | No | 2021-03-29 | C_s1_d2 | 1.54 | 23.3 | 35.9 | 1050 | 67.5 | C | 23.1 | 0.04 | s1 | n | y | d2
TN_2021_2973 | Santander | 119-C | FBA-20K2431-3 | 12F UT VTVT MEGOLON | 10.53 | 13 | Vilanova | PC/PBTUTVTVTFILLED+MEGOLON+MEGOLON | CD | 50.4 | 19.9 | No | 2021-03-29 | D_s2_d0 | 2.17 | 32.3 | 53.3 | 678 | 155.5 | D | 56.5 | 0.09 | s2 | n | n | d0
TN_2021_2974 | Santander | 121-C | FBA-20K2207-2 | 24F UT VTVT MEGOLON | 11.41 | 13 | Vilanova | PC/PBTUTVTVTFILLED+MEGOLON+MEGOLON | CD | 39.8 | 21.58 | No | 2021-03-29 | D_s2_d0 | 3.3 | 58.7 | 75.7 | 1332 | 141.3 | D | 71.9 | 0.13 | s2 | n | n | d0
TN_2021_2975 | Abrera | 83036 20352260 | 888162U | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.85 | 13 | Vilanova | 0.50400+16HI | CD | 38.5 | 23.42 | No | 2021-03-29 | C_s1_d1 | 0.72 | 11.8 | 30.4 | 786 | 62.6 | C | 19.8 | 0.04 | s1 | y | n | d1
TN_2021_2976 | Abrera | 82822 20361411 | 829715P | FG16OM16 5G1.5 | 11.69 | 13 | Vilanova | 1.8WT2203 | CD | 37.3 | 24.08 | No | 2021-03-29 | E ou F_s2_d2 | 3.3 | 118.9 | 356.6 | 1125 | 447.1 | E ou F | 218.2 | 0.77 | s2 | y | y | d2
TN_2021_2977 | Abrera | 83038 20352260 | 888132L | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.88 | 13 | Vilanova | 0.50400+2000 | CD | 38.2 | 19.79 | No | 2021-03-29 | D_s1_d1 | 2.02 | 27.5 | 42.8 | 1104 | 66 | D | 39.6 | 0.08 | s1 | y | n | d1
TN_2021_2978 | Abrera | 82612 20361249 | 829717S | AFUMEX CLASS RZ1-K (AS) 5G1.5 | 11.6 | 13 | Vilanova | 0.30400+1.4WT2203 | CD | 41.8 | 17.77 | No | 2021-03-29 | E ou F_s2_d2 | 3.3 | 86.9 | 217.7 | 1416 | 196.1 | E ou F | 139.3 | 0.56 | s2 | y | y | d2
TN_2021_2979 | Cavinova | 841522006 20046508 | 20M0219 | AFUMEX XHIZ1 6/10 KV 1X50 L1 | 27.7 | 6 | Vilanova | 14202.5MM+DMZ-E2.3MM | CD | 49.5 | 13.39 | No | 2021-03-30 | B2_s1_d2 | 0.63 | 10 | 29.2 | 1497 | 24.4 | B2 | 1.5 | 0.03 | s1 | n | y | d2
TN_2021_2980 | Cavinova | 841522006 20046508 | 20M0219 | AFUMEX XHIZ1 6/10 KV 1X50 L1 | 27.7 | 6 | Vilanova | 14202.5MM+DMZ-E2.3MM | CD | 48.8 | 13.65 | No | 2021-03-30 | B2_s1_d2 | 0.69 | 7.9 | 20.5 | 1497 | 21.7 | B2 | 11.9 | 0.04 | s1 | n | y | d2
TN_2021_2981 | Abrera | 88613 20361424 | 888133M | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.76 | 13 | Vilanova | 0.30400+1.4WT2205 | CD | 47.3 | 16.77 | No | 2021-03-30 | B2_s1_d1 | 0.54 | 8.1 | 19.2 | 684 | 50 | B2 | 15.3 | 0.04 | s1 | y | n | d1
TN_2021_2982 | Abrera | 82619 20361425 | 888134N | FG16OM16 5G1.5 | 13 | 12 | Vilanova | 0.50400+1.8WT2205 | CD | 46.4 | 20.99 | No | 2021-03-30 | B2_s1_d1 | 0.69 | 9.9 | 18.1 | 976 | 44.5 | B2 | 12.9 | 0.02 | s1 | y | n | d1
TN_2021_2983 | Abrera | 82821 20362078 | 888189Y | FG16OM16 5G1.5 | 11.71 | 13 | Vilanova | 1.8WT2205 | CD | 44.1 | 22.34 | No | 2021-03-30 | E ou F_s2_d2 | 3.3 | 115.8 | 292 | 1314 | 299.6 | E ou F | 248.2 | 0.72 | s2 | n | y | d2
TN_2021_2989 | Cavinova | 82341 20286494 | 809448K | RHZ1-RA+2OL(AS) 45KV 1X630K AL+H165 | 68.49 | 3 | Vilanova | DMZ-2 | CD | 50.1 | 12 | No | 2021-03-31 | B2_s1_d0 | 0.65 | 9.3 | 10.9 | 813 | 36.9 | B2 | 7.3 | 0.02 | s1 | n | n | d0
TN_2021_2990 | Abrera | 82623 20361428 | 888197G | FG16OM16 3G1.5 | 10.43 | 15 | Vilanova | 1.8WT2205 | CD | 48.4 | 11.65 | No | 2021-03-31 | E ou F_s2_d2 | 3.3 | 99.5 | 257.6 | 1239 | 285.2 | E ou F | 191.3 | 0.64 | s2 | n | y | d2
TN_2021_2991 | Abrera | 84187359 20193692 | 5096393 | AFUMEX CLASS 1KV RZ1-K (AS) 4G1.5 | 11.04 | 13 | Vilanova | 0.50400+1.241602 | CD | 48.1 | 13.46 | No | 2021-03-31 | C_s1_d1 | 1.18 | 15.2 | 21.3 | 873 | 44.2 | C | 28.7 | 0.07 | s1 | y | n | d1
TN_2021_2992 | Abrera | 84135414 20193681 | 857901B | AFUMEX CLASS 1KV RZ1-K (AS) 5G10 | 18.68 | 8 | Vilanova | 0.314201.401602 | CD | 44.8 | 15.61 | No | 2021-03-31 | B2_s1_d2 | 0.69 | 9.1 | 19.3 | 1500 | 29.1 | B2 | 13.5 | 0.03 | s1 | n | y | d2
TN_2021_2993 | Cavinova | 82341 20286494 | 809448K | RHZ1-RA+2OL(AS) 45KV 1X630K AL+H165 | 68.49 | 3 | Vilanova | DMZ-2 | CD | 44.7 | 19.64 | No | 2021-03-31 | B2_s1_d0 | 0.7 | 10.1 | 11.9 | 1032 | 33.6 | B2 | 22 | 0.04 | s1 | n | n | d0
TN_2021_2996 | Sta Perpetua | 82562 20360356 | 874600C | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.96 | 8 | Vilanova | COOPERTAPE+0400+1602 | CD | 59.8 | 12.29 | No | 2021-04-06 | D_s2_d2 | 1.58 | 44.3 | 108.5 | 1191 | 122.2 | D | 133.8 | 0.28 | s2 | n | y | d2
TN_2021_2997 | Sta Perpetua | 82563 20360357 | 874613S | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.1 | 8 | Vilanova | COOPERTAPE+MICA+0400+1602 | CD | 54 | 13.12 | No | 2021-04-06 | C_s1_d2 | 0.92 | 21.4 | 37.3 | 1347 | 38.9 | C | 20.1 | 0.06 | s1 | n | y | d2
TN_2021_2998 | Sta Perpetua | 82563 20360357 | 874613S | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 18.1 | 8 | Vilanova | COOPERTAPE+MICA+0400+1602 | CD | 50.9 | 16.71 | No | 2021-04-06 | C_s1_d2 | 1.1 | 23.6 | 48 | 1500 | 43.4 | C | 32.1 | 0.09 | s1 | n | y | d2
TN_2021_2999 | Sta Perpetua | 82562 20360356 | 874600C | AFUMEX CIRCUITO SERIE RHZ1 (AS) 5KV 1X6MM² (BALIZAS) | 17.96 | 8 | Vilanova | COOPERTAPE+0400+1602 | CD | 45.4 | 20.73 | No | 2021-04-06 | D_s2_d2 | 2.13 | 41.7 | 83.6 | 1287 | 85.1 | D | 127.4 | 0.23 | s2 | n | y | d2
TN_2021_3003 | Abrera | 82377 20302804 | 5096394 | EXZH CLASS ES05Z1-K (AS) 1X1 | 2.31 | 270 | Vilanova | TPR-52-TPR-45 | CD | 56.4 | 13.02 | No | 2021-04-07 | B2_s1_d1 | 1.32 | 11.7 | 20.4 | 852 | 81.9 | B2 | 37.5 | 0.09 | s1 | y | n | d1
TN_2021_3004 | ITALY | 84108775 20215631 | T7-F84374 | FG16OM16 10G1.5 - 0.6/1 KV | 17.27 | 9 | Vilanova | 0300FDIT+5300SEIT | CD | 50.89 | 12.79 | No | 2021-04-07 | B2_s1_d1 | 0.36 | 4.8 | 8 | 1395 | 23.7 | B2 | 4.5 | 0.01 | s1 | y | n | d1
TN_2021_3005 | ITALY | 84106270 20215465 | T8-I88534 | FG16OR16 7G1.5 - 0.6/1 KV | 14.46 | 11 | Vilanova | 05AMFPIT+20AHSEIT | CD | 46.1 | 13.31 | No | 2021-04-07 | B2_s2_d1 | 1.12 | 14.8 | 24.5 | 816 | 78.6 | B2 | 369.1 | 0.67 | s2 | y | n | d1
TN_2021_3006 | Cavinova | 81748 20046508 | 863291K | AFUMEX XHIZ1 6/10 KV 3X1X50 | 54.8 | 4 | Vilanova | 1420+DMZ-E | CD | 47.1 | 14.03 | No | 2021-04-07 | B2_s1_d1 | 0.54 | 7.1 | 9.9 | 1947 | 21.8 | B2 | 9.7 | 0.02 | s1 | y | n | d1
TN_2021_3007 | Cavinova | 81748 20046508 | 863291K | AFUMEX XHIZ1 6/10 KV 3X1X50 | 54.8 | 4 | Vilanova | 1420+DMZ-E | CD | 45 | 14.97 | No | 2021-04-07 | B2_s1_d0 | 0.57 | 6.1 | 8 | 891 | 17.8 | B2 | 10.8 | 0.03 | s1 | n | n | d0
TN_2021_3011 | ITALY | 84108775 20215631 | T7-F84374 | FG16OM16 10G1.5 - 0.6/1 KV | 17.27 | 9 | Vilanova | 0300FDIT+5300SEIT | CD | 55.4 | 11.94 | No | 2021-04-08 | B2_s1_d1 | 0.42 | 8.8 | 14.6 | 1311 | 34.8 | B2 | 0.1 | 0 | s1 | y | n | d1
TN_2021_3012 | ITALY | 84106270 20215465 | T8-I88534 | FG16OR16 7G1.5 - 0.6/1 KV | 14.46 | 11 | Vilanova | 05AMFPIT+20AHSEIT | CD | 55.7 | 11.46 | No | 2021-04-08 | C_s3_d0 | 1.1 | 18.2 | 35.8 | 759 | 78.3 | C | 413.4 | 0.85 | s3 | n | n | d0
TN_2021_3013 | Portugal | 84211650 20303244 | 895996J | EXZHELLENT CLASS RZ1 (AS) 1KV 1X120AL VD | 18.62 | 8 | Vilanova | TPR-55 | CD | 51.7 | 15.23 | No | 2021-04-08 | B2_s1_d2 | 0.44 | 6.4 | 9.2 | 1458 | 29.9 | B2 | 8.2 | 0.02 | s1 | n | y | d2
TN_2021_3014 | Portugal | 84200817 20303248 | 887142K | EXZHELLENT CLASS RZ1 (AS) 1KV 1X300 AL VD | 27.34 | 6 | Vilanova | TPR-55 | CD | 47.4 | 15.37 | No | 2021-04-08 | B2_s1_d1 | 0.44 | 5.9 | 8.7 | 1500 | 33.1 | B2 | 2.5 | 0.01 | s1 | y | n | d1
TN_2021_3015 | Abrera | 84064285 20193680 | 852626T | AFUMEX CLASS 1KV RZ1-K (AS) 5G6 | 15.82 | 9 | Vilanova | 0.31420+1.401602 | CD | 42.3 | 18.02 | No | 2021-04-08 | B2_s1_d2 | 0.7 | 12 | 21 | 1323 | 29.3 | B2 | 15.4 | 0.04 | s1 | n | y | d2
TN_2021_3016 | Abrera | 841873685 20193681 | 852538X | AFUMEX CLASS 1KV RZ1-K (AS) 5G10 | 18.82 | 8 | Vilanova | 0.30400+1.241602 | CD | 60.2 | 10.47 | No | 2021-04-09 | C_s1_d2 | 0.92 | 17 | 28.8 | 1320 | 28.4 | C | 6.1 | 0.02 | s1 | n | y | d2
TN_2021_3017 | Abrera | 83931689 20302814 | 5096367 | EXZHELLENT H07Z1-K 1X1.5 NE | 2.88 | 165 | Vilanova | 1602+TPR-53 | CD | 59.5 | 10.56 | No | 2021-04-09 | D_s2_d1 | 2.57 | 23.4 | 41.6 | 660 | 132.6 | D | 67.9 | 0.13 | s2 | y | n | d1
TN_2021_3018 | Abrera | 83984851 20193980 | 5096373 | AFUMEX CLASS H07Z1-K 1X1.5 AZ | 2.89 | 165 | Vilanova | 1420/1602 | CD | 61.8 | 11 | No | 2021-04-09 | C_s1_d0 | 1.57 | 15.1 | 35 | 672 | 121.7 | C | 48 | 0.11 | s1 | n | n | d0
TN_2021_3019 | Abrera | 84064285 20193680 | 852626T | AFUMEX CLASS 1KV RZ1-K (AS) 5G6 | 15.82 | 9 | Vilanova | 0.31420+1.401602 | CD | 58.6 | 14.44 | No | 2021-04-09 | C_s1_d2 | 0.78 | 15.8 | 28.5 | 1257 | 32.9 | C | 15.1 | 0.03 | s1 | n | y | d2
TN_2021_3020 | Abrera | 841873685 20193681 | 852538X | AFUMEX CLASS 1KV RZ1-K (AS) 5G10 | 18.82 | 8 | Vilanova | 0.30400+1.241602 | CD | 56.3 | 16.23 | No | 2021-04-09 | B2_s1_d2 | 0.89 | 14.6 | 29 | 1332 | 28.1 | B2 | 11.7 | 0.03 | s1 | n | y | d2
TN_2021_3021 | Abrera | 84064285 20193680 | 852626T | AFUMEX CLASS 1KV RZ1-K (AS) 5G6 | 15.82 | 9 | Vilanova | 0.31420+1.401602 | CD | 79 | 14.07 | No | 2021-04-11 | C_s1_d2 | 0.91 | 17.4 | 35.5 | 1491 | 31.2 | C | 23.3 | 0.05 | s1 | n | y | d2
TN_2021_3022 | Abrera | 83919121 20193980 | 5096371 | AFUMEX CLASS H07Z1-K 1X1.5 MARR | 2.87 | 165 | Vilanova | 1420+1602 | CD | 75.7 | 15.12 | No | 2021-04-11 | C_s1_d0 | 1.46 | 13.8 | 37.6 | 615 | 129.8 | C | 41.5 | 0.16 | s1 | n | n | d0
TN_2021_3023 | Abrera | 841873685 20193681 | 852538X | AFUMEX CLASS 1KV RZ1-K (AS) 5G10 | 18.82 | 8 | Vilanova | 0.30400+1.241602 | CD | 73.5 | 15.54 | No | 2021-04-11 | B2_s1_d2 | 0.8 | 13.5 | 23.9 | 1341 | 27.8 | B2 | 5.1 | 0.01 | s1 | n | y | d2
TN_2021_3024 | Abrera | 83931674 20302828 | 5096369 | EXZHELLENT H07Z1-K 1X4 NE | 4 | 90 | Vilanova | 1602/TPR-53 | CD | 71.7 | 11.82 | No | 2021-04-12 | C_s2_d0 | 1.51 | 14.1 | 29.8 | 732 | 82.7 | C | 50.4 | 0.13 | s2 | n | n | d0
TN_2021_3025 | Portugal | 84200817 20303248 | 887142K | EXZHELLENT CLASS RZ1 (AS) 1KV 1X300 AL VD | 27.34 | 6 | Vilanova | TPR-55 | CD | 70.8 | 11.97 | No | 2021-04-12 | B2_s1_d2 | 0.6 | 11.6 | 29.9 | 1500 | 26.3 | B2 | 10.8 | 0.04 | s1 | n | y | d2
TN_2021_3029 | Cavinova | 82341 20286494 | 809448K | RHZ1-RA+2OL(AS) 45KV 1X630K AL+H165 | 68.49 | 3 | Vilanova | DMZ-2 | CD | 61.8 | 11.39 | No | 2021-04-13 | B2_s1_d2 | 0.66 | 9.8 | 10.8 | 678 | 33.1 | B2 | 9 | 0.03 | s1 | n | y | d2
TN_2021_3030 | Cavinova | 841522006 20046508 | 20M0219 | AFUMEX XHIZ1 6/10 KV 1X50 L1 | 27.7 | 6 | Vilanova | 14202.5MM+DMZ-E2.3MM | CD | 57.1 | 13.34 | No | 2021-04-13 | C_s1_d2 | 0.74 | 12.6 | 40.6 | 1500 | 33.8 | C | 17.7 | 0.06 | s1 | n | y | d2
TN_2021_3031 | Abrera | 83827583 20302833 | 5096370 | EXZHELLENT H07Z1-K 1X6 AZ | 4.51 | 60 | Vilanova | 1602/TPR-53 | CD | 58.7 | 16.77 | No | 2021-04-13 | B2_s1_d0 | 1.1 | 10.3 | 21.2 | 669 | 67.4 | B2 | 29.6 | 0.08 | s1 | n | n | d0
TN_2021_3032 | Abrera | 83827559 20302822 | 5096372 | EXZHELLENT H07Z1-K 1X2.5 A/V | 3.51 | 120 | Vilanova | 1602/TPR-53 | CD | 73.6 | 14.09 | No | 2021-04-14 | C_s1_d2 | 1.93 | 18.1 | 33.8 | 756 | 78.4 | C | 39.4 | 0.08 | s1 | n | y | d2
TN_2021_3033 | Abrera | 83031356 20193993 | 5096374 | AFUMEX CLASS H07Z1-K 1X4 A/V | 4.02 | 90 | Vilanova | 1420/1602 | CD | 71.6 | 14.53 | No | 2021-04-14 | B2_s1_d0 | 0.66 | 7.3 | 15.9 | 573 | 72.3 | B2 | 8.1 | 0.02 | s1 | n | n | d0
TN_2021_3034 | Abrera | 84062390 20193987 | 5096376 | AFUMEX CLASS H07Z1-K 1X2.5 ROJ | 3.49 | 120 | Vilanova | 1420/1602 | CD | 51.5 | 17.36 | No | 2021-04-14 | C_s1_d0 | 1.54 | 15.9 | 39.8 | 684 | 110.1 | C | 46 | 0.11 | s1 | n | n | d0
CEL-0132-21-1 |  | 83742816 20267026 | 687488V | HEPRZ1 (AS) 30KV 1X630/25 | 59.22 | 4 | CEIS | HEPR+14202.3+60003 | CD | 46.6 | 27.27 | No | 2021-03-05 | C_s1_d2 | 1.17 | 21.74 | 31.78 |  | 42.89 | C | 14.24 | 0.03 | s1 | n | y | d2
TN_2021_3036 | Abrera | 83031357 20193998 | 5096377 | AFUMEX CLASS H07Z1-K 1X6 A/V | 4.5 | 60 | Vilanova | 1420/1602 | CD | 54.2 | 12.49 | No | 2021-04-16 | B2_s1_d0 | 0.69 | 4.8 | 13.8 | 588 | 66.5 | B2 | 9.6 | 0.03 | s1 | n | n | d0
TN_2021_3037 | Abrera | 83827583 20302833 | 5096370 | EXZHELLENT H07Z1-K 1X6 AZ | 4.51 | 60 | Vilanova | 1602/TPR-53 | CD | 54.7 | 12.65 | No | 2021-04-16 | B2_s1_d1 | 0.5 | 5.3 | 13.2 | 573 | 48.5 | B2 | 9.7 | 0.03 | s1 | y | n | d1
TN_2021_3038 | Abrera | 83827559 20302822 | 5096372 | EXZHELLENT H07Z1-K 1X2.5 A/V | 3.51 | 120 | Vilanova | 1602/TPR-53 | CD | 55.5 | 12.88 | No | 2021-04-16 | B2_s1_d1 | 0.81 | 8.3 | 18.2 | 708 | 61.4 | B2 | 28.6 | 0.1 | s1 | y | n | d1
TN_2021_3039 | Abrera | 83931674 20302828 | 5096369 | EXZHELLENT H07Z1-K 1X4 NE | 4 | 90 | Vilanova | 1602/TPR-53 | CD | 52.4 | 14.41 | No | 2021-04-16 | B2_s1_d0 | 1.34 | 11.4 | 25.7 | 711 | 66.7 | B2 | 45.9 | 0.15 | s1 | n | n | d0
TN_2021_3040 | Abrera | 83031356 20193993 | 5096374 | AFUMEX CLASS H07Z1-K 1X4 A/V | 4.02 | 90 | Vilanova | 1420/1602 | CD | 50.4 | 17.4 | No | 2021-04-16 | B2_s1_d0 | 0.89 | 7.1 | 17.1 | 663 | 63.5 | B2 | 26.3 | 0.07 | s1 | n | n | d0
TN_2021_3041 | Abrera | 84062390 20193987 | 5096376 | AFUMEX CLASS H07Z1-K 1X2.5 ROJ | 3.49 | 120 | Vilanova | 1420/1602 | CD | 48.8 | 10.08 | No | 2021-04-18 | C_s1_d0 | 1.45 | 15 | 31.6 | 711 | 83.2 | C | 31.7 | 0.12 | s1 | n | n | d0
TN_2021_3042 | Abrera | 83031357 20193998 | 5096377 | AFUMEX CLASS H07Z1-K 1X6 A/V | 4.5 | 60 | Vilanova | 1420/1602 | CD | 43.9 | 10.29 | No | 2021-04-18 | B2_s1_d0 | 0.37 | 3.9 | 9.8 | 606 | 41.8 | B2 | 3 | 0.01 | s1 | n | n | d0
TN_2021_3043 | Portugal | 84211650 20303244 | 895996J | EXZHELLENT CLASS RZ1 (AS) 1KV 1X120AL VD | 18.62 | 8 | Vilanova | TPR-55 | CD | 42.5 | 11.47 | No | 2021-04-18 | B2_s1_d2 | 0.8 | 10.2 | 17.6 | 1410 | 32 | B2 | 5.5 | 0.02 | s1 | n | y | d2
TN_2021_3044 | Portugal | 84158334 20302886 | 899010K | EXZHELLENT COMPACT RZ1-K (AS) 1KV 1X95 VD | 18.16 | 8 | Vilanova | TPR-55 | CD | 40.2 | 13.3 | No | 2021-04-18 | B2_s1_d1 | 0.49 | 10.8 | 13.7 | 1290 | 45.7 | B2 | 9.6 | 0.02 | s1 | y | n | d1
TN_2021_3045 | Portugal | 84158334 20302886 | 899010K | EXZHELLENT COMPACT RZ1-K (AS) 1KV 1X95 VD | 18.16 | 8 | Vilanova | TPR-55 | CD | 38.4 | 18.32 | No | 2021-04-18 | B2_s1_d2 | 0.87 | 10.9 | 20.5 | 1461 | 23.1 | B2 | 14 | 0.05 | s1 | n | y | d2
TN_2021_3046 | Abrera | 82377 20302804 | 5096394 | EXZH CLASS ES05Z1-K (AS) 1X1 | 2.31 | 270 | Vilanova | TPR-52-TPR-45 | CD | 61.3 | 11.23 | No | 2021-04-19 | D_s2_d1 | 2.19 | 34.4 | 39.2 | 903 | 98.5 | D | 79.7 | 0.14 | s2 | y | n | d1
TN_2021_3047 | ITALY | 20349888 | T7-I29734 | FTG18OM16 1X1.5 | 8.54 | 19 | Vilanova | IZ1000+0300FDIT+56ACSEIT | CD | 57 | 12.48 | No | 2021-04-19 | E ou F_s2_d2 | 3.3 | 81.3 | 219.9 | 842 | 343.8 | E ou F | 64.3 | 0.27 | s2 | n | y | d2
TN_2021_3048 | ITALY | 20349888 | T7-I29734 | FTG18OM16 1X1.5 | 8.54 | 19 | Vilanova | IZ1000+0300FDIT+56ACSEIT | CD | 54.4 | 15.44 | No | 2021-04-19 | E ou F_s2_d2 | 3.3 | 75.2 | 187.9 | 966 | 282.6 | E ou F | 69 | 0.25 | s2 | n | y | d2
TN_2021_3049 | Abrera | 84135330 20193655 | 871185R | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.28 | 14 | Vilanova | 0.50400+1.241602 | CD | 55 | 17.83 | No | 2021-04-19 | C_s1_d2 | 1.29 | 20.5 | 28.4 | 978 | 50.6 | C | 45.4 | 0.15 | s1 | n | y | d2
TN_2021_3050 | Abrera | 84135330 20193655 | 871213W | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.22 | 14 | Vilanova | 0.30400+1.241602 | CD | 55.4 | 19.2 | No | 2021-04-19 | C_s1_d1 | 1.69 | 26.5 | 34.4 | 1077 | 55.7 | C | 27.6 | 0.08 | s1 | y | n | d1
TN_2021_3051 | Abrera | 84135330 20193655 | 871185R | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.28 | 14 | Vilanova | 0.50400+1.241602 | CD | 69.6 | 13.29 | No | 2021-04-20 | C_s1_d1 | 1.12 | 18.9 | 25.4 | 894 | 49.4 | C | 37.7 | 0.09 | s1 | y | n | d1
TN_2021_3052 | Abrera | 84135330 20193655 | 871213W | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.22 | 14 | Vilanova | 0.30400+1.241602 | CD | 68 | 13.79 | No | 2021-04-20 | D_s1_d1 | 1.75 | 31.4 | 41.7 | 870 | 79.3 | D | 49.7 | 0.1 | s1 | y | n | d1
TN_2021_3053 | Abrera | 84135330 20193655 | 871185R | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.28 | 14 | Vilanova | 0.50400+1.241602 | CD | 64.1 | 15.44 | No | 2021-04-20 | C_s2_d2 | 1.3 | 22.4 | 36.8 | 915 | 59.9 | C | 53.7 | 0.14 | s2 | n | y | d2
TN_2021_3054 | Abrera | 84135330 20193655 | 871213W | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5 | 11.22 | 14 | Vilanova | 0.30400+1.241602 | CD | 62 | 17.87 | No | 2021-04-20 | C_s2_d1 | 1.76 | 30 | 39.1 | 1365 | 56.3 | C | 52.6 | 0.12 | s2 | y | n | d1
TN_2021_3055 | Santander | 60088989 | AA-15K2122 | TEST SAMPLE: 99 AFO416-1 12F VT-FR | 10.61 | 14 | Vilanova | AFUMEXCPR | CD | 74.8 | 14.63 | No | 2021-04-21 | C_s1_d0 | 1.21 | 16.6 | 32.7 | 636 | 115.2 | C | 27.8 | 0.09 | s1 | n | n | d0
TN_2021_3056 | ITALY | 82605 20361676 | 5096253 | FS18OR18 3G1.5MM2 300/500V | 6.73 | 21 | Vilanova | ISOPVC26ATIPIT | CD | 74.5 | 15.11 | No | 2021-04-21 | C_s2_d0 | 0.82 | 6.6 | 18.9 | 426 | 185.5 | C | 181 | 1.06 | s2 | n | n | d0
TN_2021_3057 | Sta Perpetua | 82325 20360646 | 883807K | AFUMEX CLASS 3KV RZ1 (AS) 1X300MM2 | 30.67 | 6 | Vilanova | XLPE+1420+1602 | CD | 72.7 | 14.98 | No | 2021-04-21 | B2_s1_d0 | 0.53 | 6.3 | 7.6 | 774 | 29.9 | B2 | 0 | 0 | s1 | n | n | d0
TN_2021_3058 | Sta Perpetua | 82325 20360646 | 883807K | AFUMEX CLASS 3KV RZ1 (AS) 1X300MM2 | 30.67 | 6 | Vilanova | XLPE+1420+1602 | CD | 72.4 | 14.55 | No | 2021-04-21 | B2_s1_d0 | 0.45 | 3.9 | 5.6 | 777 | 15.5 | B2 | 1.5 | 0 | s1 | n | n | d0
TN_2021_3059 | ITALY | 82605 20361676 | 5096253 | FS18OR18 3G1.5MM2 300/500V | 6.73 | 21 | Vilanova | ISOPVC26ATIPIT | CD | 71.6 | 16.42 | No | 2021-04-21 | C_s2_d1 | 0.51 | 4.5 | 13 | 393 | 151.9 | C | 80.5 | 0.63 | s2 | y | n | d1
TN_2021_3060 | TELECOM | 82064 60094424 | 073631J | CAREX LT-T3M1G0M2-36G652D (10683) | 16.33 | 9 | Vilanova | AFUMEX29AGINNERANDOUTERSHEATH | CD | 67.8 | 12.25 | No | 2021-04-22 | D_s1_d2 | 1.83 | 51 | 77.2 | 894 | 153.7 | D | 41.2 | 0.08 | s1 | n | y | d2
TN_2021_3061 | ENERGIA | 84135156 20313257 | 826394E | LXHIOZ1 (CBE. FRT) 1X240/16 18/30 (36) KV | 46.62 | 4 | Vilanova | 1420+6000 | CD | 63.2 | 13.33 | No | 2021-04-22 | B2_s1_d2 | 0.7 | 14.6 | 16.6 | 906 | 58.8 | B2 | 15.4 | 0.03 | s1 | n | y | d2
TN_2021_3062 | Abrera | 84024193 20193694 | 857438Y | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.19 | 13 | Vilanova | 0.50400+1.241602 | CD | 63.1 | 13.55 | No | 2021-04-22 | D_s1_d2 | 1.85 | 33.6 | 42.1 | 846 | 89.1 | D | 37.5 | 0.06 | s1 | n | y | d2
TN_2021_3063 | Abrera | 84024193 20193694 | 857438Y | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.19 | 13 | Vilanova | 0.50400+1.241602 | CD | 66.3 | 11.46 | No | 2021-04-23 | D_s1_d2 | 3.3 | 55.3 | 118.1 | 1491 | 99.2 | D | 43.5 | 0.11 | s1 | n | y | d2
TN_2021_3064 | Abrera | 84024193 20193694 | 857438Y | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.19 | 13 | Vilanova | 0.50400+1.241602 | CD | 62 | 12.33 | No | 2021-04-23 | D_s1_d2 | 3.3 | 50 | 91.6 | 1500 | 90.1 | D | 48.9 | 0.11 | s1 | n | y | d2
TN_2021_3065 | Portugal | 84200817 20303248 | 887142K | EXZHELLENT CLASS RZ1 (AS) 1KV 1X300 AL VD | 27.34 | 6 | Vilanova | TPR-55 | CD | 63.1 | 17.17 | No | 2021-04-23 | C_s1_d2 | 0.87 | 15.5 | 39.1 | 1497 | 33.8 | C | 5.6 | 0.03 | s1 | n | y | d2
TN_2021_3066 | Portugal | 84211650 20303244 | 895996J | EXZHELLENT CLASS RZ1 (AS) 1KV 1X120AL VD | 18.62 | 8 | Vilanova | TPR-55 | CD | 61.7 | 18.76 | No | 2021-04-23 | B2_s1_d2 | 0.5 | 6.8 | 10 | 1368 | 25.7 | B2 | 7.3 | 0.01 | s1 | n | y | d2
TN_2021_3067 | Abrera | 83931482 20193654 | 855842N | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.39 | 15 | Vilanova | 1420+1602 | CD | 53.7 | 16.31 | No | 2021-04-26 | C_s1_d1 | 1.71 | 26.8 | 37.2 | 903 | 64 | C | 30.1 | 0.06 | s1 | y | n | d1
TN_2021_3068 | Abrera | 84024177 20193677 | 892984K | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.95 | 13 | Vilanova | 1420+1602 | CD | 55.7 | 16.27 | No | 2021-04-26 | D_s1_d2 | 2.85 | 45.6 | 68.9 | 1305 | 81.9 | D | 33.4 | 0.07 | s1 | n | y | d2
TN_2021_3069 | Abrera | 83940722 20302921 | 814240U | EXZHELLENT COMPACT 1KV RZ1-K (AS) 5G1.5 | 11.85 | 13 | Vilanova | 0400+TPR-54 | CD | 53.8 | 17.34 | No | 2021-04-26 | C_s1_d1 | 0.96 | 15.1 | 22.6 | 831 | 43.7 | C | 7.1 | 0.02 | s1 | y | n | d1
TN_2021_3070 | Abrera | 84087418 203028141 | 5096260 | EXZHELLENT H07Z1-K 1X1.5 NE 750V | 2.87 | 165 | Vilanova | 0400+TPR-54 | CD | 51.9 | 18.53 | No | 2021-04-26 | D_s1_d1 | 3.3 | 46.9 | 77.6 | 1191 | 94.8 | D | 34.7 | 0.06 | s1 | y | n | d1
TN_2021_3071 | Abrera | 84087508 20193980 | 5096257 | AFUMEX CLASS H07Z1-K 1X1.5 NE 750V | 2.88 | 165 | Vilanova | 1420+1602 | CD | 50.7 | 18.97 | No | 2021-04-26 | C_s2_d0 | 1.7 | 16.7 | 36.7 | 660 | 118.9 | C | 54.8 | 0.14 | s2 | n | n | d0
TN_2021_3072 | Abrera | 84171957 20302916 | 885272C | EXZHELLENT COMPACT 1KV RZ1-K (AS) 4X10 | 16.08 | 9 | Vilanova | 0400+TPR-54 | CD | 69.9 | 13.61 | No | 2021-04-27 | B2_s1_d0 | 0.32 | 4.9 | 6.7 | 645 | 25.2 | B2 | 3.1 | 0.01 | s1 | n | n | d0
TN_2021_3073 | Abrera | 83566120 20302899 | 738444G | EXZHELLENT COMPACT 1KV RZ1-K (AS) 3G1.5 | 9.92 | 15 | Vilanova | 0400+TPR-54 | CD | 69.2 | 13.79 | No | 2021-04-27 | B2_s1_d0 | 1.09 | 12.2 | 18 | 666 | 49.1 | B2 | 19 | 0.04 | s1 | n | n | d0
TN_2021_3074 | Abrera | 83955944 20193675 | 865566H | AFUMEX CLASS 1KV RZ1-K (AS) 4X10 | 16.76 | 9 | Vilanova | 1420+1602 | CD | 69.3 | 14.82 | No | 2021-04-27 | B2_s1_d1 | 0.7 | 12.4 | 24.7 | 1461 | 24.8 | B2 | 6.9 | 0.02 | s1 | y | n | d1
TN_2021_3075 | Abrera | 84135375 20193987 | 5096256 | AFUMEX CLASS H07Z1-K 1X2.5 NE 750V | 3.44 | 120 | Vilanova | 1420+1602 | CD | 66.2 | 16.51 | No | 2021-04-27 | B2_s1_d0 | 1.16 | 10.5 | 24 | 666 | 83.1 | B2 | 26.1 | 0.09 | s1 | n | n | d0
TN_2021_3076 | Abrera | 84189069 20302799 | 5096261 | EXZH CLASS ES05Z1-K (AS) 1X1 | 2.47 | 240 | Vilanova | TPR-52-TPR-45 | CD | 62.5 | 18.75 | No | 2021-04-27 | B2_s2_d1 | 1.11 | 12.3 | 24.5 | 705 | 69.5 | B2 | 78.7 | 0.17 | s2 | y | n | d1
TN_2021_3077 | Abrera | 83955944 20193675 | 865566H | AFUMEX CLASS 1KV RZ1-K (AS) 4X10 | 16.76 | 9 | Vilanova | 1420+1602 | CD | 74.4 | 15.97 | No | 2021-04-28 | B2_s1_d1 | 0.7 | 10.2 | 18.4 | 1266 | 22.6 | B2 | 11.7 | 0.02 | s1 | y | n | d1
TN_2021_3078 | Abrera | 83931482 20193654 | 855842N | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5 | 10.39 | 15 | Vilanova | 1420+1602 | CD | 74.8 | 16.37 | No | 2021-04-28 | D_s2_d2 | 2.46 | 48 | 69.8 | 1500 | 97.9 | D | 51.4 | 0.09 | s2 | n | y | d2
TN_2021_3079 | Abrera | 83995630 20193993 | 5096255 | AFUMEX CLASS H07Z1-K 1X4 NE 750V | 3.98 | 90 | Vilanova | 1420+1602 | CD | 72.2 | 16.78 | No | 2021-04-28 | B2_s1_d0 | 1.11 | 10.8 | 23 | 681 | 88.1 | B2 | 25.4 | 0.07 | s1 | n | n | d0
TN_2021_3080 | Abrera | 84135422 20193998 | 5096254 | AFUMEX CLASS H07Z1-K 1X6 NE 750V | 4.54 | 60 | Vilanova | 1420+1602 | CD | 72 | 17.87 | No | 2021-04-28 | B2_s1_d0 | 0.63 | 3.9 | 11.4 | 549 | 48.4 | B2 | 1.8 | 0.01 | s1 | n | n | d0
TN_2021_3081 | Abrera | 84024177 20193677 | 892984K | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.95 | 13 | Vilanova | 1420+1602 | CD | 70.2 | 19.57 | No | 2021-04-28 | D_s1_d2 | 2.45 | 42.5 | 61.9 | 1191 | 82 | D | 23.6 | 0.07 | s1 | n | y | d2
TN_2021_3082 | Abrera | 83940722 20302921 | 814240U | EXZHELLENT COMPACT 1KV RZ1-K (AS) 5G1.5 | 11.85 | 13 | Vilanova | 0400+TPR-54 | CD | 74.8 | 16.35 | No | 2021-04-29 | B2_s1_d0 | 0.53 | 10.9 | 20 | 813 | 42.5 | B2 | 12.9 | 0.03 | s1 | n | n | d0
TN_2021_3083 | Abrera | 84171957 20302916 | 885272C | EXZHELLENT COMPACT 1KV RZ1-K (AS) 4X10 | 16.08 | 9 | Vilanova | 0400+TPR-54 | CD | 75.6 | 16.76 | No | 2021-04-29 | B2_s1_d2 | 0.58 | 10.4 | 17.4 | 1257 | 23.8 | B2 | 1.7 | 0 | s1 | n | y | d2
TN_2021_3084 | Abrera | 83566120 20302899 | 738444G | EXZHELLENT COMPACT 1KV RZ1-K (AS) 3G1.5 | 9.92 | 15 | Vilanova | 0400+TPR-54 | CD | 76.2 | 17.29 | No | 2021-04-29 | C_s1_d1 | 1.86 | 25.3 | 32.1 | 1017 | 77.3 | C | 41.9 | 0.09 | s1 | y | n | d1
TN_2021_3085 | Abrera | 84135435 20302828 | 5096258 | EXZHELLENT H07Z1-K 1X4 NE 750V | 4.03 | 90 | Vilanova | 0400+TPR-54 | CD | 72.5 | 19.36 | No | 2021-04-29 | C_s1_d0 | 1.53 | 14.2 | 21.8 | 729 | 56.2 | C | 33.7 | 0.08 | s1 | n | n | d0
TN_2021_3086 | Abrera | 84135367 20302822 | 5096259 | EXZHELLENT H07Z1-K 1X2.5 NE 750V | 3.53 | 120 | Vilanova | 0400+TPR-54 | CD | 71.9 | 20.66 | No | 2021-04-29 | D_s2_d0 | 2.11 | 23.3 | 38 | 783 | 82.8 | D | 69.5 | 0.15 | s2 | n | n | d0
TN_2021_3087 | Abrera | 83566120 20302899 | 738444G | EXZHELLENT COMPACT 1KV RZ1-K (AS) 3G1.5 | 9.92 | 15 | Vilanova | 0400+TPR-54 | CD | 78.9 | 19.23 | No | 2021-04-30 | C_s1_d0 | 1.76 | 21.4 | 27.9 | 978 | 57.6 | C | 28.3 | 0.06 | s1 | n | n | d0
21040009 |  | 18654 | CE6815 | ESS1226 A 1X400² SH- NF F 55 625- PRYSMIAN 255 DOP1011879 B2CA-S1A.D0.A1 CE K25 202/10 | 34.9 | 5 | Paron | IX1400+5300SEIT | -- | 32.6 | 21.1 | No | 2021-04-28 | B2_s1_d2 | 0.65 | 4.5 | 9.4 | 1467 | 11 | B2 | 5 | 0.01 | s1 | y | y | d2
2104007 |  | 18688 | -- | 1.8/3(3.6)KV RV- ECC- 1X95² ALU- LSOH-IEC60502-1 PRYSMIAN255- CE- 2021/15 | 24 | 7 | Paron | IX1400+0400FEIT+5300SEIT | -- | 33 | 20.6 | No | 2021-04-28 | B2_s1_d1 | 0.3 | 4.3 | 5.1 | 1110 | 18 | B2 | 4 | 0.01 | s1 | y | n | d1
21040008 |  | 18656 | CE6809 | ESS1220AA 1800 S 1X240 SH NFF55-625 CE 201/09 | 31.5 | 6 | Paron | IX1400+0400FEIT+5300SEIT | -- | 32.6 | 21.1 | No | 2021-04-28 | B2_s1_d0 | 0.35 | 4.5 | 6.1 | 894 | 17 | B2 | 4 | 0.01 | s1 | n | n | d0
21040010 |  | 18656 | CE6809 | ESS1220AA 1800 S 1X240 SH NFF55-625 CE 201/09 | 31.5 | 6 | Paron | IX1400+0400FEIT+5300SEIT | -- | 42.8 | 22.3 | No | 2021-04-28 | B2_s1_d0 | 0.4 | 5.7 | 7 | 759 | 23 | B2 | 9 | 0.01 | s1 | n | n | d0
21040011 |  | 18656 | CE6807 | CE6807-ESS1219AA 1000 S 1X240 SH NFF55-625 CE 2021/09 | 31.3 | 6 | Paron | IX1400+0400FEIT+5300SEIT | -- | 31.7 | 22.4 | No | 2021-04-30 | B2_s1_d0 | 0.4 | 4.9 | 6 | 786 | 22 | B2 | 3 | 0.01 | s1 | n | n | d0
21040012 |  | 18656 | CE6807 | CE6807-ESS1219AA 1000 S 1X240 SH NFF55-625 CE 2021/09 | 31.3 | 6 | Paron | IX1400+0400FEIT+5300SEIT | -- | 32 | 22.5 | No | 2021-04-30 | B2_s1_d0 | 0.4 | 5.4 | 6.6 | 633 | 24 | B2 | 3 | 0.01 | s1 | n | n | d0
21040013 |  | 18656 | CE6806 | CE6806-ESS1214AA 1000 S 1X240 SH NFF55-625 CE 2021/09 | 32 | 6 | Paron | IX1100+0400FEIT+5300SEIT | -- | 28.2 | 22 | No | 2021-04-30 | B2_s1_d0 | 0.4 | 5.4 | 6.7 | 726 | 26 | B2 | 4 | 0.01 | s1 | n | n | d0
21040014 |  | 18656 | CE6806 | CE6806-ESS1214AA 1000 S 1X240 SH NFF55-625 CE 2021/09 | 32 | 6 | Paron | IX1100+0400FEIT+5300SEIT | -- | 27.5 | 22.1 | No | 2021-04-30 | B2_s1_d0 | 0.4 | 4.4 | 5.6 | 861 | 17 | B2 | 7 | 0.01 | s1 | n | n | d0
21040002 |  | 18657 | CE6794 | SNCF RESEAU -SH-7P*1MM²-CT445-PRYSMIAN 255-2021-03 CE6794 | 21 | 7 | Paron | HE3366+3000GVFR+SW3800FR | -- | 26.4 | 20.3 | No | 2021-04-16 | B2_s1_d0 | 0.28 | 4.4 | 7.1 | 1365 | 18 | B2 | 5 | 0.01 | s1 | n | n | d0
21040005 |  | 18654 | CE6814 | CE6814 ESS1225 1800 A 1X400² SH- NF F 55 625- PRYSMIAN 255 DOP1011879 B2CA-S1A.D0.A1 CE K25 2021/10 | 36.9 | 5 | Paron | IX1400+0400FEIT+5300SEIT | -- | 26.9 | 19.8 | No | 2021-04-16 | B2_s1_d0 | 0.55 | 6.4 | 7.9 | 1143 | 18 | B2 | 3 | 0.01 | s1 | n | n | d0
21040004 |  | 18654 | CE6814 | CE6814 ESS1225 1800 A 1X400² SH- NF F 55 625- PRYSMIAN 255 DOP1011879 B2CA-S1A.D0.A1 CE K25 2021/10 | 36.9 | 5 | Paron | IX1400+0400FEIT+5300SEIT | -- | 27.1 | 20 | No | 2021-04-16 | B2_s1_d0 | 0.55 | 5.2 | 7.9 | 1395 | 15 | B2 | 5 | 0.01 | s1 | n | n | d0
21040003 |  | 18654 | CE6815 | CE6815 ESS1226 A 1X400² SH- NF F 55 625- PRYSMIAN 255 DOP1011879 B2CA-S1A.D0.A1 CE K25 2021/10 | 34.9 | 5 | Paron | IX1400+5300SEIT | -- | 26.8 | 19.8 | No | 2021-04-16 | B2_s1_d2 | 0.65 | 7.4 | 13.5 | 1497 | 19 | B2 | 3 | 0.01 | s1 | y | y | d2
CC_HRR_2021_003 |  |  | MR231 | AFUMEX CLASS 750V H07Z1-K(AS) TYPE2 1X25 | 8.57 | 17 | Vilanova | REFENCESAMPLE | CD | 57 | 13.45 | No | 2021-05-02 | B2_s1_d0 | 0.22 | 2.6 | 5.4 | 549 | 25.2 | B2 | 2 | 0 | s1 | n | n | d0
CC_HRR_2021_001 |  |  | MR230 | AFUMEX CLASS 750V H07Z1-K(AS) TYPE2 1X25 | 8.57 | 17 | Vilanova | REFENCESAMPLE | CD | 55.9 | 14.54 | No | 2021-05-02 | B2_s1_d0 | 0.19 | 2.1 | 4.4 | 564 | 17.2 | B2 | 1.9 | 0.01 | s1 | n | n | d0
CC_HRR_2021_002 |  |  | MR230 | AFUMEX CLASS 750V H07Z1-K(AS) TYPE2 1X25 | 8.57 | 17 | Vilanova | REFENCESAMPLE | CD | 53.7 | 16.73 | No | 2021-05-02 | B2_s1_d0 | 0.22 | 1.8 | 4.6 | 525 | 20.3 | B2 | 9.3 | 0.01 | s1 | n | n | d0
TN_2021_3088 | Abrera | 83956944 20193675 | 865566H | AFUMEX CLASS 1KV RZ1-K (AS) 4X10 | 16.76 | 9 | Vilanova | 1420+1602 | CD | 53.8 | 17.15 | No | 2021-05-02 | B2_s1_d0 | 0.51 | 7.3 | 13.7 | 1494 | 20.5 | B2 | 0.4 | 0.01 | s1 | n | n | d0
TN_2021_3089 | Abrera | 84024177 20193677 | 892984K | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.95 | 13 | Vilanova | 1420+1602 | CD | 61.7 | 16.47 | No | 2021-05-02 | D_s1_d2 | 2.62 | 39.7 | 57.1 | 1236 | 81.8 | D | 36.6 | 0.06 | s1 | n | y | d2
TN_2021_3090 | Abrera | 84087508 20193980 | 5096257 | AFUMEX CLASS H07Z1-K 1X1.5 NE 750V | 2.88 | 165 | Vilanova | 1420+1602 | CD | 62.2 | 12.26 | No | 2021-05-03 | D_s2_d0 | 2.2 | 22.1 | 47.5 | 666 | 141.1 | D | 58.3 | 0.15 | s2 | n | n | d0
TN_2021_3091 | ITALY | 80555 20353603 | T1-H93167 | FG16M16 1X240MM2 | 27.91 | 6 | Vilanova | BEDDING0300FDITSP0.35+546ACSEIT | CD | 61.2 | 12.7 | No | 2021-05-03 | B2_s1_d1 | 0.46 | 5.5 | 12.6 | 1500 | 26.2 | B2 | 0.5 | 0 | s1 | y | n | d1
TN_2021_3092 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 56.5 | 18.02 | No | 2021-05-03 | B2_s1_d0 | 1.12 | 14.4 | 26.7 | 849 | 62 | B2 | 38.6 | 0.1 | s1 | n | n | d0
TN_2021_3093 | ITALY | 80555 20353603 | T1-H93167 | FG16M16 1X240MM2 | 27.91 | 6 | Vilanova | BEDDING0300FDITSP0.35+546ACSEIT | CD | 50.8 | 20.69 | No | 2021-05-03 | B2_s1_d2 | 0.56 | 6.9 | 18.4 | 1500 | 30.6 | B2 | 2.9 | 0.01 | s1 | n | y | d2
TN_2021_3094 | ITALY | 80555 20353603 | T1-H93167 | FG16M16 1X240MM2 | 27.91 | 6 | Vilanova | BEDDING0300FDITSP0.35+546ACSEIT | CD | 43.4 | 20.62 | No | 2021-05-03 | B2_s1_d2 | 0.68 | 8 | 28 | 1497 | 29.1 | B2 | 6.7 | 0.01 | s1 | n | y | d2
TN_2021_3095 | ITALY | 83316 20362956 | T1-H93646 | ARG16R16 1X240MM2 | 26.16 | 6 | Vilanova | 05AMFPIT1MMTHICKNESS+54ACSPIT1.2MMTHICKNESS | CD | 56.3 | 12.57 | No | 2021-05-04 | C_s2_d2 | 0.94 | 13.5 | 35.1 | 1281 | 47 | C | 154.5 | 0.38 | s2 | n | y | d2
TN_2021_3096 | ITALY | 83316 20362956 | T1-H93646 | ARG16R16 1X240MM2 | 26.16 | 6 | Vilanova | 05AMFPIT1MMTHICKNESS+54ACSPIT1.2MMTHICKNESS | CD | 55.2 | 13.15 | No | 2021-05-04 | B2_s2_d2 | 0.92 | 11.8 | 20.5 | 1428 | 43.3 | B2 | 157.3 | 0.26 | s2 | n | y | d2
TN_2021_3097 | ITALY | 83316 20362956 | T1-H93646 | ARG16R16 1X240MM2 | 26.16 | 6 | Vilanova | 05AMFPIT1MMTHICKNESS+54ACSPIT1.2MMTHICKNESS | CD | 50.1 | 18.63 | No | 2021-05-04 | C_s2_d2 | 1.14 | 13.2 | 31 | 1500 | 49.5 | C | 180.6 | 0.37 | s2 | n | y | d2
TN_2021_3098 | Portugal | 84158334 20302886 | 907572S | EXZHELLENT COMPACT RZ1-K (AS) 1KV 1X95VD | 18.72 | 8 | Vilanova | TPR-55 | CD | 45.2 | 21.36 | No | 2021-05-04 | B2_s1_d0 | 0.42 | 5.9 | 6.9 | 708 | 23.2 | B2 | 0.5 | 0 | s1 | n | n | d0
TN_2021_3099 | Portugal | 82736 20361713 | 914233G | EXZHELLENT CLASS RZ1 (AS) 1KV 1X16 AL VD | 9.15 | 17 | Vilanova | TPR-55 | CD | 44.4 | 21.96 | No | 2021-05-04 | E ou F_s2_d2 | 3.3 | 72.6 | 223.5 | 1299 | 223.7 | E ou F | 173.9 | 0.69 | s2 | n | y | d2
TN_2021_3100 | Portugal | 82736 20361713 | 914233G | EXZHELLENT CLASS RZ1 (AS) 1KV 1X16 AL VD | 9.15 | 17 | Vilanova | TPR-55 | CD | 45 | 21.7 | No | 2021-05-04 | C_s1_d1 | 1.68 | 17.8 | 24.9 | 795 | 66 | C | 36.4 | 0.06 | s1 | y | n | d1
TN_2021_3101 | Portugal | 83330 20362317 | 914071F | TXXI 1KV 1X150 AL2 DCA-S2.D2.A2 | 20.17 | 8 | Vilanova | TPR-55 | CD | 43.5 | 22.71 | No | 2021-05-04 | B2_s1_d0 | 0.28 | 5.3 | 9.2 | 1461 | 24 | B2 | 1 | 0 | s1 | n | n | d0
TN_2021_3102 | Portugal | 82736 20361713 | 914233G | EXZHELLENT CLASS RZ1 (AS) 1KV 1X16 AL VD | 9.15 | 17 | Vilanova | TPR-55 | CD | 68.7 | 19.53 | No | 2021-05-05 | B2_s1_d0 | 0.57 | 8.4 | 18.4 | 633 | 56.1 | B2 | 29.5 | 0.05 | s1 | n | n | d0
TN_2021_3103 | Abrera | 83940722 20302921 | 814240U | EXZHELLENT COMPACT 1KV RZ1-K (AS) 5G1.5 | 11.85 | 13 | Vilanova | 0400+TPR-54 | CD | 66.5 | 21.58 | No | 2021-05-05 | B2_s1_d1 | 0.52 | 10.2 | 17.2 | 810 | 40 | B2 | 10.7 | 0.03 | s1 | y | n | d1
TN_2021_3104 | Abrera | 84171957 20302916 | 885272C | EXZHELLENT COMPACT 1KV RZ1-K (AS) 4X10 | 16.08 | 9 | Vilanova | 0400+TPR-54 | CD | 63.9 | 23.21 | No | 2021-05-05 | B2_s1_d2 | 0.55 | 5.5 | 11.3 | 1497 | 23 | B2 | 5.7 | 0.01 | s1 | n | y | d2
TN_2021_3105 | Top Cable |  | 5096266 | TOXFREE ZH RZ1-K 3G1.5 | 10.61 | 14 | Vilanova | COMPETITORSAMPLE | CD | 53.6 | 24.28 | No | 2021-05-05 | B2_s1_d0 | 0.32 | 5.6 | 9.8 | 654 | 35.7 | B2 | 3.8 | 0.01 | s1 | n | n | d0
TN_2021_3106 | Cavinova | 84305069 20268212 | 916681T | AL AFUMEX CLASS 1KV RZ1(AS) 1X500 | 38.57 | 5 | Vilanova | 14200.5MM+16022.1MM | CD | 62.1 | 22.98 | No | 2021-05-06 | B2_s1_d0 | 0.23 | 5.6 | 7.3 | 1500 | 23.7 | B2 | 6.5 | 0.01 | s1 | n | n | d0
TN_2021_3107 | Cavinova | 83295 20338894 | 880042T | RHZ1MAZ1+OL 66KV 1X185K + H150 DCA-S1B.D2.A1 | 60.89 | 3 | Vilanova | 14201.8MM+60002.9MM | CD | 61.8 | 22.91 | No | 2021-05-06 | B2_s1_d2 | 0.8 | 12.5 | 19.1 | 1482 | 33 | B2 | 8.7 | 0.02 | s1 | n | y | d2
TN_2021_3108 | Cavinova | 83295 20338894 | 880042T | RHZ1MAZ1+OL 66KV 1X185K + H150 DCA-S1B.D2.A1 | 60.89 | 3 | Vilanova | 14201.8MM+60002.9MM | CD | 63.1 | 21.82 | No | 2021-05-06 | B2_s1_d2 | 0.77 | 14 | 20.4 | 1500 | 37.8 | B2 | 5.2 | 0.02 | s1 | n | y | d2
TN_2021_3109 | Portugal | 84217358 20302887 | 910005L | EXZHELLENT COMPACT RZ1-K(AS) 1KV 1X120 | 19.88 | 8 | Vilanova | TPR55 | CD | 64.9 | 20.44 | No | 2021-05-06 | B2_s1_d1 | 0.48 | 7.3 | 14.9 | 1500 | 21.6 | B2 | 6.4 | 0.02 | s1 | y | n | d1
TN_2021_3110 | Top Cable |  | 5096266 | TOXFREE ZH RZ1-K 3G1.5 | 10.61 | 14 | Vilanova | COMPETITORSAMPLE | CD | 65.1 | 19.95 | No | 2021-05-06 | B2_s1_d0 | 0.27 | 6.2 | 12.7 | 669 | 40.6 | B2 | 6 | 0.02 | s1 | n | n | d0
TN_2021_3111 | Portugal | 84217358 20302887 | 910005L | EXZHELLENT COMPACT RZ1-K(AS) 1KV 1X120 | 19.88 | 8 | Vilanova | TPR55 | CD | 7.28 | 17.37 | No | 2021-05-07 | B2_s1_d2 | 0.7 | 10.9 | 21.4 | 1500 | 31.1 | B2 | 4.7 | 0.02 | s1 | n | y | d2
TN_2021_3112 | Cavinova | 84231119 20229626 | 868338W | HEPRZ1 (AS) 30 KV 1X400/25 AL-EPROTENAX | 51.26 | 4 | Vilanova | 14202.35MM+60003.00MM | CD | 71.4 | 19.96 | No | 2021-05-07 | C_s1_d2 | 0.9 | 21.2 | 34.6 | 1347 | 38.8 | C | 2.4 | 0.02 | s1 | n | y | d2
TN_2021_3113 | Cavinova | 84305069 20268212 | 916681T | AL AFUMEX CLASS 1KV RZ1(AS) 1X500 | 38.57 | 5 | Vilanova | 14200.5MM+16022.1MM | CD | 66.7 | 22.6 | No | 2021-05-07 | B2_s1_d2 | 0.47 | 7.4 | 12.2 | 1500 | 29.3 | B2 | 5.3 | 0.02 | s1 | n | y | d2
TN_2021_3114 | Cavinova | 84231119 20229626 | 868338W | HEPRZ1 (AS) 30 KV 1X400/25 AL-EPROTENAX | 51.26 | 4 | Vilanova | 14202.35MM+60003.00MM | CD | 65.6 | 23.34 | No | 2021-05-07 | C_s1_d2 | 1.07 | 15.9 | 22.7 | 1308 | 36.9 | C | 7.3 | 0.02 | s1 | n | y | d2
TN_2021_3115 | Portugal | 82736 20361713 | 914233G | EXZHELLENT CLASS RZ1 (AS) 1KV 1X16 AL VD | 9.15 | 17 | Vilanova | TPR-55 | CD | 76.6 | 17.67 | No | 2021-05-10 | E ou F_s2_d2 | 3.3 | 74.4 | 184.9 | 1239 | 196.9 | E ou F | 128.6 | 0.36 | s2 | n | y | d2
TN_2021_3116 | Portugal | 82736 20361713 | 914233G | EXZHELLENT CLASS RZ1 (AS) 1KV 1X16 AL VD | 9.15 | 17 | Vilanova | TPR-55 | CD | 74.8 | 18.48 | No | 2021-05-10 | E ou F_s2_d2 | 3.3 | 80.5 | 254.5 | 1251 | 267.7 | E ou F | 152.7 | 0.57 | s2 | n | y | d2
TN_2021_3117 | Portugal | 82736 20361713 | 914233G | EXZHELLENT CLASS RZ1 (AS) 1KV 1X16 AL VD | 9.15 | 17 | Vilanova | TPR-55 | CD | 66.5 | 19.59 | No | 2021-05-10 | E ou F_s2_d2 | 3.3 | 80.8 | 246.4 | 1146 | 292.5 | E ou F | 134.3 | 0.42 | s2 | n | y | d2
21050002 |  | 18656 | CE6808 | CE6808-ESS1215AA 1800 S 1X240 SH NFF55-625 CE 2021/09 | 32.3 | 6 | Paron |  | -- | 38.2 | 20.7 | No | 2021-05-04 | B2_s1_d0 | 0.35 | 5.7 | 6.6 | 741 | 26 | B2 | 4 | 0.01 | s1 | n | n | d0
21050001 |  | 18656 | CE6808 | CE6808-ESS1215AA 1800 S 1X240 SH NFF55-625 CE 2021/09 | 32.3 | 6 | Paron |  | -- | 37.8 | 20.5 | No | 2021-05-04 | B2_s1_d0 | 0.35 | 3.1 | 4.4 | 588 | 15 | B2 | 5 | 0.01 | s1 | n | n | d0
21050004 |  | 18690 |  | 750- S- 2X1.5²- SH- NFF55-625 -PRYSMIAN255- B2CA-S1A.D1.A1 CE- K25-2021/12 | 10.8 | 14 | Paron |  | -- | 39.9 | 19.5 | No | 2021-05-06 | B2_s1_d2 | 0.75 | 8.9 | 19.2 | 729 | 52 | B2 | 26 | 0.05 | s1 | y | y | d2
21050007 |  | 18690 |  | 750- S- 2X1.5²- SH- NFF55-625 -PRYSMIAN255- B2CA-S1A.D1.A1 CE- K25-2021/12 | 10.8 | 14 | Paron |  | -- | 47.5 | 20.2 | No | 2021-05-06 | B2_s1_d2 | 0.75 | 9.5 | 16.2 | 735 | 51 | B2 | 10 | 0.08 | s1 | y | y | d2
21050005 |  | 18690 | CE6805 | ESS1222- CE6805-1000- 1X35- SH-NFF55-625 PRYSMIAN255- B2CA-S1A.D1.A1 CE- K25- 2021/12 | 13.8 | 11 | Paron |  | -- | 40.2 | 19.5 | No | 2021-05-06 | B2_s1_d2 | 0.45 | 6.8 | 9.3 | 1236 | 27 | B2 | 4 | 0.01 | s1 | y | y | d2
21050006 |  | 18690 | CE6805 | ESS1222- CE6805-1000- 1X35- SH-NFF55-625 PRYSMIAN255- B2CA-S1A.D1.A1 CE- K25- 2021/12 | 13.8 | 11 | Paron |  | -- | 42.2 | 20.3 | No | 2021-05-06 | B2_s1_d1 | 0.45 | 6.3 | 8.8 | 1305 | 31 | B2 | 4 | 0.06 | s1 | y | n | d1
TN_2021_3118 | Abrera | 84135375 20193987 | 5096256 | AFUMEX CLASS H07Z1-K 1X2.5 NE 750V | 3.44 | 120 | Vilanova | 1420+1602 | CD | 60.9 | 21.04 | No | 2021-05-10 | B2_s1_d0 | 1.36 | 11.4 | 27.3 | 651 | 99.5 | B2 | 22.4 | 0.09 | s1 | n | n | d0
TN_2021_3119 | Abrera | 83995630 20193993 | 5096255 | AFUMEX CLASS H07Z1-K 1X4 NE 750V | 3.98 | 90 | Vilanova | 1420+1602 | CD | 57.7 | 22.15 | No | 2021-05-10 | B2_s1_d0 | 0.87 | 13.3 | 24.2 | 642 | 80.2 | B2 | 33.7 | 0.09 | s1 | n | n | d0
TN_2021_3120 | Abrera | 84189069 20302799 | 5096261 | EXZH CLASS ES05Z1-K (AS) 1X1 | 2.47 | 240 | Vilanova | TPR-52-TPR-45 | CD | 47 | 23.27 | No | 2021-05-10 | D_s1_d1 | 2.1 | 24.8 | 43.3 | 702 | 116 | D | 38.9 | 0.1 | s1 | y | n | d1
TN_2021_3121 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 34.5 | 24.91 | No | 2021-05-11 | C_s1_d0 | 1.63 | 20 | 36.2 | 882 | 67.6 | C | 44.3 | 0.08 | s1 | n | n | d0
TN_2021_3122 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 56.8 | 19.43 | No | 2021-05-12 | C_s1_d0 | 1.33 | 15.9 | 29.1 | 930 | 54.7 | C | 28.3 | 0.1 | s1 | n | n | d0
TN_2021_3123 |  | 80178 20352260 | 824301E | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 12.7 | 12 | Vilanova | E:0.7_1420+E:1.4_16HD | CD | 56.7 | 20.83 | No | 2021-05-12 | C_s1_d0 | 1.21 | 19.3 | 30 | 897 | 53.4 | C | 20.4 | 0.06 | s1 | n | n | d0
CC_HRR_2021_004 |  |  | MR233 | AFUMEX CLASS 750V H07Z1-K(AS) TYPE2 1X25 | 8.57 | 17 | Vilanova | REFENCESAMPLE | CD | 50 | 21.25 | No | 2021-05-12 | B2_s1_d0 | 0.27 | 1.1 | 3.1 | 564 | 10.7 | B2 | 8.9 | 0.02 | s1 | n | n | d0
TN_2021_3124 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 44 | 16.02 | No | 2021-05-13 | B2_s1_d0 | 1.28 | 15 | 28.6 | 879 | 66.7 | B2 | 41.7 | 0.12 | s1 | n | n | d0
TN_2021_3125 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 34 | 18.91 | No | 2021-05-13 | B2_s1_d0 | 1.24 | 14.7 | 27.3 | 840 | 69.6 | B2 | 32.2 | 0.07 | s1 | n | n | d0
TN_2021_3126 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 36.2 | 24.46 | No | 2021-05-13 | C_s1_d0 | 1.43 | 17.5 | 31.6 | 828 | 71.7 | C | 29.1 | 0.07 | s1 | n | n | d0
TN_2021_3127 | Portugal | 84000751 20294067 | 837730B | TXXI 1KV 1X300 DCA-S2.D2.A2 | 28.6 | 6 | Vilanova | INSULATION:PRS-03;SHEATH:TPR-55 | CD | 37.7 | 24.32 | No | 2021-05-13 | B2_s1_d2 | 0.57 | 9 | 26.2 | 1500 | 21.9 | B2 | 8.9 | 0.03 | s1 | n | y | d2
TN_2021_3128 | Cavinova | 83295 2038894 | 880042T | RHZ1MAZ1+OL 66KV 1X185K + H150 DCA-S1B.D2.A1 | 60.89 | 3 | Vilanova | 14201.8MM+60002.9MM | CD | 39.5 | 24.13 | No | 2021-05-13 | B2_s1_d2 | 0.87 | 9.6 | 17.5 | 1500 | 35.2 | B2 | 0.3 | 0.01 | s1 | n | y | d2
TN_2021_3129 | Portugal | 83330 20362317 | 914071F | TXXI 1KV 1X150 AL2 DCA-S2.D2.A2 | 20.17 | 8 | Vilanova | TPR-55 | CD | 46.2 | 23.13 | No | 2021-05-13 | B2_s1_d0 | 0.27 | 3.7 | 6.8 | 1488 | 16.5 | B2 | 6.3 | 0.02 | s1 | n | n | d0
TN_2021_3130 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 73.2 | 16.36 | No | 2021-05-14 | C_s1_d0 | 1.45 | 20.8 | 39.2 | 867 | 75.1 | C | 32.9 | 0.09 | s1 | n | n | d0
TN_2021_3131 | Sta Perpetua | 82325 20360646 | 883807K | AFUMEX CLASS 3KV RZ1 (AS) 1X300MM2 | 30.67 | 6 | Vilanova | XLPE+1420+1602 | CD | 71.9 | 17.09 | No | 2021-05-14 | B2_s1_d2 | 0.45 | 4.9 | 7.8 | 1488 | 15.5 | B2 | 6.8 | 0.01 | s1 | n | y | d2
TN_2021_3132 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 47.8 | 21.22 | No | 2021-05-14 | C_s1_d0 | 1.35 | 17.2 | 33.8 | 843 | 72.6 | C | 15.8 | 0.06 | s1 | n | n | d0
CC_HRR_2021_005 |  |  | MR233 y MR232 | AFUMEX CLASS 750V H07Z1-K(AS) TYPE2 1X25 | 8.57 | 17 | Vilanova | REFENCESAMPLE | CD | 59.6 | 19.07 | No | 2021-05-14 | B2_s1_d0 | 0.42 | 2.3 | 7 | 534 | 33 | B2 | 0.1 | 0 | s1 | n | n | d0
CC_HRR_2021_006 |  |  | MR232 | AFUMEX CLASS 750V H07Z1-K(AS) TYPE2 1X25 | 8.57 | 17 | Vilanova | REFENCESAMPLE | CD | 56.7 | 19.96 | No | 2021-05-14 | B2_s1_d0 | 0.39 | 2.8 | 7.6 | 633 | 30.2 | B2 | 19.3 | 0.03 | s1 | n | n | d0
TN_2021_3134 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 64.4 | 19.92 | No | 2021-05-17 | B2_s2_d0 | 1 | 11.6 | 21.9 | 873 | 58.1 | B2 | 50.5 | 0.09 | s2 | n | n | d0
TN_2021_3135 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 50 | 22.94 | No | 2021-05-17 | C_s1_d0 | 1.4 | 19.5 | 33.9 | 867 | 72.9 | C | 25.2 | 0.07 | s1 | n | n | d0
TN_2021_3136 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 46 | 24 | No | 2021-05-17 | B2_s1_d0 | 1.3 | 13.3 | 26.3 | 882 | 59.5 | B2 | 35.9 | 0.08 | s1 | n | n | d0
TN_2021_3137 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 68.1 | 18.89 | No | 2021-05-18 | C_s2_d0 | 1.4 | 18.5 | 34.1 | 882 | 68.7 | C | 51.6 | 0.1 | s2 | n | n | d0
TN_2021_3138 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 64.5 | 18.98 | No | 2021-05-18 | C_s1_d0 | 1.36 | 18.4 | 34.4 | 834 | 69.6 | C | 48.8 | 0.12 | s1 | n | n | d0
TN_2021_3139 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 70.9 | 19.99 | No | 2021-05-18 | C_s2_d0 | 1.43 | 19 | 32.6 | 834 | 61.8 | C | 51.7 | 0.1 | s2 | n | n | d0
TN_2021_3140 |  |  |  | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.01 | 15 | Vilanova | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | CD | 70.3 | 21.39 | No | 2021-05-18 | C_s1_d0 | 1.64 | 21.1 | 35.3 | 882 | 74.6 | C | 37.8 | 0.07 | s1 | n | n | d0
TN_2021_3145 | Abrera | 84135422 20193998 | 5096254 | AFUMEX CLASS H07Z1-K 1X6 NE 750V | 4.54 | 60 | Vilanova | 1420+1602 | CD | 69.8 | 17.35 | No | 2021-05-19 | C_s1_d0 | 1.59 | 9.3 | 25.5 | 678 | 81.6 | C | 18.7 | 0.08 | s1 | n | n | d0
TN_2021_3146 | Abrera | 84087418 203028141 | 5096260 | EXZHELLENT H07Z1-K 1X1.5 NE 750V | 2.87 | 165 | Vilanova | 0400+TPR-54 | CD | 66.7 | 17.89 | No | 2021-05-19 | D_s1_d0 | 3.3 | 39.6 | 51.9 | 774 | 112.8 | D | 47.8 | 0.07 | s1 | n | n | d0
TN_2021_3147 | Abrera | 84135367 20302822 | 5096259 | EXZHELLENT H07Z1-K 1X2.5 NE 750V | 3.53 | 120 | Vilanova | 0400+TPR-54 | CD | 62.1 | 19.15 | No | 2021-05-19 | D_s1_d0 | 3.3 | 47.9 | 63.2 | 1167 | 124.5 | D | 37.7 | 0.08 | s1 | n | n | d0
TN_2021_3148 | ITALY | 80555 20353603 | T1-H93167 | FG16M16 1X240MM2 | 27.91 | 6 | Vilanova | BEDDING0300FDITSP0.35+546ACSEIT | CD | 63.8 | 17.54 | No | 2021-05-19 | B2_s1_d2 | 0.69 | 9.7 | 25.2 | 1500 | 29.1 | B2 | 8.8 | 0.02 | s1 | n | y | d2
TN_2021_3149 | Portugal | 84211650 20303244 | 895996J | EXZHELLENT CLASS RZ1 (AS) 1KV 1X120AL VD | 18.62 | 8 | Vilanova | TPR-55 | CD | 65.5 | 20.67 | No | 2021-05-19 | B2_s1_d2 | 0.38 | 4.3 | 6.1 | 801 | 15.1 | B2 | 14.3 | 0.02 | s1 | n | y | d2
TN_2021_3151 | Abrera | 84135435 20302828 | 5096258 | EXZHELLENT H07Z1-K 1X4 NE 750V | 4.03 | 90 | Vilanova | 0400+TPR-54 | CD | 64.3 | 15.49 | No | 2021-05-20 | D_s1_d0 | 3.3 | 38.2 | 46.2 | 885 | 93.9 | D | 42.5 | 0.06 | s1 | n | n | d0
TN_2021_3152 | Abrera | 84248600 20193680 | 857233A | AFUMEX CLASS 1KV RZ1-K (AS) 5G6MM2 | 15.96 | 9 | Vilanova | 1420+16HI | CD | 63.9 | 16.08 | No | 2021-05-20 | B2_s1_d2 | 0.7 | 10.7 | 20 | 1425 | 22.6 | B2 | 4.5 | 0.02 | s1 | n | y | d2
TN_2021_3153 | Abrera | 84189047 20193655 | 891677P | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5MM2 | 11.73 | 13 | Vilanova | 1420+16HI | CD | 20.1 | 19.48 | No | 2021-05-20 | B2_s1_d1 | 0.81 | 8.7 | 19.2 | 900 | 32.8 | B2 | 12.5 | 0.03 | s1 | y | n | d1
TN_2021_3154 | Abrera | 83669 20193654 | 913651Z | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.88 | 14 | Vilanova | 1420+16HI | CD | 49 | 20.62 | No | 2021-05-20 | B2_s1_d2 | 0.7 | 7.4 | 17.8 | 831 | 35.4 | B2 | 14 | 0.02 | s1 | n | y | d2
TN_2021_3155 | Abrera | 83669 20193654 | 913651Z | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.88 | 14 | Vilanova | 1420+16HI | CD | 47.9 | 22.25 | No | 2021-05-20 | B2_s1_d1 | 0.75 | 9.8 | 25.9 | 804 | 51.6 | B2 | 10.7 | 0.02 | s1 | y | n | d1
21050008 | Paron | 18691 | CE6811H | FR-N1X1G1 1X25MM² | 11.6 | 13 | Paron | IX1400FR+56ACSEIT | -- | 40.2 | 24.8 | No | 2021-05-10 | D_s2_d2 | 3 | 45.8 | 67.4 | 1083 | 99 | D | 87 | 0.21 | s2 | y | y | d2
21050009 | Paron | 18691 | CE6811C | FR-N1X1G1 1X150MM² | 21.1 | 7 | Paron | IX1400FR+TPR55 | -- | 36 | 24.5 | No | 2021-05-10 | B2_s1_d0 | 0.3 | 5.5 | 7.1 | 1470 | 24 | B2 | 3 | 0 | s1 | n | n | d0
21050010 | Paron | 18691 | CE6811C | FR-N1X1G1 1X150MM² | 21.1 | 7 | Paron | IX1400FR+TPR55 | -- | 34.6 | 26.1 | No | 2021-05-10 | B2_s1_d1 | 0.4 | 4 | 7.9 | 1449 | 16 | B2 | 6 | 0.01 | s1 | y | n | d1
21050012 | Paron | 18691 | CE6811F | FR-N1X1G1 1X25MM² | 11.6 | 13 | Paron | IX1400FR+TPR55 | -- | 38.5 | 22.7 | No | 2021-05-12 | B2_s1_d2 | 1.1 | 11.8 | 23 | 807 | 48 | B2 | 21 | 0.06 | s1 | y | y | d2
21050013 | Paron | 18691 | CE6811F | FR-N1X1G1 1X25MM² | 11.6 | 13 | Paron | IX1400FR+TPR55 | -- | 39 | 22.4 | No | 2021-05-12 | D_s2_d2 | 2.5 | 37.1 | 55.2 | 1329 | 69 | D | 83 | 0.07 | s2 | y | y | d2
21050014 | Paron | 18691 | CE6811B | FR-N1X1G1 1X150MM² | 21.1 | 13 | Paron | IX1400FR+04ANFEIT+TPR55 | -- | 35.5 | 23 | No | 2021-05-12 | B2_s1_d1 | 0.3 | 5.5 | 8.6 | 1497 | 30 | B2 | 6 | 0.01 | s1 | y | n | d1
21050015 | Paron | 18691 | CE6811D | FR-N1X1G1 1X25MM² | 11.6 | 13 | Paron | IX1400FR+04ANFEIT+5300SEIT | -- | 40 | 23.1 | No | 2021-05-17 | B2_s1_d2 | 0.7 | 8.2 | 14 | 822 | 32 | B2 | 8 | 0.02 | s1 | y | y | d2
21050016 | Paron | 18691 | CE6811D | FR-N1X1G1 1X25MM² | 11.6 | 13 | Paron | IX1400FR+04ANFEIT+5300SEIT | -- | 40.2 | 23.2 | No | 2021-05-17 | B2_s1_d2 | 0.65 | 9.9 | 13.2 | 1053 | 35 | B2 | 8 | 0.02 | s1 | y | y | d2
21050017 | Paron | 18691 | CE6811B | FR-N1X1G1 1X150MM² | 21.1 | 7 | Paron | IX1400FR+04ANFEIT+TPR55 | -- | 42.4 | 22.4 | No | 2021-05-17 | B2_s1_d0 | 0.2 | 2.8 | 4.8 | 555 | 20 | B2 | 0 | 0 | s1 | n | n | d0
21050018 | Paron | 18691 | CE6811E | FR-N1X1G1 1X25MM² | 11.6 | 7 | Paron | IX1400FR+04ANFEIT+TPR55 | -- | 42 | 22.3 | No | 2021-05-17 | B2_s1_d2 | 0.7 | 12.3 | 21.7 | 1014 | 31 | B2 | 17 | 0.04 | s1 | y | y | d2
21050019 | Paron | 18691 | CE6811I | FR-N1X1G1 1X150MM² | 22.1 | 7 | Paron | IX1400FR+04ANFEIT+56ACSEIT | -- | 38.8 | 23.2 | No | 2021-05-18 | B2_s1_d1 | 0.3 | 4.3 | 7.5 | 1500 | 23 | B2 | 2 | 0 | s1 | y | n | d1
21050020 | Paron | 18691 | CE6811E | FR-N1X1G1 1X25MM² | 11.6 | 13 | Paron | IX1400FR+04ANFEIT+TPR55 | -- | 38.5 | 22.8 | No | 2021-05-18 | B2_s1_d2 | 0.75 | 8.1 | 14.1 | 1002 | 28 | B2 | 9 | 0.01 | s1 | y | y | d2
21030029 | Paron | 18562 | -- | NF-USE 1350 FR-N1*1G1-U0.6/1KV 3G1.5 REPERO PLUS CCA-S1.D1.A1 NFC 32-323 2020 MT 3559 | 9.8 | 15 | Paron | SXLPE+LSOH | -- | 30 | 21.2 | No | 2021-03-18 | C_s1_d0 | 1.8 | 24.3 | 39.1 | 771 | 84 | C | 45 | 0.09 | s1 | n | n | d0
21030031 | Paron | 18562 | -- | NF-USE 1350 FR-N1*1G1-U0.6/1KV 3G2.5 REPERO PLUS CCA-S1.D1.A1 NF C 32-323 2020 OP 19700 L 14060719 | 10.57 | 14 | Paron | SXLPE+LSOH | -- | 29.9 | 19.8 | No | 2021-03-22 | C_s1_d0 | 1.25 | 19.3 | 32 | 798 | 65 | C | 48 | 0.14 | s1 | n | n | d0
21030030 | Paron | 18562 | -- | NF USE ALCOBRE X Z1 (FRT.ZH)IEC 60502-1 1151641/18 CLASS CCA - S1B.D1.A1 02115M | 9.86 | 9.86 | Paron | SXLPE+LSOH | -- | 30.6 | 19.6 | No | 2021-03-22 | B2_s1_d0 | 0.55 | 7.6 | 18.6 | 687 | 51 | B2 | 8 | 0.03 | s1 | n | n | d0
21030032 | Paron | 18657 | CE6793 | ZPFU-SH- 2P*1MM²- CE6793 -CT- 445 PRYSMIAN 255-2021-03 | 12.25 | 13 | Paron |  | -- | 31.8 | 18.9 | No | 2021-03-22 | B2_s1_d2 | 0.2 | 4.6 | 9.9 | 819 | 28 | B2 | 10 | 0.03 | s1 | y | y | d2
21030037 | Paron | 18657 | CE6793 | ZPFU-SH- 2P*1MM²- CE6793 -CT- 445 PRYSMIAN 255-2021-03 | 12.25 | 13 | Paron |  | -- | 36.8 | 21.4 | No | 2021-03-26 | B2_s1_d1 | 0.3 | 5.3 | 12.6 | 786 | 28 | B2 | 20 | 0.07 | s1 | y | n | d1
21030034 | Paron | 18657 | CE6795 | ZPAU-SH-4P*1MM² CE6795 CT 445 PRYSMIAN 255 2021-03 | 20.5 | 7 | Paron |  | -- | 33.1 | 22.6 | No | 2021-03-24 | B2_s1_d0 | 0.1 | 3.4 | 4.8 | 705 | 15 | B2 | 3 | 0 | s1 | n | n | d0
21030036 | Paron | 18657 | CE6795 | ZPAU-SH-4P*1MM² CE6795 CT 445 PRYSMIAN 255 2021-03 | 20.5 | 7 | Paron |  | -- | 36.2 | 21.1 | No | 2021-03-26 | B2_s1_d0 | 0.1 | 3.1 | 4.3 | 810 | 14 | B2 | 6 | 0.01 | s1 | n | n | d0
21030040 | Paron | 18657 | CE6796 | SNCF RESEAU -SH-28P*1MM²-CE6796 -CT 445-PRYSMIAN 255-2021-03 | 31.64 | 6 | Paron |  | -- | 28.7 | 23.6 | No | 2021-03-30 | B2_s1_d0 | 0.6 | 9.5 | 11.6 | 819 | 38 | B2 | 26 | 0.03 | s1 | n | n | d0
21030041 | Paron | 18657 | CE6796 | SNCF RESEAU -SH-28P*1MM²-CE6796 -CT 445-PRYSMIAN 255-2021-03 | 31.64 | 6 | Paron |  | -- | 36.1 | 23.5 | No | 2021-03-31 | B2_s1_d0 | 0.75 | 7.6 | 10.1 | 696 | 35 | B2 | 19 | 0.02 | s1 | n | n | d0
21030038 | Paron | 18655 | -- | 750-5G1.5-SH-NF F 55-625- PRYSMIAN 255-DOP 1011822 B2CA-S1A.D0.A1-CE-K25-2021-08 | 14 | 11 | Paron |  | -- | 33.6 | 22.4 | No | 2021-03-26 | B2_s1_d2 | 0.55 | 5.3 | 13.1 | 1023 | 18 | B2 | 3 | 0.01 | s1 | y | y | d2
21030039 | Paron | 18655 | -- | 750-5G1.5-SH-NF F 55-625- PRYSMIAN 255-DOP 1011822 B2CA-S1A.D0.A1-CE-K25-2021-08 | 14 | 11 | Paron |  | -- | 30.6 | 22 | No | 2021-03-30 | B2_s1_d2 | 0.75 | 9.6 | 17.1 | 1038 | 31 | B2 | 12 | 0.03 | s1 | y | y | d2
TN_2021_3157 | Cavinova | 84390 20361116 | 926873W | RHZ1-2OL 12/20KV 1X150 AL + H25 DCA | 38.9 | 5 | Vilanova | XLPE+0400FEIT+TPO-03 | CD | 74.2 | 17.25 | No | 2021-05-21 | B2_s1_d0 | 0.72 | 12.8 | 17.8 | 849 | 49.2 | B2 | 34.7 | 0.07 | s1 | n | n | d0
TN_2021_3158 | Abrera | 84189047 20193655 | 891677P | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5MM2 | 11.73 | 13 | Vilanova | 1420+16HI | CD | 74.3 | 18 | No | 2021-05-21 | C_s1_d1 | 1.39 | 20 | 38.6 | 882 | 67.6 | C | 24.4 | 0.04 | s1 | y | n | d1
TN_2021_3159 | Abrera | 84248600 20193680 | 857233A | AFUMEX CLASS 1KV RZ1-K (AS) 5G6MM2 | 15.96 | 9 | Vilanova | 1420+16HI | CD | 74.2 | 19.48 | No | 2021-05-21 | B2_s1_d2 | 0.8 | 13 | 25.9 | 1338 | 25.2 | B2 | 13.3 | 0.03 | s1 | n | y | d2
TN_2021_3160 | Abrera | 84248600 20193680 | 857233A | AFUMEX CLASS 1KV RZ1-K (AS) 5G6MM2 | 15.96 | 9 | Vilanova | 1420+16HI | CD | 70.1 | 21.17 | No | 2021-05-21 | C_s1_d2 | 1.14 | 19.1 | 40.7 | 1359 | 38.4 | C | 29.8 | 0.06 | s1 | n | y | d2
TN_2021_3161 | Abrera | 84189047 20193655 | 891677P | AFUMEX CLASS 1KV RZ1-K (AS) 3G2.5MM2 | 11.73 | 13 | Vilanova | 1420+16HI | CD | 66.3 | 23.12 | No | 2021-05-21 | C_s1_d0 | 1.22 | 17 | 30.1 | 843 | 55.5 | C | 6.2 | 0.02 | s1 | n | n | d0
21050029 | Maliaño | -- | -- | 48F LT- VT AF | 11.1 | 14 | Paron | PBT-FR-GELFFILLED-FRAFUMEXCPR | -- | 46.6 | 21.3 | No | 2021-05-21 | C_s1_d0 | 1.5 | 12.9 | 31.4 | 684 | 109.7 | C | 39.9 | 0.08 | s1 | n | n | d0
21050023 | Paron | 18691 | CE6811A | FR-N1X1G1 1X150MM² | 22.1 | 7 | Paron | IX1400FR+04ANFEIT+5300SEIT | -- | 45.4 | 22.8 | No | 2021-05-19 | B2_s1_d1 | 0.25 | 2.5 | 3.9 | 1431 | 10 | B2 | 1 | 0 | s1 | y | n | d1
21050024 | Paron | 18691 | CE6811G | FR-N1X1G1 1X25MM² | 11.6 | 13 | Paron | IX1400FR+04ANFEIT+56ACSEIT | -- | 46.1 | 22.4 | No | 2021-05-19 | B2_s1_d2 | 0.75 | 11 | 20.7 | 867 | 48 | B2 | 16 | 0.03 | s1 | y | y | d2
21050025 | Paron | 18691 | CE6811A | FR-N1X1G1 1X150MM² | 22.1 | 7 | Paron | IX1400FR+04ANFEIT+5300SEIT | -- | 48 | 22.3 | No | 2021-05-19 | B2_s1_d0 | 0.25 | 4.5 | 5.7 | 1461 | 23 | B2 | 3 | 0 | s1 | n | n | d0
21050026 | Paron | 18691 | CE6811G | FR-N1X1G1 1X25MM² | 11.6 | 13 | Paron | IX1400FR+04ANFEIT+56ACSEIT | -- | 48 | 22.3 | No | 2021-05-19 | C_s1_d2 | 1.15 | 20.3 | 34.9 | 882 | 60 | C | 20 | 0.04 | s1 | y | y | d2
21050027 | Paron | 18691 | CE6811J | FR-N1X1G1 1X150MM² | 21.1 | 7 | Paron | IX1400FR+56ACSEIT | -- | 42.8 | 21.5 | No | 2021-05-20 | B2_s1_d2 | 0.2 | 2.7 | 5 | 1491 | 17 | B2 | 4 | 0.01 | s1 | y | y | d2
21050028 | Paron | 18566 | -- | AFUMEX TECNUC-PK4U 52S1-OPTICAL CABLE-12SHFOS2 RED HARD RP-LSOH- 2020/35 BBT 910 459 | 15.1 | 10 | Paron |  | -- | 45.2 | 21.3 | No | 2021-05-20 | D_s2_d2 | 3.3 | 54.8 | 126.8 | 1500 | 106 | D | 224 | 0.64 | s2 | y | y | d2
TN_2021_3163 | Abrera | 83036 20352260 | 888162U | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.85 | 13 | Vilanova | 0.50400+16HI | CD | 67.1 | 16.77 | No | 2021-05-24 | B2_s1_d2 | 0.93 | 15 | 29.8 | 768 | 63.7 | B2 | 14.4 | 0.04 | s1 | n | y | d2
TN_2021_3164 | Abrera | 83035 20352260 | 887121M | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.71 | 13 | Vilanova | 0.50420+16HI | CD | 64.6 | 17.04 | No | 2021-05-24 | C_s1_d2 | 1.54 | 23.7 | 33.9 | 816 | 69.3 | C | 18 | 0.04 | s1 | n | y | d2
TN_2021_3165 | Abrera | 84189069 20302799 | 5096261 | EXZH CLASS ES05Z1-K (AS) 1X1 | 2.47 | 240 | Vilanova | TPR-52-TPR-45 | CD | 57.1 | 20.59 | No | 2021-05-24 | B2_s2_d2 | 1.3 | 11.8 | 25.8 | 729 | 66 | B2 | 51.2 | 0.01 | s2 | n | y | d2
TN_2021_3166 | Abrera | 83669 20193654 | 913651Z | AFUMEX CLASS 1KV RZ1-K (AS) 3G1.5MM2 | 10.88 | 14 | Vilanova | 1420+16HI | CD | 54.1 | 22.32 | No | 2021-05-24 | B2_s1_d0 | 0.69 | 10 | 24.2 | 753 | 53.5 | B2 | 9.1 | 0.02 | s1 | n | n | d0
TN_2021_3167 | Portugal | 84200817 20303248 | 887142K | EXZHELLENT CLASS RZ1 (AS) 1KV 1X300 AL VD | 27.34 | 6 | Vilanova | TPR-55 | CD | 52.7 | 23.65 | No | 2021-05-24 | C_s1_d2 | 1.1 | 19.9 | 42.4 | 1494 | 35.5 | C | 30.1 | 0.07 | s1 | n | y | d2
TN_2021_3168 | Abrera | 82619 20361425 | 888134N | FG16OM16 5G1.5 | 13 | 12 | Vilanova | 0.50400+1.8WT2205 | CD | 64.5 | 18.15 | No | 2021-05-25 | B2_s1_d0 | 0.91 | 12.3 | 27.2 | 837 | 53.7 | B2 | 11.9 | 0.03 | s1 | n | n | d0
TN_2021_3169 | Abrera | 88613 20361424 | 888133M | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.76 | 13 | Vilanova | 0.30400+1.4WT2205 | CD | 62.3 | 18.58 | No | 2021-05-25 | B2_s1_d1 | 0.7 | 8.9 | 24.4 | 768 | 52.9 | B2 | 4.2 | 0.03 | s1 | y | n | d1
TN_2021_3170 | Santander | S230684 60072756 | FE130 21K0198-1 | FVDI-FT-G0M1 32 8X4 32F FXT VT | 10.34 | 15 | Vilanova | CYGSALHC-1800 | CD | 58.9 | 18.68 | No | 2021-05-25 | D_s2_d2 | 3.3 | 46.5 | 117.4 | 849 | 228.9 | D | 67.1 | 0.21 | s2 | n | y | d2
TN_2021_3171 | Abrera | 88613 20361424 | 888133M | AFUMEX CLASS 1KV RZ1-K (AS) 5G1.5 | 11.76 | 13 | Vilanova | 0.30400+1.4WT2205 | CD | 57.9 | 18.4 | No | 2021-05-25 | C_s1_d1 | 1.29 | 16.3 | 30.4 | 807 | 65.9 | C | 15.8 | 0.04 | s1 | y | n | d1
TN_2021_3172 | Abrera | 83940722 20302921 | 814240U | EXZHELLENT COMPACT 1KV RZ1-K (AS) 5G1.5 | 11.85 | 13 | Vilanova | 0400+TPR-54 | CD | 59.2 | 18.64 | No | 2021-05-25 | B2_s1_d0 | 0.7 | 9.1 | 18.4 | 864 | 39.5 | B2 | 22.7 | 0.04 | s1 | n | n | d0
TN_2021_3173 | Sta Perpetua | 82325 20360646 | 883807K | AFUMEX CLASS 3KV RZ1 (AS) 1X300MM2 | 30.67 | 6 | Vilanova | XLPE+1420+1602 | CD | 64 | 18.38 | No | 2021-05-26 | B2_s1_d0 | 0.44 | 4.5 | 6 | 780 | 19.2 | B2 | 31 | 0.01 | s1 | n | n | d0
TN_2021_3174 | Portugal | 80115 20339525 | 5096262 (802003T) | G 250 V 1X500 B2CA S1A D2 A1 | 33.33 | 6 | Vilanova |  | CD | 62.3 | 19.84 | No | 2021-05-26 | B2_s1_d2 | 0.71 | 10.7 | 17.7 | 732 | 48.2 | B2 | 3.7 | 0.01 | s1 | n | y | d2
TN_2021_3175 | Portugal | 80114 20339524 | 5096263 (802003T) | G 250 V 1X300 B2CA S1A D2 A1 | 26.14 | 6 | Vilanova |  | CD | 61.2 | 20.95 | No | 2021-05-26 | B2_s1_d2 | 0.51 | 7 | 9 | 573 | 33 | B2 | 7.6 | 0.01 | s1 | n | y | d2
TN_2021_3177 | Abrera | 84189069 20302799 | 5096261 | EXZH CLASS ES05Z1-K (AS) 1X1 | 2.47 | 240 | Vilanova | TPR-52-TPR-45 | CD | 57.9 | 23.98 | No | 2021-05-26 | C_s2_d2 | 1.96 | 21.1 | 31.5 | 819 | 98.8 | C | 52.4 | 0.1 | s2 | n | y | d2
21050030 | Charvieu | 18726 | - | FR-N1X1G1 3G1.5MM² | 10.1 | 15 | Paron | IX2200+0400FEIT+5300SEIT | -- | 23.1 | 47.8 | No | 2021-05-26 | B2_s1_d2 | 1.1 | 12.2 | 28.9 | 822 | 66 | B2 | 20 | 0.05 | s1 | y | y | d2
21050031 | Charvieu | 18726 | - | FR-N1X1G1 3G1.5MM² | 10.1 | 15 | Paron | IX2200+0400FEIT+5300SEIT | -- | 23.1 | 48 | No | 2021-05-26 | C_s1_d2 | 1.25 | 15.5 | 39 | 855 | 72 | C | 40 | 0.1 | s1 | y | y | d2
21050032 | Paron | 18566 | -- | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.1 | 15 | Paron | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | -- | 23.1 | 48.1 | No | 2021-05-26 | B2_s1_d0 | 0.8 | 11 | 20.6 | 633 | 56 | B2 | 19 | 0.04 | s1 | n | n | d0
21050033 | Paron | 18566 | -- | CÂBLE DE RÉFÉRENCE DOW CORNING | 10.1 | 15 | Paron | DIELECTRICCENTRALMEMBER+LLDPEINNERJACKETBLACK+FRNC/LSZHOUTERJACKETWHITE | -- | 23.3 | 48.4 | No | 2021-05-26 | C_s1_d0 | 1.2 | 15.1 | 26.3 | 891 | 63 | C | 34 | 0.08 | s1 | n | n | d0
TN_2021_3178 | Sta Perpetua |  | 861190B | RZ1-K 5G1.5 | 12.42 | 13 | Vilanova | LE200395IX30AC+5%TABICABCM004+PAPEL+LE20041716HISEES | CD | 71.8 | 17.14 | No | 2021-05-27 | B2_s1_d2 | 1.12 | 14.1 | 24.8 | 969 | 37.7 | B2 | 9.1 | 0.02 | s1 | n | y | d2
TN_2021_3179 | Sta Perpetua |  | 861190B | RZ1-K 5G1.5 | 12.42 | 13 | Vilanova | LE200395IX30AC+5%TABICABCM004+PAPEL+LE20041716HISEES | CD | 69.9 | 18.92 | No | 2021-05-27 | B2_s1_d2 | 0.98 | 14.7 | 22.9 | 804 | 47.8 | B2 | 23.9 | 0.04 | s1 | n | y | d2
TN_2021_3180 | Sta Perpetua |  | 861190B | RZ1-K 5G1.5 | 12.42 | 13 | Vilanova | LE200395IX30AC+5%TABICABCM004+PAPEL+LE20041716HISEES | CD | 65.7 | 22.97 | No | 2021-05-27 | C_s1_d2 | 1.11 | 17.6 | 30.5 | 837 | 61.5 | C | 24.1 | 0.03 | s1 | n | y | d2